## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2321-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2321-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2321-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2321-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2321-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2321-3_0_4_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_2321-3_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_2321-3_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2321-3_0_4_node_38 | 0.4 | n |  | TRUE
9 | bus_LV_2321-3_0_4_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_2321-3_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2321-3_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2321-3_0_4_node_59 | 0.4 | n |  | TRUE
13 | bus_LV_2321-3_0_4_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_2321-3_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2321-3_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2321-3_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2321-3_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2321-3_0_4_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_2321-3_0_4_node_36 | 0.4 | n |  | TRUE
20 | bus_LV_2321-3_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2321-3_0_4_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_2321-3_0_4_node_39 | 0.4 | n |  | TRUE
23 | bus_LV_2321-3_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_2321-3_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2321-3_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_2321-3_0_4_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_2321-3_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_2321-3_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_2321-3_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_2321-3_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_2321-3_0_4_node_47 | 0.4 | n |  | TRUE
32 | bus_LV_2321-3_0_4_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_2321-3_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_2321-3_0_4_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_2321-3_0_4_node_48 | 0.4 | n |  | TRUE
36 | bus_LV_2321-3_0_4_node_49 | 0.4 | n |  | TRUE
37 | bus_LV_2321-3_0_4_node_55 | 0.4 | n |  | TRUE
38 | bus_LV_2321-3_0_4_node_56 | 0.4 | n |  | TRUE
39 | bus_LV_2321-3_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_2321-3_0_4_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_2321-3_0_4_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_2321-3_0_4_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_2321-3_0_4_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_2321-3_0_4_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_2321-3_0_4_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_2321-3_0_4_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_2321-3_0_4_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_2321-3_0_4_node_54 | 0.4 | n |  | TRUE
49 | bus_LV_2321-3_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_2321-3_0_4_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_2321-3_0_4_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_2321-3_0_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_2321-3_0_4_node_50 | 0.4 | n |  | TRUE
54 | bus_LV_2321-3_0_4_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_2321-3_0_4_node_57 | 0.4 | n |  | TRUE
56 | bus_LV_2321-3_0_4_node_58 | 0.4 | n |  | TRUE
57 | bus_MV_384_0_node_6 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2321-3_0_4_load_0 | 0 | 0.02017 | 0.0050552 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2321-3_0_4_load_16 | 5 | 0.021857 | 0.0054778 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2321-3_0_4_load_13 | 6 | 0.013035 | 0.0032668 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2321-3_0_4_load_5 | 7 | 0.0073308 | 0.0018373 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2321-3_0_4_load_38 | 8 | 0.0045384 | 0.0011374 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2321-3_0_4_load_14 | 9 | 0.01523 | 0.0038171 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2321-3_0_4_load_59 | 12 | 0.0014227 | 0.00035657 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2321-3_0_4_load_9 | 14 | 0.018846 | 0.0047232 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2321-3_0_4_load_10 | 15 | 0.022962 | 0.0057549 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2321-3_0_4_load_11 | 16 | 0.048965 | 0.012272 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2321-3_0_4_load_12 | 17 | 0.018846 | 0.0047232 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2321-3_0_4_load_17 | 23 | 0.0082204 | 0.0020602 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2321-3_0_4_load_18 | 24 | 0.013346 | 0.0033448 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2321-3_0_4_load_20 | 26 | 0.018785 | 0.0047078 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2321-3_0_4_load_23 | 30 | 0.0074748 | 0.0018734 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2321-3_0_4_load_47 | 31 | 0.0025524 | 0.00063969 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2321-3_0_4_load_27 | 32 | 0.01482 | 0.0037143 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2321-3_0_4_load_25 | 33 | 0.029885 | 0.00749 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2321-3_0_4_load_24 | 34 | 0.0078881 | 0.0019769 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2321-3_0_4_load_55 | 37 | 0.016319 | 0.00409 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2321-3_0_4_load_56 | 38 | 0.012785 | 0.0032043 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2321-3_0_4_load_28 | 39 | 0.0058802 | 0.0014737 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2321-3_0_4_load_29 | 40 | 0.0081727 | 0.0020483 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2321-3_0_4_load_31 | 41 | 0.0037983 | 0.00095195 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2321-3_0_4_load_32 | 42 | 0.019654 | 0.0049258 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2321-3_0_4_load_44 | 43 | 0.0081404 | 0.0020402 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2321-3_0_4_load_43 | 44 | 0.013304 | 0.0033344 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2321-3_0_4_load_37 | 45 | 0.012749 | 0.0031952 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2321-3_0_4_load_35 | 46 | 0.0072297 | 0.0018119 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2321-3_0_4_load_42 | 47 | 0.0021906 | 0.00054901 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2321-3_0_4_load_54 | 48 | 0.0016468 | 0.00041272 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2321-3_0_4_load_40 | 49 | 0.0026042 | 0.00065268 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2321-3_0_4_load_45 | 51 | 0.0047619 | 0.0011934 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2321-3_0_4_load_46 | 52 | 0.02038 | 0.0051076 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2321-3_0_4_load_50 | 53 | 0.0058537 | 0.0014671 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2321-3_0_4_load_58 | 56 | 0.0081229 | 0.0020358 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 41 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2321-3_0_4_line_0 |  | 0 | 1 | 0.0029449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2321-3_0_4_line_1 |  | 0 | 2 | 0.0045199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2321-3_0_4_line_2 |  | 1 | 3 | 0.020955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2321-3_0_4_line_3 |  | 2 | 4 | 0.058037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2321-3_0_4_line_4 |  | 3 | 5 | 0.090592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2321-3_0_4_line_5 |  | 3 | 6 | 0.023903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2321-3_0_4_line_6 |  | 4 | 7 | 0.043548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2321-3_0_4_line_7 |  | 5 | 8 | 0.033919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2321-3_0_4_line_8 |  | 6 | 9 | 0.055047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2321-3_0_4_line_9 |  | 7 | 10 | 0.0041186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2321-3_0_4_line_10 |  | 8 | 22 | 0.004466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2321-3_0_4_line_11 |  | 9 | 20 | 0.03135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2321-3_0_4_line_12 |  | 10 | 11 | 0.028047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2321-3_0_4_line_13 |  | 11 | 12 | 0.020937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2321-3_0_4_line_14 |  | 12 | 13 | 0.0020668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2321-3_0_4_line_15 |  | 13 | 54 | 0.08469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2321-3_0_4_line_16 |  | 14 | 15 | 0.044762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2321-3_0_4_line_17 |  | 14 | 16 | 0.018136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2321-3_0_4_line_18 |  | 15 | 17 | 0.015585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2321-3_0_4_line_19 |  | 17 | 18 | 0.021746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2321-3_0_4_line_20 |  | 18 | 19 | 0.011225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2321-3_0_4_line_21 |  | 18 | 20 | 0.033874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2321-3_0_4_line_22 |  | 18 | 21 | 0.020199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2321-3_0_4_line_23 |  | 19 | 45 | 0.015475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2321-3_0_4_line_24 |  | 19 | 46 | 0.022394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2321-3_0_4_line_25 |  | 21 | 42 | 0.015211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2321-3_0_4_line_26 |  | 21 | 39 | 0.025573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_2321-3_0_4_line_27 |  | 22 | 47 | 0.0090616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2321-3_0_4_line_28 |  | 23 | 24 | 0.0090109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_2321-3_0_4_line_29 |  | 23 | 25 | 0.047574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_2321-3_0_4_line_30 |  | 24 | 26 | 0.038869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_2321-3_0_4_line_31 |  | 25 | 27 | 0.046125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2321-3_0_4_line_32 |  | 25 | 28 | 0.10806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2321-3_0_4_line_33 |  | 26 | 29 | 0.033148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_2321-3_0_4_line_34 |  | 27 | 30 | 0.045199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2321-3_0_4_line_35 |  | 28 | 31 | 0.070892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_2321-3_0_4_line_36 |  | 29 | 32 | 0.0030655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2321-3_0_4_line_37 |  | 29 | 33 | 0.028306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2321-3_0_4_line_38 |  | 30 | 34 | 0.01441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2321-3_0_4_line_39 |  | 31 | 35 | 0.03981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_2321-3_0_4_line_40 |  | 32 | 37 | 0.023822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2321-3_0_4_line_41 |  | 35 | 36 | 0.007683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_2321-3_0_4_line_42 |  | 36 | 52 | 0.0079387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_2321-3_0_4_line_43 |  | 37 | 38 | 0.039916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2321-3_0_4_line_44 |  | 38 | 55 | 0.066482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2321-3_0_4_line_45 |  | 39 | 40 | 0.027283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_2321-3_0_4_line_46 |  | 40 | 41 | 0.019736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_2321-3_0_4_line_47 |  | 41 | 43 | 0.0035895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_2321-3_0_4_line_48 |  | 43 | 44 | 0.033817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_2321-3_0_4_line_49 |  | 44 | 51 | 0.025347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_2321-3_0_4_line_50 |  | 47 | 48 | 0.011474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2321-3_0_4_line_51 |  | 48 | 50 | 0.045091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2321-3_0_4_line_52 |  | 49 | 50 | 0.0085465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2321-3_0_4_line_53 |  | 51 | 52 | 0.010403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_2321-3_0_4_line_54 |  | 53 | 54 | 0.040053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2321-3_0_4_line_55 |  | 55 | 56 | 0.042116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2321-3_0_4_trafo_31 | 0.63 MVA 20/0.4 kV | 57 | 41 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2554817.2008 | 1151274.8657 | 2554815.8942 | 1151272.2266
1 | 2554813.8886 | 1151268.176 | 2554815.8942 | 1151272.2266
2 | 2554825.5882 | 1151294.0459 | 2554822.1576 | 1151284.8892 | 2554817.2008 | 1151274.8657
3 | 2554813.8886 | 1151268.176 | 2554816.0709 | 1151259.3328 | 2554821.2557 | 1151251.7121 | 2554827.211 | 1151246.5202 | 2554834.5054 | 1151246.9101 | 2554844.7926 | 1151246.2102 | 2554855.1184 | 1151245.5323 | 2554858.9372 | 1151245.07
4 | 2554825.5882 | 1151294.0459 | 2554831.4155 | 1151309.599 | 2554840.8339 | 1151336.2865 | 2554846.5453 | 1151350.7288 | 2554857.0619 | 1151378.9867
5 | 2554825.5882 | 1151294.0459 | 2554820.0069 | 1151298.9571 | 2554807.5082 | 1151306.6439 | 2554805.9826 | 1151307.5902
6 | 2554858.9372 | 1151245.07 | 2554868.9444 | 1151243.8832 | 2554876.8701 | 1151242.4896 | 2554882.727 | 1151240.5335 | 2554891.2247 | 1151236.6122 | 2554899.7429 | 1151231.5881
7 | 2554857.0619 | 1151378.9867 | 2554861.3031 | 1151390.3829 | 2554868.9195 | 1151410.7655
8 | 2554807.0577 | 1151357.037 | 2554803.0839 | 1151345.9753 | 2554799.5303 | 1151334.7406 | 2554796.7337 | 1151325.1901 | 2554797.1793 | 1151317.0825 | 2554800.1972 | 1151311.179 | 2554805.9826 | 1151307.5902
9 | 2554903.2904 | 1151229.4957 | 2554899.7429 | 1151231.5881
10 | 2554870.4828 | 1151414.9489 | 2554868.9195 | 1151410.7655
11 | 2554801.965 | 1151385.9821 | 2554808.7186 | 1151375.7149 | 2554809.5147 | 1151368.294 | 2554808.7674 | 1151361.7963 | 2554807.0577 | 1151357.037
12 | 2554903.2904 | 1151229.4957 | 2554909.111 | 1151225.7723 | 2554915.1937 | 1151222.2027 | 2554923.551 | 1151218.9939 | 2554928.6182 | 1151218.1777
13 | 2554928.6182 | 1151218.1777 | 2554935.1334 | 1151218.0287 | 2554941.4369 | 1151218.315 | 2554948.3256 | 1151222.5954
14 | 2554950.0812 | 1151223.6863 | 2554948.3256 | 1151222.5954
15 | 2554950.0812 | 1151223.6863 | 2554993.5091 | 1151249.4854 | 2555009.0881 | 1151257.4618 | 2555024.4596 | 1151264.3836
16 | 2554765.3681 | 1151363.3695 | 2554753.7468 | 1151340.6548 | 2554754.238 | 1151321.4142
17 | 2554754.701 | 1151303.2839 | 2554754.238 | 1151321.4142
18 | 2554765.3681 | 1151363.3695 | 2554768.3136 | 1151369.1266 | 2554769.1732 | 1151378.2044
19 | 2554771.2235 | 1151399.8539 | 2554769.1732 | 1151378.2044
20 | 2554771.2235 | 1151399.8539 | 2554773.8586 | 1151403.2581 | 2554775.5976 | 1151409.9595
21 | 2554801.965 | 1151385.9821 | 2554793.1896 | 1151391.7178 | 2554784.3937 | 1151395.7527 | 2554771.2235 | 1151399.8539
22 | 2554771.2235 | 1151399.8539 | 2554761.6842 | 1151403.0162 | 2554752.125 | 1151406.5789
23 | 2554775.5976 | 1151409.9595 | 2554783.0618 | 1151410.5037 | 2554789.1171 | 1151405.2898
24 | 2554775.5976 | 1151409.9595 | 2554761.1849 | 1151427.0997
25 | 2554752.125 | 1151406.5789 | 2554751.8995 | 1151412.3058 | 2554751.1251 | 1151421.754
26 | 2554752.125 | 1151406.5789 | 2554751.6641 | 1151401.4353 | 2554748.6634 | 1151387.2061 | 2554747.3056 | 1151381.4991
27 | 2554870.4828 | 1151414.9489 | 2554876.9075 | 1151408.5586
28 | 2554615.3193 | 1151296.114 | 2554610.3341 | 1151288.6077
29 | 2554580.5597 | 1151251.5149 | 2554609.0936 | 1151286.7398 | 2554610.3341 | 1151288.6077
30 | 2554615.3193 | 1151296.114 | 2554636.8229 | 1151328.4926
31 | 2554580.5597 | 1151251.5149 | 2554549.0783 | 1151285.3037
32 | 2554580.5597 | 1151251.5149 | 2554589.2097 | 1151241.3665 | 2554608.4147 | 1151222.2783 | 2554612.9331 | 1151217.9085 | 2554624.5981 | 1151208.5823 | 2554635.6512 | 1151201.5619 | 2554649.9 | 1151191.8605 | 2554664.1863 | 1151184.0598
33 | 2554655.1616 | 1151356.1057 | 2554636.8229 | 1151328.4926
34 | 2554549.0783 | 1151285.3037 | 2554557.5173 | 1151298.0131 | 2554564.0159 | 1151312.9384 | 2554568.9245 | 1151325.6907
35 | 2554664.1863 | 1151184.0598 | 2554670.0507 | 1151202.4362 | 2554672.5733 | 1151253.9772
36 | 2554655.1616 | 1151356.1057 | 2554656.736 | 1151358.736
37 | 2554655.1616 | 1151356.1057 | 2554652.8373 | 1151384.3161
38 | 2554568.9245 | 1151325.6907 | 2554574.1009 | 1151339.1387
39 | 2554712.2277 | 1151250.4653 | 2554672.5733 | 1151253.9772
40 | 2554665.5823 | 1151380.5582 | 2554665.6707 | 1151379.7498 | 2554662.0175 | 1151367.56 | 2554656.736 | 1151358.736
41 | 2554713.3748 | 1151258.0606 | 2554712.2277 | 1151250.4653
42 | 2554713.3748 | 1151258.0606 | 2554714.7857 | 1151265.8729
43 | 2554665.5823 | 1151380.5582 | 2554664.127 | 1151393.8576 | 2554657.3128 | 1151407.2382 | 2554648.6605 | 1151414.8457
44 | 2554591.036 | 1151400.7352 | 2554603.8387 | 1151413.0226 | 2554619.3853 | 1151421.7764 | 2554633.7904 | 1151421.6676 | 2554646.7149 | 1151416.5563 | 2554648.6605 | 1151414.8457
45 | 2554747.3056 | 1151381.4991 | 2554744.7876 | 1151370.9157 | 2554740.1114 | 1151355.1922
46 | 2554740.1114 | 1151355.1922 | 2554734.4853 | 1151336.2747
47 | 2554734.4853 | 1151336.2747 | 2554733.4621 | 1151332.8341
48 | 2554723.8221 | 1151300.4199 | 2554733.4621 | 1151332.8341
49 | 2554723.8221 | 1151300.4199 | 2554722.6363 | 1151296.4329 | 2554716.6901 | 1151276.0974
50 | 2554876.9075 | 1151408.5586 | 2554885.0429 | 1151400.4669
51 | 2554885.0429 | 1151400.4669 | 2554925.7187 | 1151419.9259
52 | 2554925.7187 | 1151419.9259 | 2554929.8108 | 1151417.0271 | 2554930.5062 | 1151413.5645
53 | 2554714.7857 | 1151265.8729 | 2554716.5386 | 1151275.5792 | 2554716.6901 | 1151276.0974
54 | 2555024.4596 | 1151264.3836 | 2555047.6029 | 1151274.9938 | 2555061.3424 | 1151279.9113
55 | 2554598.8648 | 1151360.155 | 2554599.8519 | 1151372.9542 | 2554597.404 | 1151385.2013 | 2554591.036 | 1151400.7352

## bus_geodata
| x | y | coords
0 | 2554815.8942 | 1151272.2266
1 | 2554817.2008 | 1151274.8657
2 | 2554813.8886 | 1151268.176
3 | 2554825.5882 | 1151294.0459
4 | 2554858.9372 | 1151245.07
5 | 2554857.0619 | 1151378.9867
6 | 2554805.9826 | 1151307.5902
7 | 2554899.7429 | 1151231.5881
8 | 2554868.9195 | 1151410.7655
9 | 2554807.0577 | 1151357.037
10 | 2554903.2904 | 1151229.4957
11 | 2554928.6182 | 1151218.1777
12 | 2554948.3256 | 1151222.5954
13 | 2554950.0812 | 1151223.6863
14 | 2554754.238 | 1151321.4142
15 | 2554765.3681 | 1151363.3695
16 | 2554754.701 | 1151303.2839
17 | 2554769.1732 | 1151378.2044
18 | 2554771.2235 | 1151399.8539
19 | 2554775.5976 | 1151409.9595
20 | 2554801.965 | 1151385.9821
21 | 2554752.125 | 1151406.5789
22 | 2554870.4828 | 1151414.9489
23 | 2554610.3341 | 1151288.6077
24 | 2554615.3193 | 1151296.114
25 | 2554580.5597 | 1151251.5149
26 | 2554636.8229 | 1151328.4926
27 | 2554549.0783 | 1151285.3037
28 | 2554664.1863 | 1151184.0598
29 | 2554655.1616 | 1151356.1057
30 | 2554568.9245 | 1151325.6907
31 | 2554672.5733 | 1151253.9772
32 | 2554656.736 | 1151358.736
33 | 2554652.8373 | 1151384.3161
34 | 2554574.1009 | 1151339.1387
35 | 2554712.2277 | 1151250.4653
36 | 2554713.3748 | 1151258.0606
37 | 2554665.5823 | 1151380.5582
38 | 2554648.6605 | 1151414.8457
39 | 2554747.3056 | 1151381.4991
40 | 2554740.1114 | 1151355.1922
41 | 2554734.4853 | 1151336.2747
42 | 2554751.1251 | 1151421.754
43 | 2554733.4621 | 1151332.8341
44 | 2554723.8221 | 1151300.4199
45 | 2554789.1171 | 1151405.2898
46 | 2554761.1849 | 1151427.0997
47 | 2554876.9075 | 1151408.5586
48 | 2554885.0429 | 1151400.4669
49 | 2554930.5062 | 1151413.5645
50 | 2554925.7187 | 1151419.9259
51 | 2554716.6901 | 1151276.0974
52 | 2554714.7857 | 1151265.8729
53 | 2555061.3424 | 1151279.9113
54 | 2555024.4596 | 1151264.3836
55 | 2554591.036 | 1151400.7352
56 | 2554598.8648 | 1151360.155
57 | 2554752.125 | 1151406.5789

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97727 | -0.43762 | 0.02017 | 0.0050552
1 | 0.97737 | -0.43575 | 0 | 0
2 | 0.97721 | -0.43882 | 0 | 0
3 | 0.97804 | -0.42246 | 0 | 0
4 | 0.97642 | -0.45432 | 0 | 0
5 | 0.97528 | -0.47682 | 0.021857 | 0.0054778
6 | 0.97955 | -0.39305 | 0.013035 | 0.0032668
7 | 0.97583 | -0.46596 | 0.0073308 | 0.0018373
8 | 0.97493 | -0.48365 | 0.0045384 | 0.0011374
9 | 0.98367 | -0.31272 | 0.01523 | 0.0038171
10 | 0.9758 | -0.46651 | 0 | 0
11 | 0.97561 | -0.47025 | 0 | 0
12 | 0.97547 | -0.47304 | 0.0014227 | 0.00035657
13 | 0.97546 | -0.47326 | 0 | 0
14 | 0.98317 | -0.32316 | 0.018846 | 0.0047232
15 | 0.98597 | -0.26858 | 0.022962 | 0.0057549
16 | 0.98235 | -0.33918 | 0.048965 | 0.012272
17 | 0.98728 | -0.24325 | 0.018846 | 0.0047232
18 | 0.98947 | -0.20072 | 0 | 0
19 | 0.98927 | -0.20471 | 0 | 0
20 | 0.98646 | -0.25872 | 0 | 0
21 | 0.99158 | -0.16026 | 0 | 0
22 | 0.9749 | -0.48418 | 0 | 0
23 | 0.97633 | -0.45347 | 0.0082204 | 0.0020602
24 | 0.97586 | -0.46287 | 0.013346 | 0.0033448
25 | 0.97905 | -0.40042 | 0 | 0
26 | 0.97403 | -0.49876 | 0.018785 | 0.0047078
27 | 0.97839 | -0.41332 | 0 | 0
28 | 0.98598 | -0.26612 | 0 | 0
29 | 0.97276 | -0.52375 | 0 | 0
30 | 0.97775 | -0.42597 | 0.0074748 | 0.0018734
31 | 0.99053 | -0.17903 | 0.0025524 | 0.00063969
32 | 0.97261 | -0.52669 | 0.01482 | 0.0037143
33 | 0.97197 | -0.53934 | 0.029885 | 0.00749
34 | 0.97764 | -0.42804 | 0.0078881 | 0.0019769
35 | 0.99314 | -0.12957 | 0 | 0
36 | 0.99364 | -0.12006 | 0 | 0
37 | 0.97179 | -0.54304 | 0.016319 | 0.00409
38 | 0.97101 | -0.55846 | 0.012785 | 0.0032043
39 | 0.99447 | -0.10485 | 0.0058802 | 0.0014737
40 | 0.99764 | -0.04469 | 0.0081727 | 0.0020483
41 | 1 | 0 | -0.4553 | -0.11666
42 | 0.99131 | -0.16556 | 0.019654 | 0.0049258
43 | 0.99969 | -0.005846 | 0.0081404 | 0.0020402
44 | 0.99688 | -0.058686 | 0.013304 | 0.0033344
45 | 0.98909 | -0.20822 | 0.012749 | 0.0031952
46 | 0.98912 | -0.20759 | 0.0072297 | 0.0018119
47 | 0.97485 | -0.48525 | 0.0021906 | 0.00054901
48 | 0.9748 | -0.48614 | 0.0016468 | 0.00041272
49 | 0.97467 | -0.48871 | 0.0026042 | 0.00065268
50 | 0.9747 | -0.4883 | 0 | 0
51 | 0.99493 | -0.095516 | 0.0047619 | 0.0011934
52 | 0.99416 | -0.11024 | 0.02038 | 0.0051076
53 | 0.97478 | -0.48665 | 0.0058537 | 0.0014671
54 | 0.975 | -0.48235 | 0 | 0
55 | 0.9705 | -0.56845 | 0 | 0
56 | 0.97018 | -0.57478 | 0.0081229 | 0.0020358
57 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.034804 | -0.0087292 | 0.034807 | 0.0087311 | 3.1015e-06 | 1.948e-06 | 0.052995 | 0.052995 | 0.052995 | 0.97727 | -0.43762 | 0.97737 | -0.43575 | 14.5591
1 | 0.014633 | 0.003674 | -0.014632 | -0.0036735 | 8.4162e-07 | 4.8201e-07 | 0.022283 | 0.022283 | 0.022283 | 0.97727 | -0.43762 | 0.97721 | -0.43882 | 6.1218
2 | -0.034807 | -0.0087311 | 0.034829 | 0.008745 | 2.2069e-05 | 1.3862e-05 | 0.052995 | 0.052995 | 0.052995 | 0.97737 | -0.43575 | 0.97804 | -0.42246 | 14.5591
3 | 0.014632 | 0.0036735 | -0.014622 | -0.0036673 | 1.0807e-05 | 6.1899e-06 | 0.022283 | 0.022284 | 0.022284 | 0.97721 | -0.43882 | 0.97642 | -0.45432 | 6.1219
4 | 0.032926 | 0.0082846 | -0.032841 | -0.0082311 | 8.5293e-05 | 5.3454e-05 | 0.050107 | 0.050107 | 0.050107 | 0.97804 | -0.42246 | 0.97528 | -0.47682 | 13.7657
5 | -0.067755 | -0.01703 | 0.06785 | 0.01709 | 9.5282e-05 | 6.068e-05 | 0.1031 | 0.1031 | 0.1031 | 0.97804 | -0.42246 | 0.97955 | -0.39305 | 28.3246
6 | 0.014622 | 0.0036673 | -0.014613 | -0.0036627 | 8.1091e-06 | 4.6454e-06 | 0.022284 | 0.022284 | 0.022284 | 0.97642 | -0.45432 | 0.97583 | -0.46596 | 6.1219
7 | 0.010985 | 0.0027534 | -0.010981 | -0.0027515 | 3.5728e-06 | 1.8635e-06 | 0.01676 | 0.01676 | 0.01676 | 0.97528 | -0.47682 | 0.97493 | -0.48365 | 4.6044
8 | -0.080885 | -0.020357 | 0.081197 | 0.020556 | 0.0003118 | 0.00019886 | 0.1229 | 0.1229 | 0.1229 | 0.97955 | -0.39305 | 0.98367 | -0.31272 | 33.7644
9 | 0.0072827 | 0.0018254 | -0.0072825 | -0.0018253 | 1.9048e-07 | 7.0453e-08 | 0.011105 | 0.011105 | 0.011105 | 0.97583 | -0.46596 | 0.9758 | -0.46651 | 3.0509
10 | 0.0064426 | 0.0016141 | -0.0064424 | -0.001614 | 1.6193e-07 | 4.7946e-08 | 0.009833 | 0.009833 | 0.009833 | 0.97493 | -0.48365 | 0.9749 | -0.48418 | 2.7014
11 | -0.096427 | -0.024373 | 0.096678 | 0.024533 | 0.0002504 | 0.00015985 | 0.14594 | 0.14594 | 0.14594 | 0.98367 | -0.31272 | 0.98646 | -0.25872 | 40.0937
12 | 0.0072825 | 0.0018253 | -0.0072812 | -0.0018249 | 1.2971e-06 | 4.7986e-07 | 0.011105 | 0.011105 | 0.011105 | 0.9758 | -0.46651 | 0.97561 | -0.47025 | 3.0509
13 | 0.0072812 | 0.0018249 | -0.0072803 | -0.0018245 | 9.6833e-07 | 3.5832e-07 | 0.011105 | 0.011106 | 0.011106 | 0.97561 | -0.47025 | 0.97547 | -0.47304 | 3.051
14 | 0.0058575 | 0.0014679 | -0.0058575 | -0.0014679 | 6.188e-08 | 1.3802e-08 | 0.0089352 | 0.0089353 | 0.0089353 | 0.97547 | -0.47304 | 0.97546 | -0.47326 | 2.4547
15 | 0.0058575 | 0.0014679 | -0.0058549 | -0.0014674 | 2.5357e-06 | 5.6613e-07 | 0.0089353 | 0.0089356 | 0.0089356 | 0.97546 | -0.47326 | 0.975 | -0.48235 | 2.4548
16 | -0.067848 | -0.017019 | 0.068025 | 0.017131 | 0.00017702 | 0.00011272 | 0.10269 | 0.10269 | 0.10269 | 0.98317 | -0.32316 | 0.98597 | -0.26858 | 28.2122
17 | 0.049003 | 0.012296 | -0.048965 | -0.012272 | 3.7414e-05 | 2.3715e-05 | 0.07417 | 0.07417 | 0.07417 | 0.98317 | -0.32316 | 0.98235 | -0.33918 | 20.3763
18 | -0.090987 | -0.022886 | 0.091098 | 0.022957 | 0.00011025 | 7.0361e-05 | 0.13735 | 0.13735 | 0.13735 | 0.98597 | -0.26858 | 0.98728 | -0.24325 | 37.7325
19 | -0.10994 | -0.02768 | 0.11017 | 0.027823 | 0.00022404 | 0.00014311 | 0.16575 | 0.16575 | 0.16575 | 0.98728 | -0.24325 | 0.98947 | -0.20072 | 45.5358
20 | 0.019986 | 0.0050109 | -0.019982 | -0.0050087 | 3.8026e-06 | 2.2895e-06 | 0.030056 | 0.030056 | 0.030056 | 0.98947 | -0.20072 | 0.98927 | -0.20471 | 8.2572
21 | 0.096948 | 0.024706 | -0.096678 | -0.024533 | 0.00027055 | 0.00017272 | 0.14594 | 0.14594 | 0.14594 | 0.98947 | -0.20072 | 0.98646 | -0.25872 | 40.0937
22 | -0.2271 | -0.057539 | 0.22754 | 0.057822 | 0.00044232 | 0.00028257 | 0.34175 | 0.34175 | 0.34175 | 0.98947 | -0.20072 | 0.99158 | -0.16026 | 46.9432
23 | 0.012751 | 0.0031964 | -0.012749 | -0.0031952 | 2.1348e-06 | 1.1676e-06 | 0.01918 | 0.01918 | 0.01918 | 0.98927 | -0.20471 | 0.98909 | -0.20822 | 5.2692
24 | 0.0072307 | 0.0018123 | -0.0072297 | -0.0018119 | 9.9341e-07 | 3.483e-07 | 0.010876 | 0.010876 | 0.010876 | 0.98927 | -0.20471 | 0.98912 | -0.20759 | 2.988
25 | 0.019659 | 0.0049288 | -0.019654 | -0.0049258 | 4.9649e-06 | 2.9814e-06 | 0.029502 | 0.029502 | 0.029502 | 0.99158 | -0.16026 | 0.99131 | -0.16556 | 8.1051
26 | -0.2472 | -0.062751 | 0.24786 | 0.063173 | 0.00066086 | 0.00042229 | 0.37125 | 0.37125 | 0.37125 | 0.99158 | -0.16026 | 0.99447 | -0.10485 | 50.9957
27 | 0.0064424 | 0.001614 | -0.0064421 | -0.0016139 | 3.2856e-07 | 9.7293e-08 | 0.009833 | 0.009833 | 0.009833 | 0.9749 | -0.48418 | 0.97485 | -0.48525 | 2.7014
28 | 0.11447 | 0.02884 | -0.11442 | -0.028808 | 5.1454e-05 | 3.2705e-05 | 0.17451 | 0.17451 | 0.17451 | 0.97633 | -0.45347 | 0.97586 | -0.46287 | 23.9714
29 | -0.12269 | -0.030901 | 0.123 | 0.031099 | 0.00031206 | 0.00019853 | 0.18704 | 0.18704 | 0.18704 | 0.97633 | -0.45347 | 0.97905 | -0.40042 | 25.6923
30 | 0.10107 | 0.025463 | -0.1009 | -0.025353 | 0.0001732 | 0.00010988 | 0.15416 | 0.15416 | 0.15416 | 0.97586 | -0.46287 | 0.97403 | -0.49876 | 21.1761
31 | 0.015382 | 0.0038614 | -0.015373 | -0.003856 | 9.456e-06 | 5.4722e-06 | 0.023381 | 0.023382 | 0.023382 | 0.97905 | -0.40042 | 0.97839 | -0.41332 | 6.4235
32 | -0.13838 | -0.03496 | 0.13928 | 0.035532 | 0.00089712 | 0.00057142 | 0.21042 | 0.21042 | 0.21042 | 0.97905 | -0.40042 | 0.98598 | -0.26612 | 28.904
33 | 0.082111 | 0.020645 | -0.082014 | -0.020583 | 9.7837e-05 | 6.1792e-05 | 0.12546 | 0.12547 | 0.12547 | 0.97403 | -0.49876 | 0.97276 | -0.52375 | 17.2342
34 | 0.015373 | 0.003856 | -0.015364 | -0.0038506 | 9.2664e-06 | 5.3632e-06 | 0.023382 | 0.023382 | 0.023382 | 0.97839 | -0.41332 | 0.97775 | -0.42597 | 6.4235
35 | -0.13928 | -0.035532 | 0.13987 | 0.035907 | 0.00058853 | 0.00037484 | 0.21042 | 0.21042 | 0.21042 | 0.98598 | -0.26612 | 0.99053 | -0.17903 | 28.9038
36 | 0.052106 | 0.013079 | -0.052099 | -0.013075 | 7.3044e-06 | 4.6367e-06 | 0.079713 | 0.079713 | 0.079713 | 0.97276 | -0.52375 | 0.97261 | -0.52669 | 21.8991
37 | 0.029908 | 0.0075039 | -0.029885 | -0.00749 | 2.222e-05 | 1.3869e-05 | 0.045752 | 0.045752 | 0.045752 | 0.97276 | -0.52375 | 0.97197 | -0.53934 | 12.5693
38 | 0.0078889 | 0.0019773 | -0.0078881 | -0.0019769 | 7.7891e-07 | 3.178e-07 | 0.012006 | 0.012006 | 0.012006 | 0.97775 | -0.42597 | 0.97764 | -0.42804 | 3.2984
39 | -0.14242 | -0.036546 | 0.14276 | 0.036765 | 0.00034264 | 0.00021826 | 0.21425 | 0.21425 | 0.21425 | 0.99053 | -0.17903 | 0.99314 | -0.12957 | 29.4304
40 | 0.037278 | 0.0093604 | -0.037249 | -0.0093421 | 2.9064e-05 | 1.8306e-05 | 0.057039 | 0.057039 | 0.057039 | 0.97261 | -0.52669 | 0.97179 | -0.54304 | 15.6701
41 | -0.14276 | -0.036765 | 0.14283 | 0.036807 | 6.6128e-05 | 4.2123e-05 | 0.21425 | 0.21425 | 0.21425 | 0.99314 | -0.12957 | 0.99364 | -0.12006 | 29.4304
42 | -0.14283 | -0.036807 | 0.1429 | 0.03685 | 6.8328e-05 | 4.3524e-05 | 0.21425 | 0.21425 | 0.21425 | 0.99364 | -0.12006 | 0.99416 | -0.11024 | 29.4304
43 | 0.02093 | 0.0052522 | -0.020915 | -0.0052428 | 1.5376e-05 | 9.3467e-06 | 0.032051 | 0.032051 | 0.032051 | 0.97179 | -0.54304 | 0.97101 | -0.55846 | 8.8052
44 | 0.0081292 | 0.0020385 | -0.0081253 | -0.0020368 | 3.8694e-06 | 1.6545e-06 | 0.012458 | 0.012458 | 0.012458 | 0.97101 | -0.55846 | 0.9705 | -0.56845 | 3.4226
45 | -0.25374 | -0.064647 | 0.25448 | 0.065119 | 0.00073887 | 0.00047217 | 0.38005 | 0.38005 | 0.38005 | 0.99447 | -0.10485 | 0.99764 | -0.04469 | 52.2043
46 | -0.26266 | -0.067167 | 0.26322 | 0.067531 | 0.00056933 | 0.00036385 | 0.39224 | 0.39224 | 0.39224 | 0.99764 | -0.04469 | 1 | 0 | 53.8786
47 | 0.19042 | 0.049126 | -0.19037 | -0.049092 | 5.4228e-05 | 3.4612e-05 | 0.28385 | 0.28385 | 0.28385 | 1 | 0 | 0.99969 | -0.005846 | 38.9906
48 | 0.18223 | 0.047051 | -0.18176 | -0.046753 | 0.0004682 | 0.00029876 | 0.27174 | 0.27174 | 0.27174 | 0.99969 | -0.005846 | 0.99688 | -0.058686 | 37.3263
49 | 0.16846 | 0.043418 | -0.16815 | -0.043226 | 0.00030151 | 0.00019231 | 0.25188 | 0.25188 | 0.25188 | 0.99688 | -0.058686 | 0.99493 | -0.095516 | 34.5985
50 | 0.0042515 | 0.0010649 | -0.0042513 | -0.0010649 | 1.812e-07 | -2.7083e-08 | 0.0064893 | 0.0064894 | 0.0064894 | 0.97485 | -0.48525 | 0.9748 | -0.48614 | 1.7828
51 | 0.0026046 | 0.00065222 | -0.0026043 | -0.00065261 | 2.6727e-07 | -3.9101e-07 | 0.0039756 | 0.0039758 | 0.0039758 | 0.9748 | -0.48614 | 0.9747 | -0.4883 | 1.0923
52 | -0.0026042 | -0.00065268 | 0.0026043 | 0.00065261 | 5.0661e-08 | -7.4096e-08 | 0.0039758 | 0.0039758 | 0.0039758 | 0.97467 | -0.48871 | 0.9747 | -0.4883 | 1.0923
53 | 0.16339 | 0.042032 | -0.16328 | -0.041958 | 0.00011685 | 7.4515e-05 | 0.24476 | 0.24476 | 0.24476 | 0.99493 | -0.095516 | 0.99416 | -0.11024 | 33.6203
54 | -0.0058537 | -0.0014671 | 0.0058549 | 0.0014674 | 1.1993e-06 | 2.6813e-07 | 0.0089358 | 0.0089356 | 0.0089358 | 0.97478 | -0.48665 | 0.975 | -0.48235 | 2.4549
55 | 0.0081253 | 0.0020368 | -0.0081229 | -0.0020358 | 2.4513e-06 | 1.0486e-06 | 0.012458 | 0.012458 | 0.012458 | 0.9705 | -0.56845 | 0.97018 | -0.57478 | 3.4227

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4591 | 0.11761

## res_load
| p_mw | q_mvar
0 | 0.02017 | 0.0050552
1 | 0.021857 | 0.0054778
2 | 0.013035 | 0.0032668
3 | 0.0073308 | 0.0018373
4 | 0.0045384 | 0.0011374
5 | 0.01523 | 0.0038171
6 | 0.0014227 | 0.00035657
7 | 0.018846 | 0.0047232
8 | 0.022962 | 0.0057549
9 | 0.048965 | 0.012272
10 | 0.018846 | 0.0047232
11 | 0.0082204 | 0.0020602
12 | 0.013346 | 0.0033448
13 | 0.018785 | 0.0047078
14 | 0.0074748 | 0.0018734
15 | 0.0025524 | 0.00063969
16 | 0.01482 | 0.0037143
17 | 0.029885 | 0.00749
18 | 0.0078881 | 0.0019769
19 | 0.016319 | 0.00409
20 | 0.012785 | 0.0032043
21 | 0.0058802 | 0.0014737
22 | 0.0081727 | 0.0020483
23 | 0.0037983 | 0.00095195
24 | 0.019654 | 0.0049258
25 | 0.0081404 | 0.0020402
26 | 0.013304 | 0.0033344
27 | 0.012749 | 0.0031952
28 | 0.0072297 | 0.0018119
29 | 0.0021906 | 0.00054901
30 | 0.0016468 | 0.00041272
31 | 0.0026042 | 0.00065268
32 | 0.0047619 | 0.0011934
33 | 0.02038 | 0.0051076
34 | 0.0058537 | 0.0014671
35 | 0.0081229 | 0.0020358

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1