## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2321-8_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2321-8_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2321-8_0_5_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_2321-8_0_5_node_1 | 0.4 | n |  | TRUE
4 | bus_LV_2321-8_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2321-8_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_2321-8_0_5_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2321-8_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2321-8_0_5_node_126 | 0.4 | n |  | TRUE
9 | bus_LV_2321-8_0_5_node_127 | 0.4 | n |  | TRUE
10 | bus_LV_2321-8_0_5_node_128 | 0.4 | n |  | TRUE
11 | bus_LV_2321-8_0_5_node_130 | 0.4 | n |  | TRUE
12 | bus_LV_2321-8_0_5_node_54 | 0.4 | n |  | TRUE
13 | bus_LV_2321-8_0_5_node_52 | 0.4 | n |  | TRUE
14 | bus_LV_2321-8_0_5_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2321-8_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2321-8_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2321-8_0_5_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2321-8_0_5_node_139 | 0.4 | n |  | TRUE
19 | bus_LV_2321-8_0_5_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2321-8_0_5_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2321-8_0_5_node_78 | 0.4 | n |  | TRUE
22 | bus_LV_2321-8_0_5_node_79 | 0.4 | n |  | TRUE
23 | bus_LV_2321-8_0_5_node_77 | 0.4 | n |  | TRUE
24 | bus_LV_2321-8_0_5_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_2321-8_0_5_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_2321-8_0_5_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_2321-8_0_5_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_2321-8_0_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_2321-8_0_5_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_2321-8_0_5_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_2321-8_0_5_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_2321-8_0_5_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2321-8_0_5_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_2321-8_0_5_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_2321-8_0_5_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_2321-8_0_5_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_2321-8_0_5_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_2321-8_0_5_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_2321-8_0_5_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_2321-8_0_5_node_102 | 0.4 | n |  | TRUE
41 | bus_LV_2321-8_0_5_node_101 | 0.4 | n |  | TRUE
42 | bus_LV_2321-8_0_5_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_2321-8_0_5_node_83 | 0.4 | n |  | TRUE
44 | bus_LV_2321-8_0_5_node_81 | 0.4 | n |  | TRUE
45 | bus_LV_2321-8_0_5_node_100 | 0.4 | n |  | TRUE
46 | bus_LV_2321-8_0_5_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_2321-8_0_5_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_2321-8_0_5_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_2321-8_0_5_node_98 | 0.4 | n |  | TRUE
50 | bus_LV_2321-8_0_5_node_80 | 0.4 | n |  | TRUE
51 | bus_LV_2321-8_0_5_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_2321-8_0_5_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_2321-8_0_5_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_2321-8_0_5_node_92 | 0.4 | n |  | TRUE
55 | bus_LV_2321-8_0_5_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_2321-8_0_5_node_93 | 0.4 | n |  | TRUE
57 | bus_LV_2321-8_0_5_node_90 | 0.4 | n |  | TRUE
58 | bus_LV_2321-8_0_5_node_135 | 0.4 | n |  | TRUE
59 | bus_LV_2321-8_0_5_node_41 | 0.4 | n |  | TRUE
60 | bus_LV_2321-8_0_5_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_2321-8_0_5_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_2321-8_0_5_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_2321-8_0_5_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_2321-8_0_5_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_2321-8_0_5_node_45 | 0.4 | n |  | TRUE
66 | bus_LV_2321-8_0_5_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_2321-8_0_5_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_2321-8_0_5_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_2321-8_0_5_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_2321-8_0_5_node_48 | 0.4 | n |  | TRUE
71 | bus_LV_2321-8_0_5_node_53 | 0.4 | n |  | TRUE
72 | bus_LV_2321-8_0_5_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_2321-8_0_5_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_2321-8_0_5_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_2321-8_0_5_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_2321-8_0_5_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_2321-8_0_5_node_51 | 0.4 | n |  | TRUE
78 | bus_LV_2321-8_0_5_node_129 | 0.4 | n |  | TRUE
79 | bus_LV_2321-8_0_5_node_131 | 0.4 | n |  | TRUE
80 | bus_LV_2321-8_0_5_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_2321-8_0_5_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_2321-8_0_5_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_2321-8_0_5_node_70 | 0.4 | n |  | TRUE
84 | bus_LV_2321-8_0_5_node_71 | 0.4 | n |  | TRUE
85 | bus_LV_2321-8_0_5_node_72 | 0.4 | n |  | TRUE
86 | bus_LV_2321-8_0_5_node_68 | 0.4 | n |  | TRUE
87 | bus_LV_2321-8_0_5_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_2321-8_0_5_node_119 | 0.4 | n |  | TRUE
89 | bus_LV_2321-8_0_5_node_117 | 0.4 | n |  | TRUE
90 | bus_LV_2321-8_0_5_node_65 | 0.4 | n |  | TRUE
91 | bus_LV_2321-8_0_5_node_67 | 0.4 | n |  | TRUE
92 | bus_LV_2321-8_0_5_node_69 | 0.4 | n |  | TRUE
93 | bus_LV_2321-8_0_5_node_106 | 0.4 | n |  | TRUE
94 | bus_LV_2321-8_0_5_node_107 | 0.4 | n |  | TRUE
95 | bus_LV_2321-8_0_5_node_124 | 0.4 | n |  | TRUE
96 | bus_LV_2321-8_0_5_node_125 | 0.4 | n |  | TRUE
97 | bus_LV_2321-8_0_5_node_109 | 0.4 | n |  | TRUE
98 | bus_LV_2321-8_0_5_node_105 | 0.4 | n |  | TRUE
99 | bus_LV_2321-8_0_5_node_108 | 0.4 | n |  | TRUE
100 | bus_LV_2321-8_0_5_node_73 | 0.4 | n |  | TRUE
101 | bus_LV_2321-8_0_5_node_74 | 0.4 | n |  | TRUE
102 | bus_LV_2321-8_0_5_node_75 | 0.4 | n |  | TRUE
103 | bus_LV_2321-8_0_5_node_76 | 0.4 | n |  | TRUE
104 | bus_LV_2321-8_0_5_node_82 | 0.4 | n |  | TRUE
105 | bus_LV_2321-8_0_5_node_113 | 0.4 | n |  | TRUE
106 | bus_LV_2321-8_0_5_node_115 | 0.4 | n |  | TRUE
107 | bus_LV_2321-8_0_5_node_112 | 0.4 | n |  | TRUE
108 | bus_LV_2321-8_0_5_node_118 | 0.4 | n |  | TRUE
109 | bus_LV_2321-8_0_5_node_114 | 0.4 | n |  | TRUE
110 | bus_LV_2321-8_0_5_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_2321-8_0_5_node_84 | 0.4 | n |  | TRUE
112 | bus_LV_2321-8_0_5_node_103 | 0.4 | n |  | TRUE
113 | bus_LV_2321-8_0_5_node_85 | 0.4 | n |  | TRUE
114 | bus_LV_2321-8_0_5_node_99 | 0.4 | n |  | TRUE
115 | bus_LV_2321-8_0_5_node_86 | 0.4 | n |  | TRUE
116 | bus_LV_2321-8_0_5_node_87 | 0.4 | n |  | TRUE
117 | bus_LV_2321-8_0_5_node_88 | 0.4 | n |  | TRUE
118 | bus_LV_2321-8_0_5_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_2321-8_0_5_node_123 | 0.4 | n |  | TRUE
120 | bus_LV_2321-8_0_5_node_121 | 0.4 | n |  | TRUE
121 | bus_LV_2321-8_0_5_node_91 | 0.4 | n |  | TRUE
122 | bus_LV_2321-8_0_5_node_95 | 0.4 | n |  | TRUE
123 | bus_LV_2321-8_0_5_node_94 | 0.4 | n |  | TRUE
124 | bus_LV_2321-8_0_5_node_96 | 0.4 | n |  | TRUE
125 | bus_LV_2321-8_0_5_node_97 | 0.4 | n |  | TRUE
126 | bus_LV_2321-8_0_5_node_138 | 0.4 | n |  | TRUE
127 | bus_LV_2321-8_0_5_node_110 | 0.4 | n |  | TRUE
128 | bus_LV_2321-8_0_5_node_111 | 0.4 | n |  | TRUE
129 | bus_LV_2321-8_0_5_node_133 | 0.4 | n |  | TRUE
130 | bus_LV_2321-8_0_5_node_134 | 0.4 | n |  | TRUE
131 | bus_LV_2321-8_0_5_node_116 | 0.4 | n |  | TRUE
132 | bus_LV_2321-8_0_5_node_120 | 0.4 | n |  | TRUE
133 | bus_LV_2321-8_0_5_node_122 | 0.4 | n |  | TRUE
134 | bus_LV_2321-8_0_5_node_136 | 0.4 | n |  | TRUE
135 | bus_MV_384_0_node_175 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2321-8_0_5_load_0 | 0 | 0.0053649 | 0.0013446 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2321-8_0_5_load_2 | 1 | 0.003138 | 0.00078645 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2321-8_0_5_load_5 | 2 | 0.0035742 | 0.00089578 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2321-8_0_5_load_1 | 3 | 0.0051452 | 0.0012895 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2321-8_0_5_load_3 | 4 | 0.0043716 | 0.0010956 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2321-8_0_5_load_4 | 6 | 0.0040448 | 0.0010137 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2321-8_0_5_load_7 | 7 | 0.0012286 | 0.00030791 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2321-8_0_5_load_126 | 8 | 0.0045014 | 0.0011281 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2321-8_0_5_load_128 | 10 | 0.004794 | 0.0012015 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2321-8_0_5_load_130 | 11 | 0.0064413 | 0.0016143 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2321-8_0_5_load_54 | 12 | 0.0043257 | 0.0010841 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2321-8_0_5_load_52 | 13 | 0.0031402 | 0.00078701 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2321-8_0_5_load_8 | 14 | 0.0024429 | 0.00061225 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2321-8_0_5_load_139 | 18 | 0.0059054 | 0.00148 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2321-8_0_5_load_14 | 20 | 0.0023972 | 0.00060078 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2321-8_0_5_load_77 | 23 | 0.0030189 | 0.00075661 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2321-8_0_5_load_24 | 24 | 0.0031464 | 0.00078856 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2321-8_0_5_load_23 | 25 | 0.0026412 | 0.00066195 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2321-8_0_5_load_17 | 26 | 0.0023935 | 0.00059988 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2321-8_0_5_load_18 | 27 | 0.0032869 | 0.00082378 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2321-8_0_5_load_19 | 28 | 0.00085063 | 0.00021319 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2321-8_0_5_load_21 | 30 | 0.002691 | 0.00067442 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2321-8_0_5_load_32 | 31 | 0.0010533 | 0.00026398 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2321-8_0_5_load_22 | 32 | 0.0015136 | 0.00037935 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2321-8_0_5_load_28 | 33 | 0.0035544 | 0.00089081 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2321-8_0_5_load_26 | 34 | 0.0019844 | 0.00049733 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2321-8_0_5_load_25 | 35 | 0.0033055 | 0.00082844 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2321-8_0_5_load_30 | 38 | 0.002704 | 0.00067769 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2321-8_0_5_load_102 | 40 | 0.0048744 | 0.0012216 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2321-8_0_5_load_101 | 41 | 0.0036397 | 0.0009122 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2321-8_0_5_load_83 | 43 | 0.0024981 | 0.00062607 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2321-8_0_5_load_81 | 44 | 0.0031077 | 0.00077887 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2321-8_0_5_load_100 | 45 | 0.0025849 | 0.00064783 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2321-8_0_5_load_35 | 47 | 0.0034379 | 0.00086163 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2321-8_0_5_load_36 | 48 | 0.0033182 | 0.00083161 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2321-8_0_5_load_98 | 49 | 0.0039794 | 0.00099733 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2321-8_0_5_load_38 | 51 | 0.004511 | 0.0011306 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2321-8_0_5_load_37 | 52 | 0.0026905 | 0.00067431 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2321-8_0_5_load_93 | 56 | 0.0028582 | 0.00071634 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2321-8_0_5_load_90 | 57 | 0.0036704 | 0.00091989 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2321-8_0_5_load_135 | 58 | 0.0039328 | 0.00098565 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2321-8_0_5_load_41 | 59 | 0.0036827 | 0.00092298 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2321-8_0_5_load_42 | 60 | 0.0032962 | 0.0008261 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2321-8_0_5_load_44 | 62 | 0.0054503 | 0.001366 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2321-8_0_5_load_56 | 64 | 0.0035292 | 0.0008845 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2321-8_0_5_load_50 | 66 | 0.0037399 | 0.0009373 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2321-8_0_5_load_47 | 67 | 0.0045319 | 0.0011358 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2321-8_0_5_load_55 | 68 | 0.0020092 | 0.00050355 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2321-8_0_5_load_57 | 69 | 0.0040695 | 0.0010199 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2321-8_0_5_load_48 | 70 | 0.0058757 | 0.0014726 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2321-8_0_5_load_49 | 72 | 0.0041377 | 0.001037 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2321-8_0_5_load_59 | 73 | 0.0021533 | 0.00053967 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2321-8_0_5_load_60 | 74 | 0.0042202 | 0.0010577 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2321-8_0_5_load_61 | 75 | 0.0037445 | 0.00093845 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2321-8_0_5_load_51 | 77 | 0.0034342 | 0.0008607 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2321-8_0_5_load_129 | 78 | 0.0052055 | 0.0013046 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2321-8_0_5_load_131 | 79 | 0.0030615 | 0.00076728 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2321-8_0_5_load_58 | 80 | 0.0037598 | 0.00094229 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2321-8_0_5_load_63 | 81 | 0.0040972 | 0.0010268 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2321-8_0_5_load_64 | 82 | 0.00408 | 0.0010226 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2321-8_0_5_load_70 | 83 | 0.0028678 | 0.00071873 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2321-8_0_5_load_71 | 84 | 0.0022393 | 0.00056123 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2321-8_0_5_load_72 | 85 | 0.0058925 | 0.0014768 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2321-8_0_5_load_68 | 86 | 0.0066821 | 0.0016747 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2321-8_0_5_load_66 | 87 | 0.0030182 | 0.00075644 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2321-8_0_5_load_119 | 88 | 0.0021076 | 0.00052821 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2321-8_0_5_load_117 | 89 | 0.0024182 | 0.00060607 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2321-8_0_5_load_65 | 90 | 0.0043454 | 0.0010891 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2321-8_0_5_load_67 | 91 | 0.0020653 | 0.00051761 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2321-8_0_5_load_69 | 92 | 0.0020156 | 0.00050516 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2321-8_0_5_load_106 | 93 | 0.0020939 | 0.00052478 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2321-8_0_5_load_107 | 94 | 0.0020987 | 0.00052598 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2321-8_0_5_load_124 | 95 | 0.0020956 | 0.00052521 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2321-8_0_5_load_125 | 96 | 0.0021043 | 0.0005274 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2321-8_0_5_load_105 | 98 | 0.0028897 | 0.00072423 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2321-8_0_5_load_108 | 99 | 0.0036678 | 0.00091925 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2321-8_0_5_load_73 | 100 | 0.0035273 | 0.00088401 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2321-8_0_5_load_74 | 101 | 0.0041371 | 0.0010369 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2321-8_0_5_load_75 | 102 | 0.0040316 | 0.0010104 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2321-8_0_5_load_76 | 103 | 0.0034137 | 0.00085556 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2321-8_0_5_load_113 | 105 | 0.0032786 | 0.00082168 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2321-8_0_5_load_112 | 107 | 0.0032781 | 0.00082157 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2321-8_0_5_load_118 | 108 | 0.0022263 | 0.00055797 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2321-8_0_5_load_114 | 109 | 0.0030296 | 0.00075929 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2321-8_0_5_load_89 | 110 | 0.0024051 | 0.00060277 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2321-8_0_5_load_84 | 111 | 0.0036916 | 0.00092521 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2321-8_0_5_load_103 | 112 | 0.0032788 | 0.00082174 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2321-8_0_5_load_99 | 114 | 0.0060631 | 0.0015196 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2321-8_0_5_load_86 | 115 | 0.0019362 | 0.00048526 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2321-8_0_5_load_87 | 116 | 0.0019559 | 0.00049021 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2321-8_0_5_load_88 | 117 | 0.0024206 | 0.00060667 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2321-8_0_5_load_104 | 118 | 0.0060121 | 0.0015068 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2321-8_0_5_load_123 | 119 | 0.0022432 | 0.00056221 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2321-8_0_5_load_91 | 121 | 0.0028247 | 0.00070795 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2321-8_0_5_load_95 | 122 | 0.0020773 | 0.00052063 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2321-8_0_5_load_94 | 123 | 0.0020535 | 0.00051465 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2321-8_0_5_load_96 | 124 | 0.0021737 | 0.00054478 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2321-8_0_5_load_97 | 125 | 0.0016554 | 0.00041487 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2321-8_0_5_load_138 | 126 | 0.0016317 | 0.00040895 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2321-8_0_5_load_111 | 128 | 0.0032223 | 0.00080758 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2321-8_0_5_load_133 | 129 | 0.0010179 | 0.00025511 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2321-8_0_5_load_134 | 130 | 0.00029946 | 7.5052e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2321-8_0_5_load_116 | 131 | 0.0030291 | 0.00075917 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2321-8_0_5_load_120 | 132 | 0.002418 | 0.00060601 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2321-8_0_5_load_122 | 133 | 0.0024204 | 0.0006066 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2321-8_0_5_load_136 | 134 | 0.0018093 | 0.00045344 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 120 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2321-8_0_5_line_0 |  | 0 | 1 | 0.00092291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2321-8_0_5_line_1 |  | 0 | 2 | 0.031605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2321-8_0_5_line_2 |  | 2 | 5 | 0.036736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2321-8_0_5_line_3 |  | 3 | 4 | 0.017007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2321-8_0_5_line_4 |  | 3 | 5 | 0.020429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2321-8_0_5_line_5 |  | 4 | 6 | 0.017882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2321-8_0_5_line_6 |  | 5 | 7 | 0.015049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2321-8_0_5_line_7 |  | 6 | 12 | 0.018433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2321-8_0_5_line_8 |  | 7 | 8 | 0.025875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2321-8_0_5_line_9 |  | 8 | 9 | 0.016077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2321-8_0_5_line_10 |  | 9 | 78 | 0.011856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2321-8_0_5_line_11 |  | 9 | 10 | 0.01551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2321-8_0_5_line_12 |  | 10 | 11 | 0.010858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2321-8_0_5_line_13 |  | 12 | 13 | 0.0024274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2321-8_0_5_line_14 |  | 13 | 77 | 0.025019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2321-8_0_5_line_15 |  | 14 | 15 | 0.059066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2321-8_0_5_line_16 |  | 15 | 16 | 0.001979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2321-8_0_5_line_17 |  | 15 | 17 | 0.04578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2321-8_0_5_line_18 |  | 16 | 18 | 0.033688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2321-8_0_5_line_19 |  | 17 | 19 | 0.028688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2321-8_0_5_line_20 |  | 17 | 20 | 0.02202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2321-8_0_5_line_21 |  | 19 | 24 | 0.017788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2321-8_0_5_line_22 |  | 21 | 22 | 0.02755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2321-8_0_5_line_23 |  | 21 | 23 | 0.002115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2321-8_0_5_line_24 |  | 22 | 105 | 0.022197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2321-8_0_5_line_25 |  | 22 | 106 | 0.025357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2321-8_0_5_line_26 |  | 23 | 31 | 0.010184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2321-8_0_5_line_27 |  | 24 | 25 | 0.0049274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2321-8_0_5_line_28 |  | 25 | 32 | 0.021486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2321-8_0_5_line_29 |  | 26 | 27 | 0.0082076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2321-8_0_5_line_30 |  | 26 | 28 | 0.022774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2321-8_0_5_line_31 |  | 27 | 29 | 0.022014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2321-8_0_5_line_32 |  | 28 | 30 | 0.0057045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2321-8_0_5_line_33 |  | 29 | 31 | 0.0041249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2321-8_0_5_line_34 |  | 30 | 32 | 0.002509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2321-8_0_5_line_35 |  | 33 | 34 | 0.010611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2321-8_0_5_line_36 |  | 34 | 35 | 0.01904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2321-8_0_5_line_37 |  | 35 | 36 | 0.015586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2321-8_0_5_line_38 |  | 36 | 37 | 0.007798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2321-8_0_5_line_39 |  | 36 | 38 | 0.047644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2321-8_0_5_line_40 |  | 36 | 39 | 0.050709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2321-8_0_5_line_41 |  | 37 | 40 | 0.022705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2321-8_0_5_line_42 |  | 37 | 41 | 0.014279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2321-8_0_5_line_43 |  | 38 | 42 | 0.014854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2321-8_0_5_line_44 |  | 39 | 43 | 0.017707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2321-8_0_5_line_45 |  | 39 | 44 | 0.0089162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2321-8_0_5_line_46 |  | 41 | 45 | 0.020777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2321-8_0_5_line_47 |  | 42 | 46 | 0.034044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2321-8_0_5_line_48 |  | 42 | 47 | 0.017032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2321-8_0_5_line_49 |  | 42 | 48 | 0.021287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2321-8_0_5_line_50 |  | 43 | 49 | 0.0024288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2321-8_0_5_line_51 |  | 44 | 50 | 0.016757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2321-8_0_5_line_52 |  | 46 | 51 | 0.011397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2321-8_0_5_line_53 |  | 46 | 52 | 0.013092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2321-8_0_5_line_54 |  | 47 | 53 | 0.014998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2321-8_0_5_line_55 |  | 48 | 54 | 0.015232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2321-8_0_5_line_56 |  | 49 | 114 | 0.018964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2321-8_0_5_line_57 |  | 50 | 104 | 0.004827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2321-8_0_5_line_58 |  | 50 | 103 | 0.03707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2321-8_0_5_line_59 |  | 53 | 55 | 0.029102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2321-8_0_5_line_60 |  | 54 | 56 | 0.0098529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2321-8_0_5_line_61 |  | 54 | 57 | 0.013508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2321-8_0_5_line_62 |  | 55 | 58 | 0.043745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2321-8_0_5_line_63 |  | 56 | 122 | 0.0032826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2321-8_0_5_line_64 |  | 57 | 121 | 0.021148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2321-8_0_5_line_65 |  | 59 | 60 | 0.0015484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2321-8_0_5_line_66 |  | 59 | 61 | 0.020242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2321-8_0_5_line_67 |  | 60 | 62 | 0.028873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2321-8_0_5_line_68 |  | 61 | 63 | 0.029044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2321-8_0_5_line_69 |  | 62 | 64 | 0.0037431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2321-8_0_5_line_70 |  | 63 | 68 | 0.035482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2321-8_0_5_line_71 |  | 64 | 69 | 0.031062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2321-8_0_5_line_72 |  | 65 | 66 | 0.028384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2321-8_0_5_line_73 |  | 65 | 67 | 0.01587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2321-8_0_5_line_74 |  | 67 | 70 | 0.025482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2321-8_0_5_line_75 |  | 68 | 71 | 0.037721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2321-8_0_5_line_76 |  | 69 | 80 | 0.011922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2321-8_0_5_line_77 |  | 70 | 72 | 0.013609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2321-8_0_5_line_78 |  | 71 | 77 | 0.016722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2321-8_0_5_line_79 |  | 72 | 73 | 0.01839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2321-8_0_5_line_80 |  | 73 | 74 | 0.021279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2321-8_0_5_line_81 |  | 74 | 83 | 0.012431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2321-8_0_5_line_82 |  | 75 | 76 | 0.014624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2321-8_0_5_line_83 |  | 76 | 85 | 0.048213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2321-8_0_5_line_84 |  | 76 | 86 | 0.025806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2321-8_0_5_line_85 |  | 78 | 79 | 0.019452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2321-8_0_5_line_86 |  | 80 | 81 | 0.015514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2321-8_0_5_line_87 |  | 81 | 82 | 0.013238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2321-8_0_5_line_88 |  | 82 | 88 | 0.021922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2321-8_0_5_line_89 |  | 83 | 84 | 0.027132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2321-8_0_5_line_90 |  | 84 | 95 | 0.00036283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2321-8_0_5_line_91 |  | 86 | 87 | 0.012527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2321-8_0_5_line_92 |  | 87 | 90 | 0.018711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2321-8_0_5_line_93 |  | 88 | 89 | 0.00050383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2321-8_0_5_line_94 |  | 89 | 106 | 0.015838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2321-8_0_5_line_95 |  | 90 | 91 | 0.011145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2321-8_0_5_line_96 |  | 91 | 92 | 0.00079643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2321-8_0_5_line_97 |  | 92 | 93 | 0.017047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2321-8_0_5_line_98 |  | 93 | 94 | 0.00045364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2321-8_0_5_line_99 |  | 94 | 116 | 0.0099546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2321-8_0_5_line_100 |  | 95 | 96 | 1.0396e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2321-8_0_5_line_101 |  | 96 | 133 | 0.00028763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2321-8_0_5_line_102 |  | 97 | 98 | 0.032722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2321-8_0_5_line_103 |  | 97 | 99 | 0.014647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2321-8_0_5_line_104 |  | 98 | 118 | 0.024655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2321-8_0_5_line_105 |  | 99 | 127 | 0.087172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2321-8_0_5_line_106 |  | 100 | 101 | 0.00037893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2321-8_0_5_line_107 |  | 100 | 102 | 0.022849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2321-8_0_5_line_108 |  | 102 | 103 | 0.0013741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2321-8_0_5_line_109 |  | 104 | 110 | 0.019658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2321-8_0_5_line_110 |  | 104 | 111 | 0.0081539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2321-8_0_5_line_111 |  | 105 | 107 | 0.039765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2321-8_0_5_line_112 |  | 106 | 108 | 0.018983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_2321-8_0_5_line_113 |  | 106 | 109 | 0.020251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2321-8_0_5_line_114 |  | 108 | 132 | 0.01059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
115 | LV_2321-8_0_5_line_115 |  | 109 | 131 | 0.028323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2321-8_0_5_line_116 |  | 110 | 112 | 0.018212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2321-8_0_5_line_117 |  | 111 | 113 | 0.032053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2321-8_0_5_line_118 |  | 113 | 115 | 0.021234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2321-8_0_5_line_119 |  | 113 | 116 | 0.012275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2321-8_0_5_line_120 |  | 113 | 117 | 0.017971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_2321-8_0_5_line_121 |  | 115 | 118 | 0.024743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2321-8_0_5_line_122 |  | 117 | 119 | 0.015131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
123 | LV_2321-8_0_5_line_123 |  | 119 | 120 | 0.020651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
124 | LV_2321-8_0_5_line_124 |  | 120 | 133 | 0.016557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2321-8_0_5_line_125 |  | 120 | 132 | 0.023037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_2321-8_0_5_line_126 |  | 122 | 123 | 0.020574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2321-8_0_5_line_127 |  | 123 | 124 | 0.015439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2321-8_0_5_line_128 |  | 124 | 125 | 0.022891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2321-8_0_5_line_129 |  | 125 | 126 | 0.0070078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2321-8_0_5_line_130 |  | 127 | 128 | 0.053314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2321-8_0_5_line_131 |  | 128 | 129 | 0.12678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2321-8_0_5_line_132 |  | 129 | 130 | 0.037328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2321-8_0_5_line_133 |  | 130 | 134 | 0.47208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2321-8_0_5_trafo_121 | 0.63 MVA 20/0.4 kV | 135 | 120 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2554998.906 | 1151164.6122 | 2554998.986 | 1151163.6928
1 | 2554998.986 | 1151163.6928 | 2554970.0051 | 1151151.0835
2 | 2554988.3665 | 1151119.3567 | 2554978.8594 | 1151138.1598 | 2554970.0051 | 1151151.0835
3 | 2555008.2719 | 1151123.954 | 2555009.5965 | 1151122.4215 | 2555020.2696 | 1151111.909
4 | 2555008.2719 | 1151123.954 | 2554988.3665 | 1151119.3567
5 | 2555030.6756 | 1151097.765 | 2555028.4285 | 1151103.5264 | 2555021.2767 | 1151110.917 | 2555020.2696 | 1151111.909
6 | 2554988.3665 | 1151119.3567 | 2554987.1263 | 1151107.4931 | 2554987.9053 | 1151104.4706
7 | 2555029.202 | 1151079.5248 | 2555031.1246 | 1151096.6137 | 2555030.6756 | 1151097.765
8 | 2554976.5727 | 1151084.5747 | 2554978.248 | 1151086.2709 | 2554986.1093 | 1151091.6148 | 2554988.534 | 1151094.5982 | 2554989.3713 | 1151098.7829 | 2554987.9053 | 1151104.4706
9 | 2554966.7121 | 1151071.9721 | 2554971.8828 | 1151079.8264 | 2554976.5727 | 1151084.5747
10 | 2554966.7121 | 1151071.9721 | 2554974.6947 | 1151063.2065
11 | 2554966.7121 | 1151071.9721 | 2554957.1874 | 1151084.2127
12 | 2554950.5195 | 1151092.782 | 2554957.1874 | 1151084.2127
13 | 2555029.202 | 1151079.5248 | 2555028.9306 | 1151077.1126
14 | 2555026.1335 | 1151052.2504 | 2555028.9306 | 1151077.1126
15 | 2555106.7894 | 1151248.7156 | 2555092.4314 | 1151245.9437 | 2555077.7922 | 1151240.4724 | 2555050.4303 | 1151231.4393
16 | 2555106.7516 | 1151246.7371 | 2555106.7894 | 1151248.7156
17 | 2555106.5632 | 1151294.452 | 2555105.9237 | 1151276.6698 | 2555106.6134 | 1151262.1461 | 2555106.8591 | 1151252.9173 | 2555106.7894 | 1151248.7156
18 | 2555097.1429 | 1151214.9925 | 2555098.1993 | 1151224.9008 | 2555102.6725 | 1151231.8932 | 2555106.1794 | 1151243.095 | 2555106.7516 | 1151246.7371
19 | 2555106.5632 | 1151294.452 | 2555134.364 | 1151301.8372
20 | 2555106.5632 | 1151294.452 | 2555088.7368 | 1151289.7161 | 2555085.3708 | 1151288.5114
21 | 2555134.364 | 1151301.8372 | 2555133.2324 | 1151284.0854
22 | 2555129.0681 | 1151193.9321 | 2555126.2423 | 1151192.7303 | 2555123.2586 | 1151190.9406 | 2555121.4111 | 1151188.1529 | 2555119.7026 | 1151183.4299 | 2555117.6444 | 1151170.9499
23 | 2555129.0681 | 1151193.9321 | 2555131.0152 | 1151194.7579
24 | 2555117.6444 | 1151170.9499 | 2555107.5684 | 1151170.147 | 2555095.4875 | 1151169.6941
25 | 2555112.4087 | 1151146.1429 | 2555117.6444 | 1151170.9499
26 | 2555131.0152 | 1151194.7579 | 2555138.5464 | 1151197.9523 | 2555140.4307 | 1151198.6323
27 | 2555133.2324 | 1151284.0854 | 2555132.9189 | 1151279.168
28 | 2555131.9767 | 1151257.7269 | 2555131.7559 | 1151260.9244 | 2555132.9189 | 1151279.168
29 | 2555143.7921 | 1151220.7095 | 2555140.7213 | 1151228.321
30 | 2555132.609 | 1151249.5378 | 2555132.7197 | 1151248.155 | 2555140.7213 | 1151228.321
31 | 2555144.3107 | 1151200.0326 | 2555146.6948 | 1151203.7611 | 2555147.411 | 1151208.1914 | 2555146.269 | 1151214.5699 | 2555143.7921 | 1151220.7095
32 | 2555132.609 | 1151249.5378 | 2555132.1537 | 1151255.2241
33 | 2555144.3107 | 1151200.0326 | 2555140.4307 | 1151198.6323
34 | 2555132.1537 | 1151255.2241 | 2555132.123 | 1151255.6078 | 2555131.9767 | 1151257.7269
35 | 2555200.1796 | 1151222.47 | 2555209.995 | 1151226.5006
36 | 2555227.6064 | 1151233.7356 | 2555226.7999 | 1151233.4014 | 2555209.995 | 1151226.5006
37 | 2555242.0054 | 1151239.7025 | 2555227.6064 | 1151233.7356
38 | 2555242.0054 | 1151239.7025 | 2555249.8258 | 1151239.622
39 | 2555242.0054 | 1151239.7025 | 2555241.4997 | 1151247.0323 | 2555237.2405 | 1151257.4027 | 2555225.7085 | 1151284.1052
40 | 2555231.6431 | 1151190.1652 | 2555241.5747 | 1151232.3686 | 2555242.0054 | 1151239.7025
41 | 2555249.8258 | 1151239.622 | 2555257.7397 | 1151248.9902 | 2555261.9984 | 1151252.9717 | 2555266.6292 | 1151253.3374
42 | 2555249.8258 | 1151239.622 | 2555263.9712 | 1151237.6715
43 | 2555219.8192 | 1151297.7422 | 2555225.7085 | 1151284.1052
44 | 2555231.6431 | 1151190.1652 | 2555248.6842 | 1151185.3563
45 | 2555231.6431 | 1151190.1652 | 2555229.2893 | 1151181.5654
46 | 2555284.618 | 1151235.3679 | 2555268.3195 | 1151237.072 | 2555263.9712 | 1151237.6715
47 | 2555219.8192 | 1151297.7422 | 2555188.2995 | 1151284.6593
48 | 2555219.8192 | 1151297.7422 | 2555213.0632 | 1151313.3772
49 | 2555219.8192 | 1151297.7422 | 2555239.7345 | 1151305.2597
50 | 2555251.0217 | 1151184.6967 | 2555248.6842 | 1151185.3563
51 | 2555224.8655 | 1151165.4029 | 2555229.2893 | 1151181.5654
52 | 2555177.7518 | 1151280.269 | 2555188.2995 | 1151284.6593
53 | 2555188.2995 | 1151284.6593 | 2555193.3282 | 1151272.572
54 | 2555207.1828 | 1151327.1738 | 2555212.4025 | 1151314.9063 | 2555213.0632 | 1151313.3772
55 | 2555253.9852 | 1151310.6389 | 2555239.7345 | 1151305.2597
56 | 2555269.2727 | 1151179.5463 | 2555251.0217 | 1151184.6967
57 | 2555223.6946 | 1151160.7204 | 2555224.8655 | 1151165.4029
58 | 2555224.8655 | 1151165.4029 | 2555188.9505 | 1151174.5851
59 | 2555207.1828 | 1151327.1738 | 2555225.8296 | 1151334.9166 | 2555234.0157 | 1151338.6131
60 | 2555253.9852 | 1151310.6389 | 2555263.167 | 1151314.213
61 | 2555253.9852 | 1151310.6389 | 2555258.939 | 1151298.0723
62 | 2555234.0157 | 1151338.6131 | 2555273.8776 | 1151356.6316
63 | 2555266.226 | 1151315.4038 | 2555263.167 | 1151314.213
64 | 2555258.939 | 1151298.0723 | 2555266.6947 | 1151278.3977
65 | 2555086.5891 | 1151005.2236 | 2555086.7909 | 1151006.7588
66 | 2555083.812 | 1150985.1733 | 2555085.7241 | 1150998.6438 | 2555086.5891 | 1151005.2236
67 | 2555086.7909 | 1151006.7588 | 2555090.554 | 1151035.3856
68 | 2555054.7439 | 1150986.0911 | 2555063.563 | 1150985.058 | 2555083.812 | 1150985.1733
69 | 2555091.0419 | 1151039.0968 | 2555090.554 | 1151035.3856
70 | 2555054.7439 | 1150986.0911 | 2555046.5688 | 1150989.076 | 2555036.6371 | 1150995.2979 | 2555030.2855 | 1151000.9261 | 2555026.4894 | 1151006.292
71 | 2555091.0419 | 1151039.0968 | 2555091.5186 | 1151042.7233 | 2555095.1952 | 1151069.8795
72 | 2555154.9989 | 1150982.6183 | 2555170.1554 | 1150987.3966 | 2555181.5753 | 1150992.4603
73 | 2555154.9989 | 1150982.6183 | 2555155.3938 | 1150996.4447 | 2555155.3305 | 1150998.4817
74 | 2555155.3305 | 1150998.4817 | 2555154.5384 | 1151023.9513
75 | 2555015.1782 | 1151041.6713 | 2555016.3805 | 1151031.0569 | 2555019.1423 | 1151019.5969 | 2555023.3436 | 1151010.7387 | 2555026.4894 | 1151006.292
76 | 2555095.1952 | 1151069.8795 | 2555096.7947 | 1151081.694
77 | 2555154.1154 | 1151037.5537 | 2555154.5384 | 1151023.9513
78 | 2555015.1782 | 1151041.6713 | 2555022.8734 | 1151044.304 | 2555026.1335 | 1151052.2504 | 2555026.1335 | 1151052.2504
79 | 2555154.1154 | 1151037.5537 | 2555154.0259 | 1151040.4332 | 2555153.4259 | 1151055.9303
80 | 2555153.4259 | 1151055.9303 | 2555152.6027 | 1151077.1933
81 | 2555152.6027 | 1151077.1933 | 2555152.1218 | 1151089.6148
82 | 2555224.2038 | 1151019.9883 | 2555212.4076 | 1151011.344
83 | 2555224.2038 | 1151019.9883 | 2555241.4288 | 1151032.4998 | 2555262.3603 | 1151049.4333
84 | 2555224.2038 | 1151019.9883 | 2555211.9133 | 1151042.6799
85 | 2554987.792 | 1151048.8245 | 2554974.6947 | 1151063.2065
86 | 2555096.7947 | 1151081.694 | 2555097.0185 | 1151083.3476 | 2555099.4851 | 1151096.9719
87 | 2555101.842 | 1151109.9984 | 2555100.8374 | 1151104.4411 | 2555099.4851 | 1151096.9719
88 | 2555101.842 | 1151109.9984 | 2555102.3025 | 1151112.5454 | 2555105.6327 | 1151130.9078 | 2555105.8039 | 1151131.5571
89 | 2555158.2523 | 1151115.8742 | 2555153.1393 | 1151098.5142 | 2555151.9732 | 1151093.4537 | 2555152.1218 | 1151089.6148
90 | 2555158.3548 | 1151116.2222 | 2555158.2523 | 1151115.8742
91 | 2555205.9469 | 1151053.6954 | 2555211.9133 | 1151042.6799
92 | 2555205.5738 | 1151071.6654 | 2555204.7651 | 1151068.8139 | 2555203.3777 | 1151059.7974 | 2555205.6012 | 1151054.3336 | 2555205.9469 | 1151053.6954
93 | 2555105.9324 | 1151132.0442 | 2555105.8039 | 1151131.5571
94 | 2555112.4087 | 1151146.1429 | 2555108.2631 | 1151140.8822 | 2555105.9324 | 1151132.0442
95 | 2555205.5738 | 1151071.6654 | 2555208.6145 | 1151082.3875
96 | 2555208.8317 | 1151083.1537 | 2555208.6145 | 1151082.3875
97 | 2555208.8317 | 1151083.1537 | 2555213.4827 | 1151099.554
98 | 2555213.6064 | 1151099.9904 | 2555213.4827 | 1151099.554
99 | 2555216.3224 | 1151109.5674 | 2555213.6064 | 1151099.9904
100 | 2555158.3577 | 1151116.2322 | 2555158.3548 | 1151116.2222
101 | 2555158.439 | 1151116.5081 | 2555158.3577 | 1151116.2322
102 | 2555313.2846 | 1151090.0171 | 2555307.3287 | 1151094.1747 | 2555298.7911 | 1151096.9285 | 2555288.3157 | 1151100.2192 | 2555283.1359 | 1151102.0909
103 | 2555313.2846 | 1151090.0171 | 2555319.7935 | 1151092.1031 | 2555327.5739 | 1151092.8012
104 | 2555259.875 | 1151110.2602 | 2555269.1863 | 1151107.1317 | 2555283.1359 | 1151102.0909
105 | 2555327.5739 | 1151092.8012 | 2555414.2159 | 1151102.3962
106 | 2555165.1154 | 1151180.6789 | 2555165.4825 | 1151180.5851
107 | 2555165.4825 | 1151180.5851 | 2555187.6192 | 1151174.9255
108 | 2555187.6192 | 1151174.9255 | 2555188.9505 | 1151174.5851
109 | 2555223.6946 | 1151160.7204 | 2555242.8452 | 1151156.2844
110 | 2555223.6946 | 1151160.7204 | 2555221.7445 | 1151152.8031
111 | 2555058.1644 | 1151181.3837 | 2555058.9742 | 1151181.1825 | 2555064.2557 | 1151179.2531 | 2555070.2923 | 1151175.6617 | 2555085.3474 | 1151170.0129 | 2555088.2827 | 1151169.424 | 2555095.4875 | 1151169.6941
112 | 2555112.4087 | 1151146.1429 | 2555121.3868 | 1151143.808 | 2555130.8283 | 1151141.5568
113 | 2555112.4087 | 1151146.1429 | 2555104.784 | 1151143.6763 | 2555092.8411 | 1151146.3449
114 | 2555130.8283 | 1151141.5568 | 2555138.618 | 1151139.6994 | 2555141.1167 | 1151139.05
115 | 2555065.1994 | 1151152.5211 | 2555092.8411 | 1151146.3449
116 | 2555260.5876 | 1151152.1746 | 2555242.8452 | 1151156.2844
117 | 2555215.3197 | 1151121.4402 | 2555217.0857 | 1151133.8891 | 2555221.7445 | 1151152.8031
118 | 2555215.3197 | 1151121.4402 | 2555233.65 | 1151117.5239 | 2555236.0682 | 1151116.9286
119 | 2555215.3197 | 1151121.4402 | 2555217.3773 | 1151113.2874 | 2555216.3224 | 1151109.5674
120 | 2555215.3197 | 1151121.4402 | 2555204.8776 | 1151120.9511 | 2555197.6275 | 1151122.9371
121 | 2555236.0682 | 1151116.9286 | 2555250.8803 | 1151113.2823 | 2555259.875 | 1151110.2602
122 | 2555183.0344 | 1151126.9346 | 2555197.6275 | 1151122.9371
123 | 2555163.1168 | 1151132.3906 | 2555183.0344 | 1151126.9346
124 | 2555163.1168 | 1151132.3906 | 2555158.439 | 1151116.5081
125 | 2555163.1168 | 1151132.3906 | 2555157.5547 | 1151134.7778 | 2555141.1167 | 1151139.05
126 | 2555266.226 | 1151315.4038 | 2555285.3984 | 1151322.867 | 2555285.3984 | 1151322.867
127 | 2555293.5386 | 1151310.1574 | 2555292.2927 | 1151314.9005 | 2555285.3984 | 1151322.867
128 | 2555292.9151 | 1151287.8255 | 2555292.5276 | 1151289.7413 | 2555295.1537 | 1151299.1822 | 2555294.6363 | 1151305.9784 | 2555293.5386 | 1151310.1574
129 | 2555294.3043 | 1151280.9568 | 2555292.9151 | 1151287.8255
130 | 2555414.2159 | 1151102.3962 | 2555429.9718 | 1151114.5856 | 2555442.455 | 1151122.2304 | 2555455.3019 | 1151128.2271 | 2555459.5446 | 1151129.9465
131 | 2555584.07 | 1151153.7308 | 2555459.5446 | 1151129.9465
132 | 2555584.07 | 1151153.7308 | 2555584.5769 | 1151149.8928 | 2555586.4623 | 1151137.0611 | 2555587.7095 | 1151127.2023 | 2555587.3249 | 1151119.8125 | 2555587.5419 | 1151116.6704
133 | 2555587.5419 | 1151116.6704 | 2555871.2456 | 1150739.3471

## bus_geodata
| x | y | coords
0 | 2554998.986 | 1151163.6928
1 | 2554998.906 | 1151164.6122
2 | 2554970.0051 | 1151151.0835
3 | 2555008.2719 | 1151123.954
4 | 2555020.2696 | 1151111.909
5 | 2554988.3665 | 1151119.3567
6 | 2555030.6756 | 1151097.765
7 | 2554987.9053 | 1151104.4706
8 | 2554976.5727 | 1151084.5747
9 | 2554966.7121 | 1151071.9721
10 | 2554957.1874 | 1151084.2127
11 | 2554950.5195 | 1151092.782
12 | 2555029.202 | 1151079.5248
13 | 2555028.9306 | 1151077.1126
14 | 2555050.4303 | 1151231.4393
15 | 2555106.7894 | 1151248.7156
16 | 2555106.7516 | 1151246.7371
17 | 2555106.5632 | 1151294.452
18 | 2555097.1429 | 1151214.9925
19 | 2555134.364 | 1151301.8372
20 | 2555085.3708 | 1151288.5114
21 | 2555129.0681 | 1151193.9321
22 | 2555117.6444 | 1151170.9499
23 | 2555131.0152 | 1151194.7579
24 | 2555133.2324 | 1151284.0854
25 | 2555132.9189 | 1151279.168
26 | 2555140.7213 | 1151228.321
27 | 2555143.7921 | 1151220.7095
28 | 2555132.609 | 1151249.5378
29 | 2555144.3107 | 1151200.0326
30 | 2555132.1537 | 1151255.2241
31 | 2555140.4307 | 1151198.6323
32 | 2555131.9767 | 1151257.7269
33 | 2555200.1796 | 1151222.47
34 | 2555209.995 | 1151226.5006
35 | 2555227.6064 | 1151233.7356
36 | 2555242.0054 | 1151239.7025
37 | 2555249.8258 | 1151239.622
38 | 2555225.7085 | 1151284.1052
39 | 2555231.6431 | 1151190.1652
40 | 2555266.6292 | 1151253.3374
41 | 2555263.9712 | 1151237.6715
42 | 2555219.8192 | 1151297.7422
43 | 2555248.6842 | 1151185.3563
44 | 2555229.2893 | 1151181.5654
45 | 2555284.618 | 1151235.3679
46 | 2555188.2995 | 1151284.6593
47 | 2555213.0632 | 1151313.3772
48 | 2555239.7345 | 1151305.2597
49 | 2555251.0217 | 1151184.6967
50 | 2555224.8655 | 1151165.4029
51 | 2555177.7518 | 1151280.269
52 | 2555193.3282 | 1151272.572
53 | 2555207.1828 | 1151327.1738
54 | 2555253.9852 | 1151310.6389
55 | 2555234.0157 | 1151338.6131
56 | 2555263.167 | 1151314.213
57 | 2555258.939 | 1151298.0723
58 | 2555273.8776 | 1151356.6316
59 | 2555086.5891 | 1151005.2236
60 | 2555086.7909 | 1151006.7588
61 | 2555083.812 | 1150985.1733
62 | 2555090.554 | 1151035.3856
63 | 2555054.7439 | 1150986.0911
64 | 2555091.0419 | 1151039.0968
65 | 2555154.9989 | 1150982.6183
66 | 2555181.5753 | 1150992.4603
67 | 2555155.3305 | 1150998.4817
68 | 2555026.4894 | 1151006.292
69 | 2555095.1952 | 1151069.8795
70 | 2555154.5384 | 1151023.9513
71 | 2555015.1782 | 1151041.6713
72 | 2555154.1154 | 1151037.5537
73 | 2555153.4259 | 1151055.9303
74 | 2555152.6027 | 1151077.1933
75 | 2555212.4076 | 1151011.344
76 | 2555224.2038 | 1151019.9883
77 | 2555026.1335 | 1151052.2504
78 | 2554974.6947 | 1151063.2065
79 | 2554987.792 | 1151048.8245
80 | 2555096.7947 | 1151081.694
81 | 2555099.4851 | 1151096.9719
82 | 2555101.842 | 1151109.9984
83 | 2555152.1218 | 1151089.6148
84 | 2555158.2523 | 1151115.8742
85 | 2555262.3603 | 1151049.4333
86 | 2555211.9133 | 1151042.6799
87 | 2555205.9469 | 1151053.6954
88 | 2555105.8039 | 1151131.5571
89 | 2555105.9324 | 1151132.0442
90 | 2555205.5738 | 1151071.6654
91 | 2555208.6145 | 1151082.3875
92 | 2555208.8317 | 1151083.1537
93 | 2555213.4827 | 1151099.5539
94 | 2555213.6064 | 1151099.9904
95 | 2555158.3548 | 1151116.2222
96 | 2555158.3577 | 1151116.2322
97 | 2555313.2846 | 1151090.0171
98 | 2555283.1359 | 1151102.0909
99 | 2555327.5739 | 1151092.8012
100 | 2555165.4825 | 1151180.5851
101 | 2555165.1154 | 1151180.6789
102 | 2555187.6192 | 1151174.9255
103 | 2555188.9505 | 1151174.5851
104 | 2555223.6946 | 1151160.7204
105 | 2555095.4875 | 1151169.6941
106 | 2555112.4087 | 1151146.1429
107 | 2555058.1644 | 1151181.3837
108 | 2555130.8283 | 1151141.5568
109 | 2555092.8411 | 1151146.3449
110 | 2555242.8452 | 1151156.2844
111 | 2555221.7445 | 1151152.8031
112 | 2555260.5876 | 1151152.1746
113 | 2555215.3197 | 1151121.4402
114 | 2555269.2727 | 1151179.5463
115 | 2555236.0682 | 1151116.9286
116 | 2555216.3224 | 1151109.5674
117 | 2555197.6275 | 1151122.9371
118 | 2555259.875 | 1151110.2602
119 | 2555183.0344 | 1151126.9346
120 | 2555163.1168 | 1151132.3906
121 | 2555266.6947 | 1151278.3977
122 | 2555266.226 | 1151315.4038
123 | 2555285.3984 | 1151322.867
124 | 2555293.5386 | 1151310.1574
125 | 2555292.9151 | 1151287.8255
126 | 2555294.3043 | 1151280.9569
127 | 2555414.2159 | 1151102.3962
128 | 2555459.5446 | 1151129.9465
129 | 2555584.07 | 1151153.7308
130 | 2555587.5419 | 1151116.6704
131 | 2555065.1994 | 1151152.5211
132 | 2555141.1167 | 1151139.05
133 | 2555158.439 | 1151116.5081
134 | 2555871.2456 | 1150739.3471
135 | 2555112.4087 | 1151146.1429

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97171 | -0.54555 | 0.0053649 | 0.0013446
1 | 0.9717 | -0.5456 | 0.003138 | 0.00078645
2 | 0.97196 | -0.54059 | 0.0035742 | 0.00089578
3 | 0.97308 | -0.51837 | 0.0051452 | 0.0012895
4 | 0.97376 | -0.50508 | 0.0043716 | 0.0010956
5 | 0.97237 | -0.53241 | 0 | 0
6 | 0.97454 | -0.4897 | 0.0040448 | 0.0010137
7 | 0.97202 | -0.53941 | 0.0012286 | 0.00030791
8 | 0.97144 | -0.55088 | 0.0045014 | 0.0011281
9 | 0.97114 | -0.55667 | 0 | 0
10 | 0.97098 | -0.55989 | 0.004794 | 0.0012015
11 | 0.97092 | -0.56118 | 0.0064413 | 0.0016143
12 | 0.97541 | -0.47251 | 0.0043257 | 0.0010841
13 | 0.97554 | -0.47005 | 0.0031402 | 0.00078701
14 | 0.99169 | -0.15916 | 0.0024429 | 0.00061225
15 | 0.99183 | -0.1566 | 0 | 0
16 | 0.99181 | -0.15681 | 0 | 0
17 | 0.99217 | -0.14983 | 0 | 0
18 | 0.99163 | -0.16034 | 0.0059054 | 0.00148
19 | 0.99246 | -0.14437 | 0 | 0
20 | 0.99213 | -0.15077 | 0.0023972 | 0.00060078
21 | 0.99477 | -0.099611 | 0 | 0
22 | 0.99556 | -0.08441 | 0 | 0
23 | 0.99471 | -0.10078 | 0.0030189 | 0.00075661
24 | 0.99263 | -0.14099 | 0.0031464 | 0.00078856
25 | 0.99269 | -0.13978 | 0.0026412 | 0.00066195
26 | 0.99362 | -0.12191 | 0.0023935 | 0.00059988
27 | 0.9938 | -0.11844 | 0.0032869 | 0.00082378
28 | 0.99317 | -0.1306 | 0.00085063 | 0.00021319
29 | 0.99434 | -0.10785 | 0 | 0
30 | 0.99306 | -0.13269 | 0.002691 | 0.00067442
31 | 0.99445 | -0.10586 | 0.0010533 | 0.00026398
32 | 0.99302 | -0.13349 | 0.0015136 | 0.00037935
33 | 0.98731 | -0.24413 | 0.0035544 | 0.00089081
34 | 0.98734 | -0.24345 | 0.0019844 | 0.00049733
35 | 0.98744 | -0.24157 | 0.0033055 | 0.00082844
36 | 0.98756 | -0.2391 | 0 | 0
37 | 0.98749 | -0.24065 | 0 | 0
38 | 0.98583 | -0.27284 | 0.002704 | 0.00067769
39 | 0.99034 | -0.18533 | 0 | 0
40 | 0.98738 | -0.24263 | 0.0048744 | 0.0012216
41 | 0.9874 | -0.24224 | 0.0036397 | 0.0009122
42 | 0.98533 | -0.28266 | 0 | 0
43 | 0.99014 | -0.18928 | 0.0024981 | 0.00062607
44 | 0.99093 | -0.17393 | 0.0031077 | 0.00077887
45 | 0.98735 | -0.2432 | 0.0025849 | 0.00064783
46 | 0.9851 | -0.28706 | 0 | 0
47 | 0.98521 | -0.28491 | 0.0034379 | 0.00086163
48 | 0.98489 | -0.29117 | 0.0033182 | 0.00083161
49 | 0.99011 | -0.18972 | 0.0039794 | 0.00099733
50 | 0.99209 | -0.1516 | 0 | 0
51 | 0.98505 | -0.28799 | 0.004511 | 0.0011306
52 | 0.98507 | -0.2877 | 0.0026905 | 0.00067431
53 | 0.98516 | -0.28597 | 0 | 0
54 | 0.98462 | -0.29636 | 0 | 0
55 | 0.98505 | -0.28803 | 0 | 0
56 | 0.98451 | -0.29857 | 0.0028582 | 0.00071634
57 | 0.98454 | -0.29794 | 0.0036704 | 0.00091989
58 | 0.98489 | -0.29112 | 0.0039328 | 0.00098565
59 | 0.98508 | -0.28449 | 0.0036827 | 0.00092298
60 | 0.98518 | -0.28262 | 0.0032962 | 0.0008261
61 | 0.98387 | -0.30771 | 0 | 0
62 | 0.98708 | -0.24599 | 0.0054503 | 0.001366
63 | 0.98215 | -0.34113 | 0 | 0
64 | 0.98735 | -0.24089 | 0.0035292 | 0.0008845
65 | 0.99736 | -0.050873 | 0 | 0
66 | 0.99726 | -0.052733 | 0.0037399 | 0.0009373
67 | 0.99741 | -0.049833 | 0.0045319 | 0.0011358
68 | 0.98004 | -0.38212 | 0.0020092 | 0.00050355
69 | 0.98965 | -0.1967 | 0.0040695 | 0.0010199
70 | 0.9976 | -0.04614 | 0.0058757 | 0.0014726
71 | 0.97786 | -0.4245 | 0 | 0
72 | 0.99778 | -0.042768 | 0.0041377 | 0.001037
73 | 0.99808 | -0.036882 | 0.0021533 | 0.00053967
74 | 0.99848 | -0.029274 | 0.0042202 | 0.0010577
75 | 0.99397 | -0.11561 | 0.0037445 | 0.00093845
76 | 0.99402 | -0.11465 | 0 | 0
77 | 0.9769 | -0.44335 | 0.0034342 | 0.0008607
78 | 0.97105 | -0.55848 | 0.0052055 | 0.0013046
79 | 0.971 | -0.55958 | 0.0030615 | 0.00076728
80 | 0.99058 | -0.17893 | 0.0037598 | 0.00094229
81 | 0.99184 | -0.15483 | 0.0040972 | 0.0010268
82 | 0.99297 | -0.13335 | 0.00408 | 0.0010226
83 | 0.99876 | -0.023916 | 0.0028678 | 0.00071873
84 | 0.99943 | -0.010872 | 0.0022393 | 0.00056123
85 | 0.99376 | -0.11966 | 0.0058925 | 0.0014768
86 | 0.99425 | -0.11026 | 0.0066821 | 0.0016747
87 | 0.99444 | -0.10666 | 0.0030182 | 0.00075644
88 | 0.99492 | -0.096312 | 0.0021076 | 0.00052821
89 | 0.99496 | -0.095444 | 0.0024182 | 0.00060607
90 | 0.99477 | -0.10028 | 0.0043454 | 0.0010891
91 | 0.99501 | -0.095631 | 0.0020653 | 0.00051761
92 | 0.99502 | -0.09527 | 0.0020156 | 0.00050516
93 | 0.99546 | -0.08694 | 0.0020939 | 0.00052478
94 | 0.99547 | -0.086702 | 0.0020987 | 0.00052598
95 | 0.99944 | -0.010684 | 0.0020956 | 0.00052521
96 | 0.99944 | -0.010678 | 0.0021043 | 0.0005274
97 | 0.99472 | -0.10123 | 0 | 0
98 | 0.99502 | -0.095441 | 0.0028897 | 0.00072423
99 | 0.99459 | -0.10382 | 0.0036678 | 0.00091925
100 | 0.9914 | -0.16492 | 0.0035273 | 0.00088401
101 | 0.9914 | -0.16494 | 0.0041371 | 0.0010369
102 | 0.99156 | -0.16181 | 0.0040316 | 0.0010104
103 | 0.99158 | -0.16153 | 0.0034137 | 0.00085556
104 | 0.99249 | -0.14389 | 0 | 0
105 | 0.99543 | -0.08697 | 0.0032786 | 0.00082168
106 | 0.99644 | -0.06752 | 0 | 0
107 | 0.99531 | -0.089264 | 0.0032781 | 0.00082157
108 | 0.9977 | -0.043514 | 0.0022263 | 0.00055797
109 | 0.99633 | -0.069674 | 0.0030296 | 0.00075929
110 | 0.99239 | -0.14587 | 0.0024051 | 0.00060277
111 | 0.99321 | -0.13005 | 0.0036916 | 0.00092521
112 | 0.99233 | -0.14692 | 0.0032788 | 0.00082174
113 | 0.99614 | -0.073792 | 0 | 0
114 | 0.99001 | -0.19176 | 0.0060631 | 0.0015196
115 | 0.99573 | -0.081584 | 0.0019362 | 0.00048526
116 | 0.99576 | -0.081107 | 0.0019559 | 0.00049021
117 | 0.99741 | -0.049447 | 0.0024206 | 0.00060667
118 | 0.99531 | -0.089829 | 0.0060121 | 0.0015068
119 | 0.9985 | -0.028678 | 0.0022432 | 0.00056221
120 | 1 | 0 | -0.34965 | -0.088617
121 | 0.98449 | -0.29901 | 0.0028247 | 0.00070795
122 | 0.98448 | -0.29913 | 0.0020773 | 0.00052063
123 | 0.98434 | -0.30191 | 0.0020535 | 0.00051465
124 | 0.98426 | -0.30343 | 0.0021737 | 0.00054478
125 | 0.98419 | -0.30479 | 0.0016554 | 0.00041487
126 | 0.98418 | -0.30499 | 0.0016317 | 0.00040895
127 | 0.99408 | -0.11361 | 0 | 0
128 | 0.99377 | -0.11961 | 0.0032223 | 0.00080758
129 | 0.99341 | -0.12665 | 0.0010179 | 0.00025511
130 | 0.99334 | -0.12805 | 0.00029946 | 7.5052e-05
131 | 0.99625 | -0.071181 | 0.0030291 | 0.00075917
132 | 0.99842 | -0.029942 | 0.002418 | 0.00060601
133 | 0.99945 | -0.010508 | 0.0024204 | 0.0006066
134 | 0.99256 | -0.14321 | 0.0018093 | 0.00045344
135 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.003138 | 0.00078644 | -0.003138 | -0.00078645 | 7.9917e-09 | -6.3178e-09 | 0.0048053 | 0.0048053 | 0.0048053 | 0.97171 | -0.54555 | 0.9717 | -0.5456 | 1.3201
1 | -0.0085029 | -0.002131 | 0.0085049 | 0.0021319 | 2.0094e-06 | 8.944e-07 | 0.013021 | 0.013021 | 0.013021 | 0.97171 | -0.54555 | 0.97196 | -0.54059 | 3.5772
2 | -0.012079 | -0.0030277 | 0.012084 | 0.0030302 | 4.711e-06 | 2.5596e-06 | 0.018493 | 0.018492 | 0.018493 | 0.97196 | -0.54059 | 0.97237 | -0.53241 | 5.0804
3 | -0.042516 | -0.010677 | 0.042543 | 0.010694 | 2.6963e-05 | 1.7045e-05 | 0.065022 | 0.065022 | 0.065022 | 0.97308 | -0.51837 | 0.97376 | -0.50508 | 17.8633
4 | 0.037371 | 0.0093875 | -0.037346 | -0.0093718 | 2.5026e-05 | 1.5763e-05 | 0.057155 | 0.057155 | 0.057155 | 0.97308 | -0.51837 | 0.97237 | -0.53241 | 15.7018
5 | -0.046915 | -0.01179 | 0.046949 | 0.011812 | 3.4476e-05 | 2.1842e-05 | 0.071703 | 0.071703 | 0.071703 | 0.97376 | -0.50508 | 0.97454 | -0.4897 | 19.6986
6 | 0.025262 | 0.0063415 | -0.025254 | -0.0063363 | 8.4358e-06 | 5.2123e-06 | 0.038662 | 0.038662 | 0.038662 | 0.97237 | -0.53241 | 0.97202 | -0.53941 | 10.6215
7 | -0.050994 | -0.012825 | 0.051036 | 0.012852 | 4.1923e-05 | 2.6601e-05 | 0.077879 | 0.077879 | 0.077879 | 0.97454 | -0.4897 | 0.97541 | -0.47251 | 21.3952
8 | 0.024025 | 0.0060284 | -0.024012 | -0.0060203 | 1.3127e-05 | 8.081e-06 | 0.036781 | 0.036782 | 0.036782 | 0.97202 | -0.53941 | 0.97144 | -0.55088 | 10.1048
9 | 0.019511 | 0.0048922 | -0.019505 | -0.0048889 | 5.3852e-06 | 3.2475e-06 | 0.029887 | 0.029887 | 0.029887 | 0.97144 | -0.55088 | 0.97114 | -0.55667 | 8.2106
10 | 0.0082678 | 0.0020721 | -0.0082671 | -0.0020718 | 7.135e-07 | 3.0996e-07 | 0.012668 | 0.012668 | 0.012668 | 0.97114 | -0.55667 | 0.97105 | -0.55848 | 3.4803
11 | 0.011237 | 0.0028169 | -0.011236 | -0.0028159 | 1.7244e-06 | 9.1171e-07 | 0.017218 | 0.017219 | 0.017219 | 0.97114 | -0.55667 | 0.97098 | -0.55989 | 4.7304
12 | 0.0064417 | 0.0016145 | -0.0064413 | -0.0016143 | 3.968e-07 | 1.1966e-07 | 0.0098718 | 0.0098719 | 0.0098719 | 0.97098 | -0.55989 | 0.97092 | -0.56118 | 2.7121
13 | -0.055362 | -0.013936 | 0.055368 | 0.01394 | 6.4961e-06 | 4.1272e-06 | 0.084477 | 0.084477 | 0.084477 | 0.97541 | -0.47251 | 0.97554 | -0.47005 | 23.2081
14 | -0.058508 | -0.014727 | 0.058583 | 0.014775 | 7.4763e-05 | 4.7535e-05 | 0.089267 | 0.089267 | 0.089267 | 0.97554 | -0.47005 | 0.9769 | -0.44335 | 24.524
15 | -0.0024429 | -0.00061225 | 0.0024432 | 0.00061167 | 2.9758e-07 | -5.7173e-07 | 0.0036655 | 0.0036652 | 0.0036655 | 0.99169 | -0.15916 | 0.99183 | -0.1566 | 1.007
16 | 0.0059065 | 0.0014803 | -0.0059064 | -0.0014802 | 5.8275e-08 | 1.1756e-08 | 0.0088614 | 0.0088614 | 0.0088614 | 0.99183 | -0.1566 | 0.99181 | -0.15681 | 2.4344
17 | -0.0083497 | -0.0020919 | 0.0083524 | 0.0020931 | 2.6938e-06 | 1.133e-06 | 0.012527 | 0.012526 | 0.012527 | 0.99183 | -0.1566 | 0.99217 | -0.14983 | 3.4414
18 | 0.0059064 | 0.0014802 | -0.0059054 | -0.00148 | 9.9201e-07 | 2.0021e-07 | 0.0088614 | 0.0088615 | 0.0088615 | 0.99181 | -0.15681 | 0.99163 | -0.16034 | 2.4345
19 | -0.01075 | -0.0026936 | 0.010752 | 0.002695 | 2.796e-06 | 1.4189e-06 | 0.016122 | 0.016121 | 0.016122 | 0.99217 | -0.14983 | 0.99246 | -0.14437 | 4.429
20 | 0.0023973 | 0.00060057 | -0.0023972 | -0.00060078 | 1.0674e-07 | -2.1606e-07 | 0.0035952 | 0.0035953 | 0.0035953 | 0.99217 | -0.14983 | 0.99213 | -0.15077 | 0.98772
21 | -0.010752 | -0.002695 | 0.010754 | 0.0026959 | 1.7337e-06 | 8.7964e-07 | 0.016121 | 0.016121 | 0.016121 | 0.99246 | -0.14437 | 0.99263 | -0.14099 | 4.429
22 | -0.031396 | -0.007886 | 0.031419 | 0.0079003 | 2.2792e-05 | 1.4229e-05 | 0.04697 | 0.04697 | 0.04697 | 0.99477 | -0.099611 | 0.99556 | -0.08441 | 12.9038
23 | 0.031396 | 0.007886 | -0.031394 | -0.0078849 | 1.7498e-06 | 1.0924e-06 | 0.04697 | 0.04697 | 0.04697 | 0.99477 | -0.099611 | 0.99471 | -0.10078 | 12.9038
24 | 0.0065578 | 0.0016432 | -0.006557 | -0.001643 | 7.997e-07 | 2.2321e-07 | 0.0098015 | 0.0098016 | 0.0098016 | 0.99556 | -0.08441 | 0.99543 | -0.08697 | 2.6928
25 | -0.037977 | -0.0095435 | 0.038007 | 0.0095627 | 3.0647e-05 | 1.9284e-05 | 0.056771 | 0.056771 | 0.056771 | 0.99556 | -0.08441 | 0.99644 | -0.06752 | 15.5964
26 | 0.028375 | 0.0071283 | -0.028369 | -0.0071241 | 6.8829e-06 | 4.2729e-06 | 0.042454 | 0.042454 | 0.042454 | 0.99471 | -0.10078 | 0.99445 | -0.10586 | 11.6631
27 | -0.013901 | -0.0034845 | 0.013901 | 0.0034849 | 8.0234e-07 | 4.498e-07 | 0.020838 | 0.020838 | 0.020838 | 0.99263 | -0.14099 | 0.99269 | -0.13978 | 5.7247
28 | -0.016543 | -0.0041469 | 0.016548 | 0.0041498 | 4.9543e-06 | 2.8929e-06 | 0.024797 | 0.024797 | 0.024797 | 0.99269 | -0.13978 | 0.99302 | -0.13349 | 6.8124
29 | -0.024008 | -0.0060237 | 0.024012 | 0.0060262 | 3.9792e-06 | 2.4404e-06 | 0.035956 | 0.035956 | 0.035956 | 0.99362 | -0.12191 | 0.9938 | -0.11844 | 9.8781
30 | 0.021614 | 0.0054238 | -0.021606 | -0.0054184 | 8.9498e-06 | 5.433e-06 | 0.032372 | 0.032372 | 0.032372 | 0.99362 | -0.12191 | 0.99317 | -0.1306 | 8.8933
31 | -0.027299 | -0.0068499 | 0.027313 | 0.0068585 | 1.3794e-05 | 8.5429e-06 | 0.040878 | 0.040878 | 0.040878 | 0.9938 | -0.11844 | 0.99434 | -0.10785 | 11.2301
32 | 0.020755 | 0.0052052 | -0.020753 | -0.005204 | 2.0687e-06 | 1.2501e-06 | 0.031097 | 0.031097 | 0.031097 | 0.99317 | -0.1306 | 0.99306 | -0.13269 | 8.5432
33 | -0.027313 | -0.0068585 | 0.027315 | 0.0068601 | 2.5847e-06 | 1.6007e-06 | 0.040878 | 0.040878 | 0.040878 | 0.99434 | -0.10785 | 0.99445 | -0.10586 | 11.2301
34 | 0.018062 | 0.0045295 | -0.018061 | -0.0045291 | 6.8922e-07 | 4.0864e-07 | 0.027065 | 0.027065 | 0.027065 | 0.99306 | -0.13269 | 0.99302 | -0.13349 | 7.4355
35 | -0.0035544 | -0.00089081 | 0.0035545 | 0.00089075 | 1.1419e-07 | -6.2619e-08 | 0.005357 | 0.0053569 | 0.005357 | 0.98731 | -0.24413 | 0.98734 | -0.24345 | 1.4717
36 | -0.0055389 | -0.0013881 | 0.0055394 | 0.0013882 | 4.9751e-07 | 7.4881e-08 | 0.0083475 | 0.0083475 | 0.0083475 | 0.98734 | -0.24345 | 0.98744 | -0.24157 | 2.2933
37 | -0.0088449 | -0.0022166 | 0.0088459 | 0.0022171 | 1.0384e-06 | 4.6515e-07 | 0.013329 | 0.013329 | 0.013329 | 0.98744 | -0.24157 | 0.98756 | -0.2391 | 3.6617
38 | 0.011101 | 0.002782 | -0.0111 | -0.0027816 | 8.1811e-07 | 4.2383e-07 | 0.016726 | 0.016726 | 0.016726 | 0.98756 | -0.2391 | 0.98749 | -0.24065 | 4.5951
39 | 0.039642 | 0.0099702 | -0.039578 | -0.00993 | 6.377e-05 | 4.0204e-05 | 0.059743 | 0.059743 | 0.059743 | 0.98756 | -0.2391 | 0.98583 | -0.27284 | 16.4129
40 | -0.059589 | -0.014969 | 0.059742 | 0.015067 | 0.00015334 | 9.7485e-05 | 0.089798 | 0.089798 | 0.089798 | 0.98756 | -0.2391 | 0.99034 | -0.18533 | 24.6697
41 | 0.0048749 | 0.0012216 | -0.0048744 | -0.0012216 | 4.5945e-07 | 3.612e-09 | 0.0073458 | 0.0073459 | 0.0073459 | 0.98749 | -0.24065 | 0.98738 | -0.24263 | 2.0181
42 | 0.0062252 | 0.00156 | -0.0062247 | -0.0015598 | 4.7118e-07 | 1.189e-07 | 0.0093805 | 0.0093806 | 0.0093806 | 0.98749 | -0.24065 | 0.9874 | -0.24224 | 2.5771
43 | 0.036874 | 0.0092523 | -0.036857 | -0.0092415 | 1.7258e-05 | 1.0856e-05 | 0.055662 | 0.055662 | 0.055662 | 0.98583 | -0.27284 | 0.98533 | -0.28266 | 15.2917
44 | 0.012544 | 0.0031445 | -0.012541 | -0.0031432 | 2.3587e-06 | 1.2818e-06 | 0.018848 | 0.018848 | 0.018848 | 0.99034 | -0.18533 | 0.99014 | -0.18928 | 5.1779
45 | -0.072286 | -0.018211 | 0.072325 | 0.018236 | 3.9467e-05 | 2.5144e-05 | 0.10865 | 0.10865 | 0.10865 | 0.99034 | -0.18533 | 0.99093 | -0.17393 | 29.8476
46 | 0.002585 | 0.00064764 | -0.0025849 | -0.00064783 | 1.1824e-07 | -1.9007e-07 | 0.0038955 | 0.0038956 | 0.0038956 | 0.9874 | -0.24224 | 0.98735 | -0.2432 | 1.0702
47 | 0.0072034 | 0.0018053 | -0.0072019 | -0.0018048 | 1.5108e-06 | 5.3338e-07 | 0.010878 | 0.010878 | 0.010878 | 0.98533 | -0.28266 | 0.9851 | -0.28706 | 2.9886
48 | 0.0073727 | 0.0018472 | -0.0073719 | -0.0018469 | 7.9177e-07 | 2.8981e-07 | 0.011134 | 0.011134 | 0.011134 | 0.98533 | -0.28266 | 0.98521 | -0.28491 | 3.0588
49 | 0.022281 | 0.005589 | -0.022272 | -0.0055835 | 9.0386e-06 | 5.5137e-06 | 0.03365 | 0.03365 | 0.03365 | 0.98533 | -0.28266 | 0.98489 | -0.29117 | 9.2444
50 | 0.010043 | 0.0025171 | -0.010043 | -0.002517 | 2.0749e-07 | 1.0156e-07 | 0.015093 | 0.015094 | 0.015094 | 0.99014 | -0.18928 | 0.99011 | -0.18972 | 4.1466
51 | -0.075433 | -0.019015 | 0.075514 | 0.019067 | 8.0682e-05 | 5.142e-05 | 0.11331 | 0.11331 | 0.11331 | 0.99093 | -0.17393 | 0.99209 | -0.1516 | 31.1296
52 | 0.0045112 | 0.0011306 | -0.004511 | -0.0011306 | 1.9846e-07 | -1.8078e-08 | 0.0068143 | 0.0068144 | 0.0068144 | 0.9851 | -0.28706 | 0.98505 | -0.28799 | 1.8721
53 | 0.0026906 | 0.00067419 | -0.0026905 | -0.00067431 | 8.1091e-08 | -1.1477e-07 | 0.0040642 | 0.0040642 | 0.0040642 | 0.9851 | -0.28706 | 0.98507 | -0.2877 | 1.1165
54 | 0.003934 | 0.00098528 | -0.0039338 | -0.00098534 | 1.9853e-07 | -6.3907e-08 | 0.0059414 | 0.0059415 | 0.0059415 | 0.98521 | -0.28491 | 0.98516 | -0.28597 | 1.6323
55 | 0.018953 | 0.0047519 | -0.018949 | -0.0047491 | 4.6841e-06 | 2.8041e-06 | 0.028636 | 0.028636 | 0.028636 | 0.98489 | -0.29117 | 0.98462 | -0.29636 | 7.8672
56 | 0.0060637 | 0.0015197 | -0.0060631 | -0.0015196 | 5.9059e-07 | 1.341e-07 | 0.009113 | 0.0091131 | 0.0091131 | 0.99011 | -0.18972 | 0.99001 | -0.19176 | 2.5036
57 | -0.090632 | -0.022858 | 0.090665 | 0.02288 | 3.3474e-05 | 2.1361e-05 | 0.13599 | 0.13599 | 0.13599 | 0.99209 | -0.1516 | 0.99249 | -0.14389 | 37.3593
58 | 0.015118 | 0.0037915 | -0.015111 | -0.0037874 | 7.1483e-06 | 4.0965e-06 | 0.022676 | 0.022676 | 0.022676 | 0.99209 | -0.1516 | 0.99158 | -0.16153 | 6.2298
59 | 0.0039338 | 0.00098534 | -0.0039334 | -0.00098546 | 3.8526e-07 | -1.2394e-07 | 0.0059415 | 0.0059416 | 0.0059416 | 0.98516 | -0.28597 | 0.98505 | -0.28803 | 1.6323
60 | 0.012453 | 0.0031213 | -0.012452 | -0.0031205 | 1.3087e-06 | 7.1224e-07 | 0.01882 | 0.01882 | 0.01882 | 0.98462 | -0.29636 | 0.98451 | -0.29857 | 5.1703
61 | 0.0064958 | 0.0016278 | -0.0064953 | -0.0016277 | 4.8814e-07 | 1.4062e-07 | 0.0098167 | 0.0098167 | 0.0098167 | 0.98462 | -0.29636 | 0.98454 | -0.29794 | 2.6969
62 | 0.0039334 | 0.00098546 | -0.0039328 | -0.00098565 | 5.7914e-07 | -1.8613e-07 | 0.0059416 | 0.0059418 | 0.0059418 | 0.98505 | -0.28803 | 0.98489 | -0.29112 | 1.6324
63 | 0.0095935 | 0.0024042 | -0.0095932 | -0.0024041 | 2.5881e-07 | 1.239e-07 | 0.0145 | 0.0145 | 0.0145 | 0.98451 | -0.29857 | 0.98448 | -0.29913 | 3.9835
64 | 0.0028249 | 0.00070777 | -0.0028247 | -0.00070795 | 1.4456e-07 | -1.764e-07 | 0.0042694 | 0.0042695 | 0.0042695 | 0.98454 | -0.29794 | 0.98449 | -0.29901 | 1.1729
65 | -0.068194 | -0.01737 | 0.0682 | 0.017374 | 6.1734e-06 | 3.9313e-06 | 0.10311 | 0.10311 | 0.10311 | 0.98508 | -0.28449 | 0.98518 | -0.28262 | 28.3272
66 | 0.064511 | 0.016447 | -0.064439 | -0.016401 | 7.2231e-05 | 4.597e-05 | 0.097548 | 0.097548 | 0.097548 | 0.98508 | -0.28449 | 0.98387 | -0.30771 | 26.799
67 | -0.071496 | -0.0182 | 0.071623 | 0.018281 | 0.0001265 | 8.0592e-05 | 0.10809 | 0.10809 | 0.10809 | 0.98518 | -0.28262 | 0.98708 | -0.24599 | 29.695
68 | 0.064439 | 0.016401 | -0.064335 | -0.016336 | 0.00010364 | 6.5962e-05 | 0.097548 | 0.097548 | 0.097548 | 0.98387 | -0.30771 | 0.98215 | -0.34113 | 26.799
69 | -0.077073 | -0.019647 | 0.077092 | 0.019659 | 1.8987e-05 | 1.2104e-05 | 0.11631 | 0.11631 | 0.11631 | 0.98708 | -0.24599 | 0.98735 | -0.24089 | 31.9521
70 | 0.064335 | 0.016336 | -0.064209 | -0.016255 | 0.00012661 | 8.0585e-05 | 0.097548 | 0.097549 | 0.097549 | 0.98215 | -0.34113 | 0.98004 | -0.38212 | 26.7991
71 | -0.080621 | -0.020544 | 0.080794 | 0.020653 | 0.00017231 | 0.00010988 | 0.12162 | 0.12162 | 0.12162 | 0.98735 | -0.24089 | 0.98965 | -0.1967 | 33.4133
72 | 0.0037402 | 0.00093714 | -0.0037399 | -0.0009373 | 3.3144e-07 | -1.5825e-07 | 0.0055801 | 0.0055803 | 0.0055803 | 0.99736 | -0.050873 | 0.99726 | -0.052733 | 1.533
73 | -0.0037402 | -0.00093714 | 0.0037404 | 0.00093705 | 1.8531e-07 | -8.8519e-08 | 0.0055801 | 0.0055801 | 0.0055801 | 0.99736 | -0.050873 | 0.99741 | -0.049833 | 1.533
74 | -0.0082722 | -0.0020728 | 0.0082737 | 0.0020734 | 1.4553e-06 | 5.9878e-07 | 0.012341 | 0.012341 | 0.012341 | 0.99741 | -0.049833 | 0.9976 | -0.04614 | 3.3904
75 | 0.0622 | 0.015751 | -0.062073 | -0.015671 | 0.00012632 | 8.0369e-05 | 0.094498 | 0.094498 | 0.094498 | 0.98004 | -0.38212 | 0.97786 | -0.4245 | 25.961
76 | -0.084863 | -0.021673 | 0.084936 | 0.02172 | 7.2956e-05 | 4.6539e-05 | 0.12774 | 0.12774 | 0.12774 | 0.98965 | -0.1967 | 0.99058 | -0.17893 | 35.0942
77 | -0.014149 | -0.003546 | 0.014152 | 0.0035473 | 2.2732e-06 | 1.2771e-06 | 0.021105 | 0.021105 | 0.021105 | 0.9976 | -0.04614 | 0.99778 | -0.042768 | 5.7981
78 | 0.062073 | 0.015671 | -0.062017 | -0.015635 | 5.5998e-05 | 3.5629e-05 | 0.094498 | 0.094498 | 0.094498 | 0.97786 | -0.4245 | 0.9769 | -0.44335 | 25.9611
79 | -0.018289 | -0.0045843 | 0.018294 | 0.0045873 | 5.1304e-06 | 3.0432e-06 | 0.027276 | 0.027276 | 0.027276 | 0.99778 | -0.042768 | 0.99808 | -0.036882 | 7.4933
80 | -0.020448 | -0.005127 | 0.020455 | 0.0051315 | 7.4161e-06 | 4.4681e-06 | 0.030486 | 0.030486 | 0.030486 | 0.99808 | -0.036882 | 0.99848 | -0.029274 | 8.3752
81 | -0.024675 | -0.0061892 | 0.024682 | 0.006193 | 6.3043e-06 | 3.8721e-06 | 0.036775 | 0.036775 | 0.036775 | 0.99848 | -0.029274 | 0.99876 | -0.023916 | 10.103
82 | -0.0037445 | -0.00093845 | 0.0037446 | 0.00093837 | 1.7233e-07 | -7.9277e-08 | 0.0056056 | 0.0056055 | 0.0056056 | 0.99397 | -0.11561 | 0.99402 | -0.11465 | 1.54
83 | 0.0058939 | 0.0014771 | -0.0058925 | -0.0014768 | 1.4075e-06 | 2.7596e-07 | 0.008823 | 0.0088232 | 0.0088232 | 0.99402 | -0.11465 | 0.99376 | -0.11966 | 2.424
84 | -0.0096386 | -0.0024155 | 0.0096406 | 0.0024164 | 2.0146e-06 | 9.5477e-07 | 0.014429 | 0.014428 | 0.014429 | 0.99402 | -0.11465 | 0.99425 | -0.11026 | 3.9639
85 | 0.0030616 | 0.00076714 | -0.0030615 | -0.00076728 | 1.6056e-07 | -1.3786e-07 | 0.0046915 | 0.0046916 | 0.0046916 | 0.97105 | -0.55848 | 0.971 | -0.55958 | 1.2889
86 | -0.088696 | -0.022662 | 0.088799 | 0.022728 | 0.00010352 | 6.6052e-05 | 0.13339 | 0.13339 | 0.13339 | 0.99058 | -0.17893 | 0.99184 | -0.15483 | 36.6458
87 | -0.092897 | -0.023755 | 0.092993 | 0.023817 | 9.6657e-05 | 6.169e-05 | 0.13954 | 0.13954 | 0.13954 | 0.99184 | -0.15483 | 0.99297 | -0.13335 | 38.3345
88 | -0.097073 | -0.024839 | 0.097248 | 0.024951 | 0.0001744 | 0.00011133 | 0.14565 | 0.14565 | 0.14565 | 0.99297 | -0.13335 | 0.99492 | -0.096312 | 40.0141
89 | -0.027549 | -0.0069118 | 0.027567 | 0.0069224 | 1.7143e-05 | 1.0616e-05 | 0.041048 | 0.041048 | 0.041048 | 0.99876 | -0.023916 | 0.99943 | -0.010872 | 11.2768
90 | -0.029806 | -0.0074836 | 0.029806 | 0.0074838 | 2.68e-07 | 1.6677e-07 | 0.044382 | 0.044382 | 0.044382 | 0.99943 | -0.010872 | 0.99944 | -0.010684 | 12.1927
91 | -0.016323 | -0.0040911 | 0.016326 | 0.0040927 | 2.8035e-06 | 1.6318e-06 | 0.024429 | 0.024429 | 0.024429 | 0.99425 | -0.11026 | 0.99444 | -0.10666 | 6.7113
92 | -0.019344 | -0.0048492 | 0.01935 | 0.0048527 | 5.8788e-06 | 3.5196e-06 | 0.028945 | 0.028945 | 0.028945 | 0.99444 | -0.10666 | 0.99477 | -0.10028 | 7.952
93 | -0.099355 | -0.025479 | 0.099359 | 0.025482 | 4.1835e-06 | 2.6709e-06 | 0.1488 | 0.1488 | 0.1488 | 0.99492 | -0.096312 | 0.99496 | -0.095444 | 40.8801
94 | -0.10178 | -0.026088 | 0.10192 | 0.026176 | 0.00013798 | 8.8101e-05 | 0.15242 | 0.15242 | 0.15242 | 0.99496 | -0.095444 | 0.99644 | -0.06752 | 41.8736
95 | -0.023695 | -0.0059418 | 0.0237 | 0.005945 | 5.2508e-06 | 3.2158e-06 | 0.035445 | 0.035445 | 0.035445 | 0.99477 | -0.10028 | 0.99501 | -0.095631 | 9.7377
96 | -0.025766 | -0.0064626 | 0.025766 | 0.0064629 | 4.4347e-07 | 2.7347e-07 | 0.038534 | 0.038534 | 0.038534 | 0.99501 | -0.095631 | 0.99502 | -0.09527 | 10.5862
97 | -0.027782 | -0.006968 | 0.027793 | 0.0069749 | 1.1035e-05 | 6.841e-06 | 0.041548 | 0.041548 | 0.041548 | 0.99502 | -0.09527 | 0.99546 | -0.08694 | 11.4143
98 | -0.029887 | -0.0074996 | 0.029887 | 0.0074998 | 3.3957e-07 | 2.1143e-07 | 0.044678 | 0.044678 | 0.044678 | 0.99546 | -0.08694 | 0.99547 | -0.086702 | 12.2742
99 | -0.031986 | -0.0080258 | 0.031994 | 0.0080312 | 8.5346e-06 | 5.3327e-06 | 0.047815 | 0.047815 | 0.047815 | 0.99547 | -0.086702 | 0.99576 | -0.081107 | 13.136
100 | -0.031902 | -0.008009 | 0.031902 | 0.008009 | 8.7963e-09 | 5.4988e-09 | 0.047502 | 0.047502 | 0.047502 | 0.99944 | -0.010684 | 0.99944 | -0.010678 | 13.0499
101 | -0.034006 | -0.0085364 | 0.034006 | 0.0085366 | 2.7654e-07 | 1.7321e-07 | 0.050635 | 0.050635 | 0.050635 | 0.99944 | -0.010678 | 0.99945 | -0.010508 | 13.9106
102 | -0.010025 | -0.0025056 | 0.010028 | 0.002507 | 2.7588e-06 | 1.3408e-06 | 0.014994 | 0.014994 | 0.014994 | 0.99472 | -0.10123 | 0.99502 | -0.095441 | 4.1193
103 | 0.010025 | 0.0025056 | -0.010024 | -0.002505 | 1.2349e-06 | 6.0023e-07 | 0.014994 | 0.014994 | 0.014994 | 0.99472 | -0.10123 | 0.99459 | -0.10382 | 4.1194
104 | -0.012918 | -0.0032312 | 0.012921 | 0.0032331 | 3.4496e-06 | 1.8874e-06 | 0.019316 | 0.019316 | 0.019316 | 0.99502 | -0.095441 | 0.99531 | -0.089829 | 5.3065
105 | 0.0063561 | 0.0015858 | -0.0063532 | -0.001585 | 2.9547e-06 | 7.6029e-07 | 0.009507 | 0.0095074 | 0.0095074 | 0.99459 | -0.10382 | 0.99408 | -0.11361 | 2.6119
106 | 0.0041371 | 0.0010369 | -0.0041371 | -0.0010369 | 5.4789e-09 | -1.3796e-09 | 0.0062095 | 0.0062095 | 0.0062095 | 0.9914 | -0.16492 | 0.9914 | -0.16494 | 1.7059
107 | -0.0076644 | -0.0019209 | 0.0076655 | 0.0019213 | 1.1339e-06 | 4.31e-07 | 0.011504 | 0.011504 | 0.011504 | 0.9914 | -0.16492 | 0.99156 | -0.16181 | 3.1603
108 | -0.011697 | -0.0029317 | 0.011697 | 0.0029318 | 1.5877e-07 | 8.3892e-08 | 0.017554 | 0.017554 | 0.017554 | 0.99156 | -0.16181 | 0.99158 | -0.16153 | 4.8224
109 | 0.0056845 | 0.0014245 | -0.005684 | -0.0014244 | 5.3544e-07 | 8.8676e-08 | 0.0085226 | 0.0085227 | 0.0085227 | 0.99249 | -0.14389 | 0.99239 | -0.14587 | 2.3414
110 | -0.09635 | -0.024304 | 0.096414 | 0.024345 | 6.3855e-05 | 4.0762e-05 | 0.14451 | 0.14451 | 0.14451 | 0.99249 | -0.14389 | 0.99321 | -0.13005 | 39.7007
111 | 0.0032785 | 0.00082128 | -0.0032781 | -0.00082157 | 3.5815e-07 | -2.8765e-07 | 0.0049007 | 0.0049009 | 0.0049009 | 0.99543 | -0.08697 | 0.99531 | -0.089264 | 1.3464
112 | -0.14598 | -0.037257 | 0.14615 | 0.037365 | 0.00016952 | 0.000108 | 0.21824 | 0.21824 | 0.21824 | 0.99644 | -0.06752 | 0.9977 | -0.043514 | 29.9779
113 | 0.0060595 | 0.0015184 | -0.0060589 | -0.0015182 | 6.2183e-07 | 1.3421e-07 | 0.0090488 | 0.0090489 | 0.0090489 | 0.99644 | -0.06752 | 0.99633 | -0.069674 | 2.486
114 | -0.14838 | -0.037923 | 0.14848 | 0.037985 | 9.7469e-05 | 6.2104e-05 | 0.22156 | 0.22156 | 0.22156 | 0.9977 | -0.043514 | 0.99842 | -0.029942 | 30.434
115 | 0.0030293 | 0.00075894 | -0.0030291 | -0.00075917 | 2.1741e-07 | -2.2969e-07 | 0.0045242 | 0.0045243 | 0.0045243 | 0.99633 | -0.069674 | 0.99625 | -0.071181 | 1.243
116 | 0.0032789 | 0.00082161 | -0.0032788 | -0.00082174 | 1.6509e-07 | -1.2964e-07 | 0.0049165 | 0.0049166 | 0.0049166 | 0.99239 | -0.14587 | 0.99233 | -0.14692 | 1.3507
117 | -0.10011 | -0.02527 | 0.10038 | 0.025443 | 0.00027059 | 0.00017276 | 0.15004 | 0.15004 | 0.15004 | 0.99321 | -0.13005 | 0.99614 | -0.073792 | 41.2201
118 | 0.020885 | 0.0052342 | -0.020877 | -0.0052296 | 7.7501e-06 | 4.6837e-06 | 0.031197 | 0.031197 | 0.031197 | 0.99614 | -0.073792 | 0.99573 | -0.081584 | 8.5707
119 | 0.033962 | 0.0085288 | -0.03395 | -0.0085214 | 1.185e-05 | 7.4244e-06 | 0.050738 | 0.050738 | 0.050738 | 0.99614 | -0.073792 | 0.99576 | -0.081107 | 13.939
120 | -0.15522 | -0.039206 | 0.1554 | 0.039321 | 0.00018132 | 0.00011558 | 0.23198 | 0.23198 | 0.23198 | 0.99614 | -0.073792 | 0.99741 | -0.049447 | 31.8648
121 | 0.018941 | 0.0047443 | -0.018933 | -0.0047399 | 7.4332e-06 | 4.4356e-06 | 0.028304 | 0.028304 | 0.028304 | 0.99573 | -0.081584 | 0.99531 | -0.089829 | 7.7758
122 | -0.15782 | -0.039928 | 0.15798 | 0.040028 | 0.00015746 | 0.00010038 | 0.23559 | 0.23559 | 0.23559 | 0.99741 | -0.049447 | 0.9985 | -0.028678 | 32.3609
123 | -0.16022 | -0.040591 | 0.16045 | 0.040732 | 0.00022105 | 0.00014093 | 0.23893 | 0.23893 | 0.23893 | 0.9985 | -0.028678 | 1 | 0 | 32.8201
124 | 0.036445 | 0.0091546 | -0.036427 | -0.0091432 | 1.8265e-05 | 1.1473e-05 | 0.054238 | 0.054238 | 0.054238 | 1 | 0 | 0.99945 | -0.010508 | 14.9006
125 | 0.15111 | 0.03873 | -0.15089 | -0.038591 | 0.00021899 | 0.00013955 | 0.22516 | 0.22516 | 0.22516 | 1 | 0 | 0.99842 | -0.029942 | 30.929
126 | 0.0075159 | 0.0018835 | -0.0075149 | -0.0018831 | 9.9565e-07 | 3.7565e-07 | 0.01136 | 0.01136 | 0.01136 | 0.98448 | -0.29913 | 0.98434 | -0.30191 | 3.1209
127 | 0.0054614 | 0.0013684 | -0.005461 | -0.0013684 | 3.9463e-07 | 5.632e-08 | 0.0082559 | 0.0082559 | 0.0082559 | 0.98434 | -0.30191 | 0.98426 | -0.30343 | 2.2681
128 | 0.0032873 | 0.00082359 | -0.0032871 | -0.00082374 | 2.1201e-07 | -1.5522e-07 | 0.0049697 | 0.0049698 | 0.0049698 | 0.98426 | -0.30343 | 0.98419 | -0.30479 | 1.3653
129 | 0.0016317 | 0.00040887 | -0.0016317 | -0.00040895 | 1.5994e-08 | -7.8816e-08 | 0.002467 | 0.0024671 | 0.0024671 | 0.98419 | -0.30479 | 0.98418 | -0.30499 | 0.67777
130 | 0.0063532 | 0.001585 | -0.0063514 | -0.0015845 | 1.8072e-06 | 4.6563e-07 | 0.0095074 | 0.0095076 | 0.0095076 | 0.99408 | -0.11361 | 0.99377 | -0.11961 | 2.612
131 | 0.0031291 | 0.00077696 | -0.0031281 | -0.00077794 | 1.0426e-06 | -9.7468e-07 | 0.0046828 | 0.0046834 | 0.0046834 | 0.99377 | -0.11961 | 0.99341 | -0.12665 | 1.2866
132 | 0.0021102 | 0.00052283 | -0.00211 | -0.00052322 | 1.3967e-07 | -3.9386e-07 | 0.0031587 | 0.0031588 | 0.0031588 | 0.99341 | -0.12665 | 0.99334 | -0.12805 | 0.86781
133 | 0.0018106 | 0.00044817 | -0.0018093 | -0.00045344 | 1.3014e-06 | -5.2734e-06 | 0.0027102 | 0.0027124 | 0.0027124 | 0.99334 | -0.12805 | 0.99256 | -0.14321 | 0.74516

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34965 | 0.088617

## res_load
| p_mw | q_mvar
0 | 0.0053649 | 0.0013446
1 | 0.003138 | 0.00078645
2 | 0.0035742 | 0.00089578
3 | 0.0051452 | 0.0012895
4 | 0.0043716 | 0.0010956
5 | 0.0040448 | 0.0010137
6 | 0.0012286 | 0.00030791
7 | 0.0045014 | 0.0011281
8 | 0.004794 | 0.0012015
9 | 0.0064413 | 0.0016143
10 | 0.0043257 | 0.0010841
11 | 0.0031402 | 0.00078701
12 | 0.0024429 | 0.00061225
13 | 0.0059054 | 0.00148
14 | 0.0023972 | 0.00060078
15 | 0.0030189 | 0.00075661
16 | 0.0031464 | 0.00078856
17 | 0.0026412 | 0.00066195
18 | 0.0023935 | 0.00059988
19 | 0.0032869 | 0.00082378
20 | 0.00085063 | 0.00021319
21 | 0.002691 | 0.00067442
22 | 0.0010533 | 0.00026398
23 | 0.0015136 | 0.00037935
24 | 0.0035544 | 0.00089081
25 | 0.0019844 | 0.00049733
26 | 0.0033055 | 0.00082844
27 | 0.002704 | 0.00067769
28 | 0.0048744 | 0.0012216
29 | 0.0036397 | 0.0009122
30 | 0.0024981 | 0.00062607
31 | 0.0031077 | 0.00077887
32 | 0.0025849 | 0.00064783
33 | 0.0034379 | 0.00086163
34 | 0.0033182 | 0.00083161
35 | 0.0039794 | 0.00099733
36 | 0.004511 | 0.0011306
37 | 0.0026905 | 0.00067431
38 | 0.0028582 | 0.00071634
39 | 0.0036704 | 0.00091989
40 | 0.0039328 | 0.00098565
41 | 0.0036827 | 0.00092298
42 | 0.0032962 | 0.0008261
43 | 0.0054503 | 0.001366
44 | 0.0035292 | 0.0008845
45 | 0.0037399 | 0.0009373
46 | 0.0045319 | 0.0011358
47 | 0.0020092 | 0.00050355
48 | 0.0040695 | 0.0010199
49 | 0.0058757 | 0.0014726
50 | 0.0041377 | 0.001037
51 | 0.0021533 | 0.00053967
52 | 0.0042202 | 0.0010577
53 | 0.0037445 | 0.00093845
54 | 0.0034342 | 0.0008607
55 | 0.0052055 | 0.0013046
56 | 0.0030615 | 0.00076728
57 | 0.0037598 | 0.00094229
58 | 0.0040972 | 0.0010268
59 | 0.00408 | 0.0010226
60 | 0.0028678 | 0.00071873
61 | 0.0022393 | 0.00056123
62 | 0.0058925 | 0.0014768
63 | 0.0066821 | 0.0016747
64 | 0.0030182 | 0.00075644
65 | 0.0021076 | 0.00052821
66 | 0.0024182 | 0.00060607
67 | 0.0043454 | 0.0010891
68 | 0.0020653 | 0.00051761
69 | 0.0020156 | 0.00050516
70 | 0.0020939 | 0.00052478
71 | 0.0020987 | 0.00052598
72 | 0.0020956 | 0.00052521
73 | 0.0021043 | 0.0005274
74 | 0.0028897 | 0.00072423
75 | 0.0036678 | 0.00091925
76 | 0.0035273 | 0.00088401
77 | 0.0041371 | 0.0010369
78 | 0.0040316 | 0.0010104
79 | 0.0034137 | 0.00085556
80 | 0.0032786 | 0.00082168
81 | 0.0032781 | 0.00082157
82 | 0.0022263 | 0.00055797
83 | 0.0030296 | 0.00075929
84 | 0.0024051 | 0.00060277
85 | 0.0036916 | 0.00092521
86 | 0.0032788 | 0.00082174
87 | 0.0060631 | 0.0015196
88 | 0.0019362 | 0.00048526
89 | 0.0019559 | 0.00049021
90 | 0.0024206 | 0.00060667
91 | 0.0060121 | 0.0015068
92 | 0.0022432 | 0.00056221
93 | 0.0028247 | 0.00070795
94 | 0.0020773 | 0.00052063
95 | 0.0020535 | 0.00051465
96 | 0.0021737 | 0.00054478
97 | 0.0016554 | 0.00041487
98 | 0.0016317 | 0.00040895
99 | 0.0032223 | 0.00080758
100 | 0.0010179 | 0.00025511
101 | 0.00029946 | 7.5052e-05
102 | 0.0030291 | 0.00075917
103 | 0.002418 | 0.00060601
104 | 0.0024204 | 0.0006066
105 | 0.0018093 | 0.00045344

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1