## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2328-2_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2328-2_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2328-2_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2328-2_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2328-2_0_6_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_2328-2_0_6_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_2328-2_0_6_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_2328-2_0_6_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_2328-2_0_6_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_2328-2_0_6_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_2328-2_0_6_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_2328-2_0_6_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_2328-2_0_6_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_2328-2_0_6_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_2328-2_0_6_node_4 | 0.4 | n |  | TRUE
15 | bus_LV_2328-2_0_6_node_5 | 0.4 | n |  | TRUE
16 | bus_LV_2328-2_0_6_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_2328-2_0_6_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_2328-2_0_6_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_2328-2_0_6_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2328-2_0_6_node_111 | 0.4 | n |  | TRUE
21 | bus_LV_2328-2_0_6_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_2328-2_0_6_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2328-2_0_6_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_2328-2_0_6_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2328-2_0_6_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2328-2_0_6_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_2328-2_0_6_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_2328-2_0_6_node_35 | 0.4 | n |  | TRUE
29 | bus_LV_2328-2_0_6_node_112 | 0.4 | n |  | TRUE
30 | bus_LV_2328-2_0_6_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2328-2_0_6_node_135 | 0.4 | n |  | TRUE
32 | bus_LV_2328-2_0_6_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_2328-2_0_6_node_136 | 0.4 | n |  | TRUE
34 | bus_LV_2328-2_0_6_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_2328-2_0_6_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_2328-2_0_6_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_2328-2_0_6_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_2328-2_0_6_node_139 | 0.4 | n |  | TRUE
39 | bus_LV_2328-2_0_6_node_141 | 0.4 | n |  | TRUE
40 | bus_LV_2328-2_0_6_node_117 | 0.4 | n |  | TRUE
41 | bus_LV_2328-2_0_6_node_118 | 0.4 | n |  | TRUE
42 | bus_LV_2328-2_0_6_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_2328-2_0_6_node_138 | 0.4 | n |  | TRUE
44 | bus_LV_2328-2_0_6_node_24 | 0.4 | n |  | TRUE
45 | bus_LV_2328-2_0_6_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_2328-2_0_6_node_120 | 0.4 | n |  | TRUE
47 | bus_LV_2328-2_0_6_node_137 | 0.4 | n |  | TRUE
48 | bus_LV_2328-2_0_6_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_2328-2_0_6_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_2328-2_0_6_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_2328-2_0_6_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_2328-2_0_6_node_89 | 0.4 | n |  | TRUE
53 | bus_LV_2328-2_0_6_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_2328-2_0_6_node_145 | 0.4 | n |  | TRUE
55 | bus_LV_2328-2_0_6_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_2328-2_0_6_node_88 | 0.4 | n |  | TRUE
57 | bus_LV_2328-2_0_6_node_144 | 0.4 | n |  | TRUE
58 | bus_LV_2328-2_0_6_node_143 | 0.4 | n |  | TRUE
59 | bus_LV_2328-2_0_6_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_2328-2_0_6_node_142 | 0.4 | n |  | TRUE
61 | bus_LV_2328-2_0_6_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_2328-2_0_6_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_2328-2_0_6_node_67 | 0.4 | n |  | TRUE
64 | bus_LV_2328-2_0_6_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_2328-2_0_6_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_2328-2_0_6_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_2328-2_0_6_node_65 | 0.4 | n |  | TRUE
68 | bus_LV_2328-2_0_6_node_51 | 0.4 | n |  | TRUE
69 | bus_LV_2328-2_0_6_node_47 | 0.4 | n |  | TRUE
70 | bus_LV_2328-2_0_6_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_2328-2_0_6_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_2328-2_0_6_node_60 | 0.4 | n |  | TRUE
73 | bus_LV_2328-2_0_6_node_66 | 0.4 | n |  | TRUE
74 | bus_LV_2328-2_0_6_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_2328-2_0_6_node_53 | 0.4 | n |  | TRUE
76 | bus_LV_2328-2_0_6_node_54 | 0.4 | n |  | TRUE
77 | bus_LV_2328-2_0_6_node_55 | 0.4 | n |  | TRUE
78 | bus_LV_2328-2_0_6_node_56 | 0.4 | n |  | TRUE
79 | bus_LV_2328-2_0_6_node_57 | 0.4 | n |  | TRUE
80 | bus_LV_2328-2_0_6_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_2328-2_0_6_node_59 | 0.4 | n |  | TRUE
82 | bus_LV_2328-2_0_6_node_115 | 0.4 | n |  | TRUE
83 | bus_LV_2328-2_0_6_node_116 | 0.4 | n |  | TRUE
84 | bus_LV_2328-2_0_6_node_62 | 0.4 | n |  | TRUE
85 | bus_LV_2328-2_0_6_node_63 | 0.4 | n |  | TRUE
86 | bus_LV_2328-2_0_6_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_2328-2_0_6_node_121 | 0.4 | n |  | TRUE
88 | bus_LV_2328-2_0_6_node_122 | 0.4 | n |  | TRUE
89 | bus_LV_2328-2_0_6_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_2328-2_0_6_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_2328-2_0_6_node_73 | 0.4 | n |  | TRUE
92 | bus_LV_2328-2_0_6_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_2328-2_0_6_node_72 | 0.4 | n |  | TRUE
94 | bus_LV_2328-2_0_6_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_2328-2_0_6_node_71 | 0.4 | n |  | TRUE
96 | bus_LV_2328-2_0_6_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_2328-2_0_6_node_78 | 0.4 | n |  | TRUE
98 | bus_LV_2328-2_0_6_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_2328-2_0_6_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_2328-2_0_6_node_77 | 0.4 | n |  | TRUE
101 | bus_LV_2328-2_0_6_node_74 | 0.4 | n |  | TRUE
102 | bus_LV_2328-2_0_6_node_76 | 0.4 | n |  | TRUE
103 | bus_LV_2328-2_0_6_node_85 | 0.4 | n |  | TRUE
104 | bus_LV_2328-2_0_6_node_83 | 0.4 | n |  | TRUE
105 | bus_LV_2328-2_0_6_node_80 | 0.4 | n |  | TRUE
106 | bus_LV_2328-2_0_6_node_81 | 0.4 | n |  | TRUE
107 | bus_LV_2328-2_0_6_node_87 | 0.4 | n |  | TRUE
108 | bus_LV_2328-2_0_6_node_90 | 0.4 | n |  | TRUE
109 | bus_LV_2328-2_0_6_node_91 | 0.4 | n |  | TRUE
110 | bus_LV_2328-2_0_6_node_97 | 0.4 | n |  | TRUE
111 | bus_LV_2328-2_0_6_node_96 | 0.4 | n |  | TRUE
112 | bus_LV_2328-2_0_6_node_92 | 0.4 | n |  | TRUE
113 | bus_LV_2328-2_0_6_node_93 | 0.4 | n |  | TRUE
114 | bus_LV_2328-2_0_6_node_94 | 0.4 | n |  | TRUE
115 | bus_LV_2328-2_0_6_node_95 | 0.4 | n |  | TRUE
116 | bus_LV_2328-2_0_6_node_102 | 0.4 | n |  | TRUE
117 | bus_LV_2328-2_0_6_node_100 | 0.4 | n |  | TRUE
118 | bus_LV_2328-2_0_6_node_98 | 0.4 | n |  | TRUE
119 | bus_LV_2328-2_0_6_node_99 | 0.4 | n |  | TRUE
120 | bus_LV_2328-2_0_6_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_2328-2_0_6_node_108 | 0.4 | n |  | TRUE
122 | bus_LV_2328-2_0_6_node_109 | 0.4 | n |  | TRUE
123 | bus_LV_2328-2_0_6_node_103 | 0.4 | n |  | TRUE
124 | bus_LV_2328-2_0_6_node_104 | 0.4 | n |  | TRUE
125 | bus_LV_2328-2_0_6_node_105 | 0.4 | n |  | TRUE
126 | bus_LV_2328-2_0_6_node_106 | 0.4 | n |  | TRUE
127 | bus_LV_2328-2_0_6_node_107 | 0.4 | n |  | TRUE
128 | bus_LV_2328-2_0_6_node_133 | 0.4 | n |  | TRUE
129 | bus_LV_2328-2_0_6_node_134 | 0.4 | n |  | TRUE
130 | bus_LV_2328-2_0_6_node_110 | 0.4 | n |  | TRUE
131 | bus_LV_2328-2_0_6_node_113 | 0.4 | n |  | TRUE
132 | bus_LV_2328-2_0_6_node_114 | 0.4 | n |  | TRUE
133 | bus_LV_2328-2_0_6_node_119 | 0.4 | n |  | TRUE
134 | bus_LV_2328-2_0_6_node_123 | 0.4 | n |  | TRUE
135 | bus_LV_2328-2_0_6_node_124 | 0.4 | n |  | TRUE
136 | bus_LV_2328-2_0_6_node_132 | 0.4 | n |  | TRUE
137 | bus_LV_2328-2_0_6_node_128 | 0.4 | n |  | TRUE
138 | bus_LV_2328-2_0_6_node_125 | 0.4 | n |  | TRUE
139 | bus_LV_2328-2_0_6_node_126 | 0.4 | n |  | TRUE
140 | bus_LV_2328-2_0_6_node_127 | 0.4 | n |  | TRUE
141 | bus_LV_2328-2_0_6_node_129 | 0.4 | n |  | TRUE
142 | bus_LV_2328-2_0_6_node_130 | 0.4 | n |  | TRUE
143 | bus_LV_2328-2_0_6_node_131 | 0.4 | n |  | TRUE
144 | bus_MV_384_0_node_31 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2328-2_0_6_load_0 | 0 | 0.0021027 | 0.00052699 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2328-2_0_6_load_2 | 2 | 0.0031835 | 0.00079785 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2328-2_0_6_load_9 | 4 | 0.0022088 | 0.00055359 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2328-2_0_6_load_22 | 6 | 0.004103 | 0.0010283 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2328-2_0_6_load_8 | 7 | 0.0011944 | 0.00029934 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2328-2_0_6_load_26 | 8 | 0.0019424 | 0.00048681 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2328-2_0_6_load_27 | 9 | 0.0022086 | 0.00055352 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2328-2_0_6_load_32 | 11 | 0.0078161 | 0.0019589 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2328-2_0_6_load_29 | 12 | 0.0028941 | 0.00072533 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2328-2_0_6_load_23 | 13 | 0.0045859 | 0.0011493 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2328-2_0_6_load_4 | 14 | 0.0028059 | 0.00070322 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2328-2_0_6_load_7 | 17 | 0.001836 | 0.00046015 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2328-2_0_6_load_17 | 18 | 0.0024275 | 0.00060838 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2328-2_0_6_load_16 | 19 | 0.0024325 | 0.00060964 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2328-2_0_6_load_111 | 20 | 0.0033483 | 0.00083917 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2328-2_0_6_load_14 | 21 | 0.0022331 | 0.00055967 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2328-2_0_6_load_11 | 23 | 0.0027344 | 0.0006853 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2328-2_0_6_load_12 | 24 | 0.0010462 | 0.00026221 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2328-2_0_6_load_15 | 25 | 0.003683 | 0.00092304 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2328-2_0_6_load_36 | 26 | 0.0018153 | 0.00045495 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2328-2_0_6_load_13 | 27 | 0.0021546 | 0.00054 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2328-2_0_6_load_35 | 28 | 0.0026625 | 0.00066727 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2328-2_0_6_load_112 | 29 | 0.0047853 | 0.0011993 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2328-2_0_6_load_18 | 30 | 0.0029112 | 0.00072962 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2328-2_0_6_load_135 | 31 | 0.00069031 | 0.00017301 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2328-2_0_6_load_30 | 32 | 0.0043732 | 0.001096 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2328-2_0_6_load_136 | 33 | 0.0010756 | 0.00026957 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2328-2_0_6_load_31 | 34 | 0.0051392 | 0.001288 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2328-2_0_6_load_20 | 36 | 0.00073457 | 0.0001841 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2328-2_0_6_load_21 | 37 | 0.00098201 | 0.00024612 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2328-2_0_6_load_139 | 38 | 0.0021797 | 0.00054629 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2328-2_0_6_load_141 | 39 | 0.0067894 | 0.0017016 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2328-2_0_6_load_117 | 40 | 0.0036108 | 0.00090496 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2328-2_0_6_load_118 | 41 | 0.0021008 | 0.00052651 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2328-2_0_6_load_34 | 42 | 0.0045497 | 0.0011403 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2328-2_0_6_load_24 | 44 | 0.0045971 | 0.0011521 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2328-2_0_6_load_33 | 45 | 0.0047514 | 0.0011908 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2328-2_0_6_load_120 | 46 | 0.0031344 | 0.00078556 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2328-2_0_6_load_137 | 47 | 0.0017971 | 0.0004504 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2328-2_0_6_load_37 | 48 | 0.0016764 | 0.00042014 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2328-2_0_6_load_40 | 51 | 0.0012188 | 0.00030547 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2328-2_0_6_load_41 | 53 | 0.0011175 | 0.00028007 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2328-2_0_6_load_145 | 54 | 0.00322 | 0.00080702 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2328-2_0_6_load_42 | 55 | 0.0010669 | 0.00026738 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2328-2_0_6_load_88 | 56 | 0.0018605 | 0.00046629 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2328-2_0_6_load_143 | 58 | 0.0015128 | 0.00037914 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2328-2_0_6_load_44 | 59 | 0.0039551 | 0.00099125 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2328-2_0_6_load_142 | 60 | 0.00077641 | 0.00019459 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2328-2_0_6_load_45 | 62 | 0.0020113 | 0.00050409 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2328-2_0_6_load_50 | 64 | 0.001365 | 0.00034211 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2328-2_0_6_load_48 | 65 | 0.0020534 | 0.00051463 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2328-2_0_6_load_46 | 66 | 0.00105 | 0.00026314 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2328-2_0_6_load_65 | 67 | 0.0018083 | 0.0004532 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2328-2_0_6_load_51 | 68 | 0.0027789 | 0.00069645 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2328-2_0_6_load_47 | 69 | 0.0010853 | 0.00027201 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2328-2_0_6_load_49 | 70 | 0.0021676 | 0.00054326 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2328-2_0_6_load_52 | 71 | 0.0027628 | 0.00069243 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2328-2_0_6_load_60 | 72 | 0.0033805 | 0.00084725 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2328-2_0_6_load_66 | 73 | 0.0023276 | 0.00058334 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2328-2_0_6_load_61 | 74 | 0.0028106 | 0.00070441 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2328-2_0_6_load_53 | 75 | 0.0010179 | 0.00025511 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2328-2_0_6_load_55 | 77 | 0.0019633 | 0.00049206 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2328-2_0_6_load_56 | 78 | 0.0030841 | 0.00077294 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2328-2_0_6_load_57 | 79 | 0.002594 | 0.00065012 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2328-2_0_6_load_58 | 80 | 0.0030844 | 0.00077302 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2328-2_0_6_load_59 | 81 | 0.0038747 | 0.00097109 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2328-2_0_6_load_115 | 82 | 0.0035684 | 0.00089433 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2328-2_0_6_load_116 | 83 | 0.0045871 | 0.0011496 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2328-2_0_6_load_62 | 84 | 0.003111 | 0.00077969 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2328-2_0_6_load_63 | 85 | 0.0028395 | 0.00071165 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2328-2_0_6_load_64 | 86 | 0.0031196 | 0.00078184 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2328-2_0_6_load_122 | 88 | 0.0029558 | 0.00074078 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2328-2_0_6_load_68 | 89 | 0.00083346 | 0.00020888 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2328-2_0_6_load_69 | 90 | 0.0019744 | 0.00049484 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2328-2_0_6_load_73 | 91 | 0.0019126 | 0.00047935 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2328-2_0_6_load_75 | 92 | 0.0011242 | 0.00028174 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2328-2_0_6_load_72 | 93 | 0.0019965 | 0.00050038 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2328-2_0_6_load_70 | 94 | 0.0011566 | 0.00028987 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2328-2_0_6_load_71 | 95 | 0.0048064 | 0.0012046 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2328-2_0_6_load_84 | 96 | 0.0012976 | 0.00032522 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2328-2_0_6_load_78 | 97 | 0.0017609 | 0.00044133 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2328-2_0_6_load_79 | 98 | 0.0019541 | 0.00048974 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2328-2_0_6_load_82 | 99 | 0.0017657 | 0.00044252 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2328-2_0_6_load_77 | 100 | 0.0019351 | 0.00048499 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2328-2_0_6_load_74 | 101 | 0.0017998 | 0.00045107 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2328-2_0_6_load_76 | 102 | 0.003108 | 0.00077893 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2328-2_0_6_load_85 | 103 | 0.0025263 | 0.00063315 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2328-2_0_6_load_81 | 106 | 0.0096135 | 0.0024094 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2328-2_0_6_load_87 | 107 | 0.0016856 | 0.00042246 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2328-2_0_6_load_90 | 108 | 0.0019276 | 0.0004831 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2328-2_0_6_load_91 | 109 | 0.0013761 | 0.00034489 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2328-2_0_6_load_97 | 110 | 0.0033039 | 0.00082805 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2328-2_0_6_load_96 | 111 | 0.0019946 | 0.00049989 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2328-2_0_6_load_92 | 112 | 0.0023154 | 0.0005803 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2328-2_0_6_load_93 | 113 | 0.0021991 | 0.00055116 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2328-2_0_6_load_94 | 114 | 0.001987 | 0.00049798 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2328-2_0_6_load_95 | 115 | 0.0023164 | 0.00058054 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2328-2_0_6_load_102 | 116 | 0.0031735 | 0.00079536 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2328-2_0_6_load_100 | 117 | 0.0028321 | 0.0007098 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2328-2_0_6_load_98 | 118 | 0.0026498 | 0.0006641 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2328-2_0_6_load_99 | 119 | 0.0017935 | 0.0004495 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2328-2_0_6_load_101 | 120 | 0.0037561 | 0.00094138 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2328-2_0_6_load_108 | 121 | 0.0034519 | 0.00086513 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2328-2_0_6_load_109 | 122 | 0.0027237 | 0.00068263 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2328-2_0_6_load_103 | 123 | 0.0028914 | 0.00072466 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2328-2_0_6_load_104 | 124 | 0.0046075 | 0.0011548 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2328-2_0_6_load_105 | 125 | 0.0021375 | 0.00053571 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2328-2_0_6_load_106 | 126 | 0.0034752 | 0.00087096 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2328-2_0_6_load_107 | 127 | 0.003027 | 0.00075863 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2328-2_0_6_load_133 | 128 | 0.00074514 | 0.00018675 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2328-2_0_6_load_134 | 129 | 0.002746 | 0.00068822 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2328-2_0_6_load_113 | 131 | 0.0031706 | 0.00079463 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2328-2_0_6_load_114 | 132 | 0.001868 | 0.00046816 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2328-2_0_6_load_119 | 133 | 0.0028259 | 0.00070823 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2328-2_0_6_load_132 | 136 | 0.0031015 | 0.00077732 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2328-2_0_6_load_125 | 138 | 0.004538 | 0.0011373 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2328-2_0_6_load_126 | 139 | 0.0037768 | 0.00094657 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2328-2_0_6_load_127 | 140 | 0.0022859 | 0.0005729 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2328-2_0_6_load_129 | 141 | 0.0033261 | 0.0008336 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2328-2_0_6_load_130 | 142 | 0.0010764 | 0.00026976 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2328-2_0_6_load_131 | 143 | 0.002888 | 0.00072379 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 136 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2328-2_0_6_line_0 |  | 0 | 1 | 0.024446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2328-2_0_6_line_1 |  | 1 | 2 | 0.035963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2328-2_0_6_line_2 |  | 1 | 3 | 0.038528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_2328-2_0_6_line_3 |  | 2 | 4 | 0.0037293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2328-2_0_6_line_4 |  | 3 | 5 | 0.03516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2328-2_0_6_line_5 |  | 3 | 6 | 0.033851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2328-2_0_6_line_6 |  | 4 | 7 | 0.022778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2328-2_0_6_line_7 |  | 5 | 11 | 0.021967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2328-2_0_6_line_8 |  | 5 | 12 | 0.027191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2328-2_0_6_line_9 |  | 6 | 13 | 0.0099167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2328-2_0_6_line_10 |  | 7 | 22 | 0.0026037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2328-2_0_6_line_11 |  | 8 | 9 | 0.0020303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2328-2_0_6_line_12 |  | 8 | 10 | 0.017146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2328-2_0_6_line_13 |  | 10 | 13 | 0.042134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2328-2_0_6_line_14 |  | 12 | 32 | 0.019267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2328-2_0_6_line_15 |  | 13 | 44 | 0.024048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2328-2_0_6_line_16 |  | 14 | 15 | 0.01402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2328-2_0_6_line_17 |  | 15 | 16 | 0.012694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2328-2_0_6_line_18 |  | 15 | 17 | 0.019416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2328-2_0_6_line_19 |  | 16 | 18 | 0.0349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2328-2_0_6_line_20 |  | 16 | 19 | 0.019818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2328-2_0_6_line_21 |  | 18 | 20 | 0.023225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2328-2_0_6_line_22 |  | 19 | 21 | 0.019333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2328-2_0_6_line_23 |  | 20 | 29 | 0.01419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2328-2_0_6_line_24 |  | 21 | 27 | 0.0031498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_2328-2_0_6_line_25 |  | 22 | 23 | 0.018372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2328-2_0_6_line_26 |  | 22 | 24 | 0.010904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2328-2_0_6_line_27 |  | 23 | 25 | 0.0022459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2328-2_0_6_line_28 |  | 24 | 26 | 0.024263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2328-2_0_6_line_29 |  | 25 | 27 | 0.023504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_2328-2_0_6_line_30 |  | 26 | 28 | 0.0012306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2328-2_0_6_line_31 |  | 29 | 126 | 0.014428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2328-2_0_6_line_32 |  | 30 | 31 | 0.10536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2328-2_0_6_line_33 |  | 30 | 32 | 0.14545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2328-2_0_6_line_34 |  | 31 | 33 | 0.021065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2328-2_0_6_line_35 |  | 32 | 34 | 0.020845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2328-2_0_6_line_36 |  | 33 | 47 | 0.048466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2328-2_0_6_line_37 |  | 34 | 42 | 0.0051134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2328-2_0_6_line_38 |  | 35 | 36 | 0.039754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2328-2_0_6_line_39 |  | 35 | 37 | 0.020811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2328-2_0_6_line_40 |  | 36 | 38 | 0.025208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2328-2_0_6_line_41 |  | 37 | 39 | 0.04379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2328-2_0_6_line_42 |  | 38 | 43 | 0.023575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2328-2_0_6_line_43 |  | 40 | 41 | 0.0095545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2328-2_0_6_line_44 |  | 40 | 42 | 0.028604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2328-2_0_6_line_45 |  | 41 | 133 | 0.029045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2328-2_0_6_line_46 |  | 43 | 47 | 0.015017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2328-2_0_6_line_47 |  | 44 | 45 | 0.0056051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2328-2_0_6_line_48 |  | 45 | 46 | 0.02283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2328-2_0_6_line_49 |  | 48 | 49 | 0.050918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2328-2_0_6_line_50 |  | 48 | 50 | 0.052894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2328-2_0_6_line_51 |  | 49 | 51 | 0.025508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2328-2_0_6_line_52 |  | 49 | 52 | 0.12242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2328-2_0_6_line_53 |  | 50 | 53 | 0.023327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2328-2_0_6_line_54 |  | 50 | 54 | 0.085891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2328-2_0_6_line_55 |  | 51 | 55 | 0.011967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2328-2_0_6_line_56 |  | 52 | 56 | 0.028591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2328-2_0_6_line_57 |  | 54 | 57 | 0.080876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2328-2_0_6_line_58 |  | 55 | 59 | 0.042931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2328-2_0_6_line_59 |  | 57 | 58 | 0.02064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2328-2_0_6_line_60 |  | 58 | 60 | 0.0066297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2328-2_0_6_line_61 |  | 59 | 61 | 0.035406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2328-2_0_6_line_62 |  | 61 | 62 | 0.030077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2328-2_0_6_line_63 |  | 62 | 63 | 0.023943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_2328-2_0_6_line_64 |  | 62 | 64 | 0.042741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_2328-2_0_6_line_65 |  | 63 | 67 | 0.013189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_2328-2_0_6_line_66 |  | 64 | 68 | 0.028213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_2328-2_0_6_line_67 |  | 64 | 65 | 0.0037293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2328-2_0_6_line_68 |  | 65 | 66 | 0.024728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2328-2_0_6_line_69 |  | 66 | 69 | 0.0019447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2328-2_0_6_line_70 |  | 67 | 73 | 0.02782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_2328-2_0_6_line_71 |  | 68 | 71 | 0.027167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_2328-2_0_6_line_72 |  | 69 | 70 | 0.014209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2328-2_0_6_line_73 |  | 71 | 72 | 0.0048261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_2328-2_0_6_line_74 |  | 72 | 74 | 0.022245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_2328-2_0_6_line_75 |  | 73 | 89 | 0.0046131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2328-2_0_6_line_76 |  | 74 | 84 | 0.0011607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_2328-2_0_6_line_77 |  | 75 | 76 | 0.020313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2328-2_0_6_line_78 |  | 76 | 77 | 0.011394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2328-2_0_6_line_79 |  | 76 | 78 | 0.012523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2328-2_0_6_line_80 |  | 77 | 79 | 0.021851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2328-2_0_6_line_81 |  | 79 | 80 | 0.052827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2328-2_0_6_line_82 |  | 80 | 81 | 0.0053992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2328-2_0_6_line_83 |  | 81 | 82 | 0.026065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2328-2_0_6_line_84 |  | 82 | 83 | 0.023893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2328-2_0_6_line_85 |  | 83 | 133 | 0.017847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2328-2_0_6_line_86 |  | 84 | 85 | 0.027415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2328-2_0_6_line_87 |  | 85 | 86 | 0.027217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_2328-2_0_6_line_88 |  | 86 | 87 | 0.028879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2328-2_0_6_line_89 |  | 87 | 88 | 0.017127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_2328-2_0_6_line_90 |  | 88 | 134 | 0.029692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_2328-2_0_6_line_91 |  | 89 | 90 | 0.00096557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2328-2_0_6_line_92 |  | 90 | 94 | 0.013825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2328-2_0_6_line_93 |  | 91 | 92 | 0.0061929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2328-2_0_6_line_94 |  | 91 | 93 | 0.022096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2328-2_0_6_line_95 |  | 92 | 96 | 0.0012359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2328-2_0_6_line_96 |  | 93 | 101 | 0.0050465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2328-2_0_6_line_97 |  | 94 | 95 | 0.0035669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2328-2_0_6_line_98 |  | 95 | 97 | 0.050252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2328-2_0_6_line_99 |  | 96 | 104 | 0.029769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2328-2_0_6_line_100 |  | 97 | 100 | 0.026057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2328-2_0_6_line_101 |  | 97 | 98 | 0.026592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2328-2_0_6_line_102 |  | 98 | 99 | 0.0097351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2328-2_0_6_line_103 |  | 99 | 104 | 0.013125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2328-2_0_6_line_104 |  | 100 | 105 | 0.079726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2328-2_0_6_line_105 |  | 101 | 102 | 0.017773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2328-2_0_6_line_106 |  | 102 | 103 | 0.016934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2328-2_0_6_line_107 |  | 104 | 107 | 0.010623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2328-2_0_6_line_108 |  | 105 | 106 | 0.016853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2328-2_0_6_line_109 |  | 107 | 108 | 0.00057043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2328-2_0_6_line_110 |  | 108 | 109 | 0.022215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2328-2_0_6_line_111 |  | 109 | 110 | 0.007572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2328-2_0_6_line_112 |  | 110 | 111 | 0.017112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2328-2_0_6_line_113 |  | 111 | 114 | 0.0077113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2328-2_0_6_line_114 |  | 112 | 113 | 0.0048688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2328-2_0_6_line_115 |  | 112 | 114 | 0.021094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2328-2_0_6_line_116 |  | 113 | 115 | 0.024675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2328-2_0_6_line_117 |  | 115 | 116 | 0.0059424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2328-2_0_6_line_118 |  | 116 | 117 | 0.017238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2328-2_0_6_line_119 |  | 117 | 118 | 0.011693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2328-2_0_6_line_120 |  | 118 | 119 | 0.012632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2328-2_0_6_line_121 |  | 119 | 120 | 0.02733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2328-2_0_6_line_122 |  | 120 | 121 | 0.0020916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2328-2_0_6_line_123 |  | 121 | 122 | 0.032473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2328-2_0_6_line_124 |  | 122 | 130 | 0.0018252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2328-2_0_6_line_125 |  | 123 | 124 | 0.0086973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
126 | LV_2328-2_0_6_line_126 |  | 123 | 125 | 0.019164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_2328-2_0_6_line_127 |  | 124 | 126 | 0.02095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
128 | LV_2328-2_0_6_line_128 |  | 125 | 127 | 0.010233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
129 | LV_2328-2_0_6_line_129 |  | 127 | 128 | 0.027668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_2328-2_0_6_line_130 |  | 128 | 129 | 0.01266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
131 | LV_2328-2_0_6_line_131 |  | 129 | 143 | 0.0052561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
132 | LV_2328-2_0_6_line_132 |  | 130 | 131 | 0.041526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2328-2_0_6_line_133 |  | 130 | 132 | 0.027656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2328-2_0_6_line_134 |  | 134 | 135 | 0.004984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
135 | LV_2328-2_0_6_line_135 |  | 135 | 136 | 0.032455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
136 | LV_2328-2_0_6_line_136 |  | 136 | 137 | 0.010585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
137 | LV_2328-2_0_6_line_137 |  | 137 | 141 | 0.014378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
138 | LV_2328-2_0_6_line_138 |  | 137 | 140 | 0.037295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2328-2_0_6_line_139 |  | 138 | 139 | 0.00056444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2328-2_0_6_line_140 |  | 138 | 140 | 0.023568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2328-2_0_6_line_141 |  | 141 | 142 | 0.026521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
142 | LV_2328-2_0_6_line_142 |  | 142 | 143 | 0.0016393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2328-2_0_6_trafo_132 | 0.63 MVA 20/0.4 kV | 144 | 136 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2553292.1738 | 1152893.9078 | 2553285.6215 | 1152870.3565
1 | 2553292.1738 | 1152893.9078 | 2553328.0392 | 1152896.5496
2 | 2553259.7959 | 1152909.0452 | 2553284.2638 | 1152899.9502 | 2553292.9203 | 1152897.1481 | 2553292.1738 | 1152893.9078
3 | 2553328.0392 | 1152896.5496 | 2553328.3504 | 1152896.5726 | 2553331.7517 | 1152896.2435
4 | 2553259.7959 | 1152909.0452 | 2553256.8579 | 1152910.1353 | 2553247.6154 | 1152913.5645 | 2553234.7681 | 1152919.1563 | 2553228.5635 | 1152924.4518
5 | 2553259.7959 | 1152909.0452 | 2553261.9781 | 1152942.8254
6 | 2553352.2322 | 1152886.8383 | 2553339.3133 | 1152894.3418 | 2553334.2236 | 1152896.0044 | 2553331.7517 | 1152896.2435
7 | 2553224.1914 | 1152902.9857 | 2553226.3838 | 1152917.4873 | 2553228.5635 | 1152924.4518
8 | 2553228.5635 | 1152924.4518 | 2553222.7629 | 1152929.4106 | 2553211.6369 | 1152945.4973
9 | 2553261.9781 | 1152942.8254 | 2553262.5701 | 1152951.9904 | 2553262.6252 | 1152952.7209
10 | 2553354.4838 | 1152885.5306 | 2553352.2322 | 1152886.8383
11 | 2553321.2125 | 1152943.8421 | 2553323.2046 | 1152943.4502
12 | 2553304.3891 | 1152947.1516 | 2553321.2125 | 1152943.8421
13 | 2553262.6252 | 1152952.7209 | 2553304.3891 | 1152947.1516
14 | 2553211.6369 | 1152945.4973 | 2553207.5572 | 1152951.396 | 2553204.2754 | 1152963.0376
15 | 2553262.6252 | 1152952.7209 | 2553264.4349 | 1152976.7006
16 | 2553438.5736 | 1152833.0401 | 2553448.8573 | 1152823.5107
17 | 2553428.0864 | 1152840.2362 | 2553438.5736 | 1152833.0401
18 | 2553438.5736 | 1152833.0401 | 2553427.2141 | 1152817.2941
19 | 2553428.0864 | 1152840.2362 | 2553444.6179 | 1152860.4742 | 2553446.5799 | 1152864.1275 | 2553447.2345 | 1152868.7024
20 | 2553428.0864 | 1152840.2362 | 2553411.208 | 1152850.623
21 | 2553442.8625 | 1152891.2694 | 2553446.6981 | 1152878.3896 | 2553447.6588 | 1152871.6675 | 2553447.2345 | 1152868.7024
22 | 2553411.208 | 1152850.623 | 2553394.7433 | 1152860.7552
23 | 2553442.8625 | 1152891.2694 | 2553438.8125 | 1152904.8694
24 | 2553392.0608 | 1152862.406 | 2553394.7433 | 1152860.7552
25 | 2553354.4838 | 1152885.5306 | 2553370.1307 | 1152875.9016
26 | 2553354.4838 | 1152885.5306 | 2553359.0487 | 1152893.3548 | 2553359.7602 | 1152895.0571
27 | 2553372.0434 | 1152874.7245 | 2553370.1307 | 1152875.9016
28 | 2553369.1172 | 1152917.443 | 2553359.7602 | 1152895.0571
29 | 2553372.0434 | 1152874.7245 | 2553392.0608 | 1152862.406
30 | 2553369.1172 | 1152917.443 | 2553369.5918 | 1152918.5784
31 | 2553434.6944 | 1152918.6977 | 2553438.8125 | 1152904.8694
32 | 2552982.7638 | 1153016.7733 | 2553059.9417 | 1152945.0482
33 | 2553204.2754 | 1152963.0376 | 2553059.9417 | 1152945.0482
34 | 2552982.7638 | 1153016.7733 | 2552988.6554 | 1153024.3535 | 2552991.9239 | 1153032.1764 | 2552992.6576 | 1153035.0714
35 | 2553204.2754 | 1152963.0376 | 2553202.353 | 1152969.8572 | 2553202.4602 | 1152983.6168
36 | 2552992.6576 | 1153035.0714 | 2552993.7291 | 1153039.2994 | 2552993.9454 | 1153048.3135 | 2552992.2393 | 1153053.8519 | 2552987.0232 | 1153057.9615 | 2552978.276 | 1153059.9199 | 2552968.7849 | 1153058.9825 | 2552964.6594 | 1153058.5252
37 | 2553202.7299 | 1152988.7049 | 2553202.4911 | 1152987.5875 | 2553202.4602 | 1152983.6168
38 | 2553044.3049 | 1153074.0776 | 2553036.702 | 1153077.1386 | 2553024.7499 | 1153079.3999 | 2553005.4523 | 1153081.3295 | 2553005.4523 | 1153081.3295
39 | 2553044.3049 | 1153074.0776 | 2553046.8858 | 1153083.2622 | 2553049.3407 | 1153094.2621
40 | 2552980.9322 | 1153075.5343 | 2552988.8434 | 1153077.7909 | 2553005.4523 | 1153081.3295
41 | 2553049.3407 | 1153094.2621 | 2553041.6279 | 1153137.3672
42 | 2552958.8313 | 1153067.5649 | 2552967.4112 | 1153071.6777 | 2552980.9322 | 1153075.5343
43 | 2553212.0599 | 1153015.5216 | 2553216.2476 | 1153024.1094
44 | 2553212.0599 | 1153015.5216 | 2553205.6526 | 1153002.3817 | 2553202.7299 | 1152988.7049
45 | 2553216.2476 | 1153024.1094 | 2553219.5478 | 1153030.8772 | 2553228.7228 | 1153050.3381
46 | 2552958.8313 | 1153067.5649 | 2552957.5729 | 1153061.6828 | 2552960.1684 | 1153058.0273 | 2552964.6594 | 1153058.5252
47 | 2553264.8567 | 1152982.2899 | 2553264.4349 | 1152976.7006
48 | 2553264.8567 | 1152982.2899 | 2553265.4703 | 1152990.4211 | 2553268.3644 | 1153004.8087
49 | 2553384.0535 | 1153312.2673 | 2553374.242 | 1153308.5303 | 2553340.4625 | 1153307.9367 | 2553333.8343 | 1153307.6542
50 | 2553282.0781 | 1153301.5759 | 2553289.9873 | 1153305.3497 | 2553304.5399 | 1153308.0047 | 2553319.5017 | 1153307.0435 | 2553333.8343 | 1153307.6542
51 | 2553384.0535 | 1153312.2673 | 2553384.1314 | 1153306.4859 | 2553384.3688 | 1153286.7612
52 | 2553384.0535 | 1153312.2673 | 2553504.8659 | 1153332.0193
53 | 2553282.0781 | 1153301.5759 | 2553283.138 | 1153289.8727 | 2553284.5525 | 1153278.3891
54 | 2553282.0781 | 1153301.5759 | 2553215.5035 | 1153355.8443
55 | 2553384.3688 | 1153286.7612 | 2553384.5128 | 1153274.7947
56 | 2553504.8659 | 1153332.0193 | 2553514.2471 | 1153344.6088 | 2553518.8961 | 1153350.4759 | 2553519.7074 | 1153355.8191
57 | 2553168.8609 | 1153289.7733 | 2553215.5035 | 1153355.8443
58 | 2553384.5128 | 1153274.7947 | 2553402.1265 | 1153235.6428
59 | 2553168.8609 | 1153289.7733 | 2553167.106 | 1153284.1396 | 2553167.4659 | 1153275.1877 | 2553167.8816 | 1153269.4224
60 | 2553168.3584 | 1153262.8098 | 2553167.8816 | 1153269.4224
61 | 2553383.7523 | 1153213.1514 | 2553394.3166 | 1153214.0033 | 2553400.1449 | 1153218.5716 | 2553402.0298 | 1153223.1816 | 2553402.1265 | 1153235.6428
62 | 2553383.7523 | 1153213.1514 | 2553380.6524 | 1153193.3652 | 2553378.6999 | 1153183.5078
63 | 2553374.0481 | 1153160.0214 | 2553378.6999 | 1153183.5078
64 | 2553340.4879 | 1153202.6551 | 2553378.6999 | 1153183.5078
65 | 2553374.0481 | 1153160.0214 | 2553387.2369 | 1153160.084
66 | 2553340.4879 | 1153202.6551 | 2553333.0607 | 1153175.4372
67 | 2553341.4697 | 1153206.2529 | 2553340.4879 | 1153202.6551
68 | 2553343.9176 | 1153230.8249 | 2553342.0602 | 1153208.417 | 2553341.4697 | 1153206.2529
69 | 2553343.9176 | 1153230.8249 | 2553344.0782 | 1153232.7629
70 | 2553387.2369 | 1153160.084 | 2553415.0565 | 1153160.2163
71 | 2553333.0607 | 1153175.4372 | 2553328.2867 | 1153157.9422 | 2553324.8438 | 1153149.592
72 | 2553345.252 | 1153246.9233 | 2553344.0782 | 1153232.7629
73 | 2553323.0042 | 1153145.1302 | 2553324.8438 | 1153149.592
74 | 2553323.0042 | 1153145.1302 | 2553314.5249 | 1153124.5652
75 | 2553419.6696 | 1153160.2382 | 2553415.0565 | 1153160.2163
76 | 2553314.5249 | 1153124.5652 | 2553314.0825 | 1153123.4921
77 | 2553288.0889 | 1153196.419 | 2553281.7855 | 1153196.8793 | 2553277.995 | 1153201.7891 | 2553278.5883 | 1153207.0428 | 2553280.3776 | 1153208.7924
78 | 2553288.0889 | 1153196.419 | 2553289.4229 | 1153192.3398 | 2553288.4092 | 1153185.3107
79 | 2553288.0889 | 1153196.419 | 2553281.7855 | 1153196.8793 | 2553277.995 | 1153201.7891
80 | 2553281.9148 | 1153164.4469 | 2553288.4092 | 1153185.3107
81 | 2553281.9148 | 1153164.4469 | 2553278.3914 | 1153153.1274 | 2553265.1255 | 1153127.5506 | 2553259.9401 | 1153116.5519
82 | 2553257.6376 | 1153111.6683 | 2553259.9401 | 1153116.5519
83 | 2553257.6376 | 1153111.6683 | 2553246.5223 | 1153088.092
84 | 2553236.3334 | 1153066.4807 | 2553246.5223 | 1153088.092
85 | 2553236.3334 | 1153066.4807 | 2553228.7228 | 1153050.3381
86 | 2553314.0825 | 1153123.4921 | 2553307.5708 | 1153107.6992 | 2553303.4941 | 1153098.205
87 | 2553292.7555 | 1153073.196 | 2553303.4941 | 1153098.205
88 | 2553281.3612 | 1153046.6601 | 2553292.7555 | 1153073.196
89 | 2553281.3612 | 1153046.6601 | 2553297.7686 | 1153041.746
90 | 2553326.2127 | 1153033.2268 | 2553297.7686 | 1153041.746
91 | 2553420.6351 | 1153160.2428 | 2553419.6696 | 1153160.2382
92 | 2553434.4595 | 1153160.3085 | 2553420.6351 | 1153160.2428
93 | 2553422.5146 | 1153100.0104 | 2553428.686 | 1153100.5254
94 | 2553400.4953 | 1153098.1732 | 2553422.5146 | 1153100.0104
95 | 2553429.9176 | 1153100.6281 | 2553428.686 | 1153100.5254
96 | 2553400.4953 | 1153098.1732 | 2553395.4662 | 1153097.7535
97 | 2553438.0263 | 1153160.3254 | 2553434.4595 | 1153160.3085
98 | 2553485.6146 | 1153144.1831 | 2553438.0263 | 1153160.3254
99 | 2553459.5276 | 1153102.1731 | 2553456.3254 | 1153102.8316 | 2553429.9176 | 1153100.6281
100 | 2553497.4881 | 1153167.3589 | 2553487.6072 | 1153147.3569 | 2553485.6146 | 1153144.1831
101 | 2553471.4752 | 1153121.6615 | 2553485.6146 | 1153144.1831
102 | 2553471.4752 | 1153121.6615 | 2553468.4652 | 1153116.8671 | 2553466.348 | 1153113.3863
103 | 2553459.5276 | 1153102.1731 | 2553466.348 | 1153113.3863
104 | 2553497.4881 | 1153167.3589 | 2553577.0578 | 1153162.3619
105 | 2553377.7548 | 1153096.2757 | 2553395.4662 | 1153097.7535
106 | 2553377.7548 | 1153096.2757 | 2553360.8796 | 1153094.8677
107 | 2553459.5276 | 1153102.1731 | 2553461.3876 | 1153097.6341 | 2553462.4435 | 1153092.015
108 | 2553577.0578 | 1153162.3619 | 2553582.255 | 1153157.7416 | 2553584.6093 | 1153148.1263
109 | 2553462.5488 | 1153091.4544 | 2553462.4435 | 1153092.015
110 | 2553462.5488 | 1153091.4544 | 2553466.6513 | 1153069.6217
111 | 2553468.0496 | 1153062.18 | 2553466.6513 | 1153069.6217
112 | 2553468.0496 | 1153062.18 | 2553470.0462 | 1153051.5542 | 2553471.3146 | 1153045.3827
113 | 2553472.8669 | 1153037.8292 | 2553471.3146 | 1153045.3827
114 | 2553478.0935 | 1153012.3975 | 2553477.1134 | 1153017.1666
115 | 2553472.8669 | 1153037.8292 | 2553477.1134 | 1153017.1666
116 | 2553478.0935 | 1153012.3975 | 2553483.0607 | 1152988.2278
117 | 2553483.0607 | 1152988.2278 | 2553484.2569 | 1152982.407
118 | 2553484.2569 | 1152982.407 | 2553487.7272 | 1152965.5214
119 | 2553490.081 | 1152954.068 | 2553487.7272 | 1152965.5214
120 | 2553490.081 | 1152954.068 | 2553492.6239 | 1152941.6947
121 | 2553498.1255 | 1152914.9245 | 2553492.6239 | 1152941.6947
122 | 2553498.1255 | 1152914.9245 | 2553498.5466 | 1152912.8757
123 | 2553498.5466 | 1152912.8757 | 2553503.8904 | 1152886.8734 | 2553504.0381 | 1152880.9481
124 | 2553504.0836 | 1152879.1234 | 2553504.0381 | 1152880.9481
125 | 2553426.2327 | 1152947.1123 | 2553428.715 | 1152938.7768
126 | 2553420.7632 | 1152965.4788 | 2553426.2327 | 1152947.1123
127 | 2553434.6944 | 1152918.6977 | 2553428.715 | 1152938.7768
128 | 2553420.7632 | 1152965.4788 | 2553417.8427 | 1152975.286
129 | 2553409.9459 | 1153001.8035 | 2553417.8427 | 1152975.286
130 | 2553409.9459 | 1153001.8035 | 2553406.3327 | 1153013.9365
131 | 2553406.3327 | 1153013.9365 | 2553404.8325 | 1153018.974
132 | 2553504.0836 | 1152879.1234 | 2553501.4829 | 1152858.3661 | 2553499.7818 | 1152853.7213 | 2553497.4429 | 1152852.9057 | 2553495.9532 | 1152854.7515 | 2553494.0406 | 1152865.394
133 | 2553512.5351 | 1152852.7888 | 2553504.0836 | 1152879.1234
134 | 2553327.6233 | 1153038.0072 | 2553326.2127 | 1153033.2268
135 | 2553327.6233 | 1153038.0072 | 2553360.055 | 1153036.7829
136 | 2553370.6329 | 1153036.3836 | 2553360.055 | 1153036.7829
137 | 2553370.6329 | 1153036.3836 | 2553385.0002 | 1153035.8385
138 | 2553370.6329 | 1153036.3836 | 2553371.6848 | 1153012.7521 | 2553369.9301 | 1152999.2253
139 | 2553346.6168 | 1153001.2595 | 2553346.0603 | 1153001.3538
140 | 2553369.9301 | 1152999.2253 | 2553362.4745 | 1152998.5717 | 2553346.6168 | 1153001.2595
141 | 2553404.355 | 1153020.5418 | 2553402.0836 | 1153026.39 | 2553398.6195 | 1153030.8748 | 2553391.8622 | 1153034.1733 | 2553385.0002 | 1153035.8385 | 2553385.0002 | 1153035.8385
142 | 2553404.355 | 1153020.5418 | 2553404.4006 | 1153020.4245 | 2553404.8325 | 1153018.974

## bus_geodata
| x | y | coords
0 | 2553285.6215 | 1152870.3565
1 | 2553292.1738 | 1152893.9078
2 | 2553328.0392 | 1152896.5496
3 | 2553259.7959 | 1152909.0452
4 | 2553331.7517 | 1152896.2435
5 | 2553228.5635 | 1152924.4518
6 | 2553261.9781 | 1152942.8254
7 | 2553352.2322 | 1152886.8383
8 | 2553321.2125 | 1152943.8421
9 | 2553323.2046 | 1152943.4502
10 | 2553304.3891 | 1152947.1516
11 | 2553224.1914 | 1152902.9857
12 | 2553211.6369 | 1152945.4973
13 | 2553262.6252 | 1152952.7209
14 | 2553448.8573 | 1152823.5107
15 | 2553438.5736 | 1152833.0401
16 | 2553428.0864 | 1152840.2362
17 | 2553427.2141 | 1152817.2941
18 | 2553447.2345 | 1152868.7024
19 | 2553411.208 | 1152850.623
20 | 2553442.8625 | 1152891.2694
21 | 2553394.7433 | 1152860.7552
22 | 2553354.4838 | 1152885.5306
23 | 2553370.1307 | 1152875.9016
24 | 2553359.7602 | 1152895.0571
25 | 2553372.0434 | 1152874.7245
26 | 2553369.1172 | 1152917.443
27 | 2553392.0608 | 1152862.406
28 | 2553369.5918 | 1152918.5784
29 | 2553438.8125 | 1152904.8694
30 | 2553059.9417 | 1152945.0482
31 | 2552982.7638 | 1153016.7733
32 | 2553204.2754 | 1152963.0376
33 | 2552992.6576 | 1153035.0714
34 | 2553202.4602 | 1152983.6168
35 | 2553044.3049 | 1153074.0776
36 | 2553005.4523 | 1153081.3295
37 | 2553049.3407 | 1153094.2621
38 | 2552980.9322 | 1153075.5343
39 | 2553041.6279 | 1153137.3672
40 | 2553212.0599 | 1153015.5216
41 | 2553216.2476 | 1153024.1094
42 | 2553202.7299 | 1152988.7049
43 | 2552958.8313 | 1153067.5649
44 | 2553264.4349 | 1152976.7006
45 | 2553264.8567 | 1152982.2899
46 | 2553268.3644 | 1153004.8087
47 | 2552964.6594 | 1153058.5252
48 | 2553333.8343 | 1153307.6542
49 | 2553384.0535 | 1153312.2673
50 | 2553282.0781 | 1153301.5759
51 | 2553384.3688 | 1153286.7612
52 | 2553504.8659 | 1153332.0193
53 | 2553284.5525 | 1153278.3891
54 | 2553215.5035 | 1153355.8443
55 | 2553384.5128 | 1153274.7947
56 | 2553519.7074 | 1153355.8191
57 | 2553168.8609 | 1153289.7733
58 | 2553167.8816 | 1153269.4224
59 | 2553402.1265 | 1153235.6428
60 | 2553168.3584 | 1153262.8098
61 | 2553383.7523 | 1153213.1514
62 | 2553378.6999 | 1153183.5078
63 | 2553374.0481 | 1153160.0213
64 | 2553340.4879 | 1153202.6551
65 | 2553341.4697 | 1153206.2529
66 | 2553343.9176 | 1153230.8249
67 | 2553387.2369 | 1153160.084
68 | 2553333.0607 | 1153175.4372
69 | 2553344.0782 | 1153232.7629
70 | 2553345.252 | 1153246.9233
71 | 2553324.8438 | 1153149.592
72 | 2553323.0042 | 1153145.1302
73 | 2553415.0565 | 1153160.2163
74 | 2553314.5249 | 1153124.5652
75 | 2553280.3776 | 1153208.7924
76 | 2553288.0889 | 1153196.419
77 | 2553288.4092 | 1153185.3107
78 | 2553277.995 | 1153201.7891
79 | 2553281.9148 | 1153164.4469
80 | 2553259.9401 | 1153116.5519
81 | 2553257.6376 | 1153111.6683
82 | 2553246.5223 | 1153088.092
83 | 2553236.3334 | 1153066.4807
84 | 2553314.0825 | 1153123.4921
85 | 2553303.4941 | 1153098.205
86 | 2553292.7555 | 1153073.196
87 | 2553281.3612 | 1153046.6601
88 | 2553297.7685 | 1153041.746
89 | 2553419.6696 | 1153160.2382
90 | 2553420.6351 | 1153160.2428
91 | 2553422.5146 | 1153100.0104
92 | 2553428.686 | 1153100.5254
93 | 2553400.4953 | 1153098.1732
94 | 2553434.4595 | 1153160.3085
95 | 2553438.0263 | 1153160.3254
96 | 2553429.9176 | 1153100.6281
97 | 2553485.6146 | 1153144.1831
98 | 2553471.4752 | 1153121.6615
99 | 2553466.348 | 1153113.3863
100 | 2553497.4881 | 1153167.3589
101 | 2553395.4662 | 1153097.7535
102 | 2553377.7548 | 1153096.2757
103 | 2553360.8796 | 1153094.8677
104 | 2553459.5276 | 1153102.1731
105 | 2553577.0578 | 1153162.3619
106 | 2553584.6093 | 1153148.1263
107 | 2553462.4435 | 1153092.015
108 | 2553462.5488 | 1153091.4544
109 | 2553466.6513 | 1153069.6217
110 | 2553468.0496 | 1153062.18
111 | 2553471.3146 | 1153045.3827
112 | 2553477.1134 | 1153017.1666
113 | 2553478.0935 | 1153012.3975
114 | 2553472.8669 | 1153037.8292
115 | 2553483.0607 | 1152988.2278
116 | 2553484.2569 | 1152982.407
117 | 2553487.7272 | 1152965.5214
118 | 2553490.081 | 1152954.068
119 | 2553492.6239 | 1152941.6947
120 | 2553498.1255 | 1152914.9245
121 | 2553498.5466 | 1152912.8757
122 | 2553504.0382 | 1152880.9481
123 | 2553426.2327 | 1152947.1123
124 | 2553428.715 | 1152938.7768
125 | 2553420.7632 | 1152965.4788
126 | 2553434.6944 | 1152918.6977
127 | 2553417.8427 | 1152975.286
128 | 2553409.9459 | 1153001.8035
129 | 2553406.3327 | 1153013.9365
130 | 2553504.0836 | 1152879.1234
131 | 2553494.0406 | 1152865.394
132 | 2553512.5351 | 1152852.7888
133 | 2553228.7228 | 1153050.3381
134 | 2553326.2127 | 1153033.2268
135 | 2553327.6233 | 1153038.0072
136 | 2553360.055 | 1153036.7829
137 | 2553370.6329 | 1153036.3836
138 | 2553346.6168 | 1153001.2595
139 | 2553346.0603 | 1153001.3538
140 | 2553369.9301 | 1152999.2253
141 | 2553385.0002 | 1153035.8385
142 | 2553404.355 | 1153020.5418
143 | 2553404.8325 | 1153018.974
144 | 2553370.6329 | 1153036.3836

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98324 | -0.32072 | 0.0021027 | 0.00052699
1 | 0.98329 | -0.31979 | 0 | 0
2 | 0.98442 | -0.29784 | 0.0031835 | 0.00079785
3 | 0.98151 | -0.35444 | 0 | 0
4 | 0.98454 | -0.29549 | 0.0022088 | 0.00055359
5 | 0.98029 | -0.37809 | 0 | 0
6 | 0.98071 | -0.36997 | 0.004103 | 0.0010283
7 | 0.9853 | -0.28088 | 0.0011944 | 0.00029934
8 | 0.98029 | -0.37824 | 0.0019424 | 0.00048681
9 | 0.98029 | -0.37832 | 0.0022086 | 0.00055352
10 | 0.98036 | -0.37695 | 0 | 0
11 | 0.98013 | -0.38121 | 0.0078161 | 0.0019589
12 | 0.97861 | -0.41092 | 0.0028941 | 0.00072533
13 | 0.98052 | -0.37378 | 0.0045859 | 0.0011493
14 | 0.98854 | -0.21837 | 0.0028059 | 0.00070322
15 | 0.98857 | -0.21767 | 0 | 0
16 | 0.98863 | -0.21662 | 0 | 0
17 | 0.98854 | -0.2183 | 0.001836 | 0.00046015
18 | 0.99005 | -0.18933 | 0.0024275 | 0.00060838
19 | 0.98785 | -0.2316 | 0.0024325 | 0.00060964
20 | 0.99101 | -0.17088 | 0.0033483 | 0.00083917
21 | 0.9871 | -0.24596 | 0.0022331 | 0.00055967
22 | 0.98538 | -0.27919 | 0 | 0
23 | 0.98603 | -0.26669 | 0.0027344 | 0.0006853
24 | 0.98533 | -0.28028 | 0.0010462 | 0.00026221
25 | 0.98611 | -0.26512 | 0.003683 | 0.00092304
26 | 0.98523 | -0.28223 | 0.0018153 | 0.00045495
27 | 0.98699 | -0.24825 | 0.0021546 | 0.00054
28 | 0.98523 | -0.28228 | 0.0026625 | 0.00066727
29 | 0.99161 | -0.15935 | 0.0047853 | 0.0011993
30 | 0.97514 | -0.47891 | 0.0029112 | 0.00072962
31 | 0.97374 | -0.50649 | 0.00069031 | 0.00017301
32 | 0.97747 | -0.43324 | 0.0043732 | 0.001096
33 | 0.97348 | -0.51174 | 0.0010756 | 0.00026957
34 | 0.97666 | -0.44922 | 0.0051392 | 0.001288
35 | 0.97204 | -0.54013 | 0 | 0
36 | 0.97233 | -0.53443 | 0.00073457 | 0.0001841
37 | 0.97189 | -0.54312 | 0.00098201 | 0.00024612
38 | 0.97253 | -0.53048 | 0.0021797 | 0.00054629
39 | 0.97161 | -0.5486 | 0.0067894 | 0.0017016
40 | 0.97562 | -0.46958 | 0.0036108 | 0.00090496
41 | 0.97537 | -0.47461 | 0.0021008 | 0.00052651
42 | 0.97648 | -0.45267 | 0.0045497 | 0.0011403
43 | 0.97276 | -0.52584 | 0 | 0
44 | 0.98024 | -0.37922 | 0.0045971 | 0.0011521
45 | 0.9802 | -0.38003 | 0.0047514 | 0.0011908
46 | 0.98013 | -0.38132 | 0.0031344 | 0.00078556
47 | 0.97291 | -0.52288 | 0.0017971 | 0.0004504
48 | 0.98634 | -0.26135 | 0.0016764 | 0.00042014
49 | 0.98673 | -0.25377 | 0 | 0
50 | 0.98602 | -0.26764 | 0 | 0
51 | 0.98697 | -0.24912 | 0.0012188 | 0.00030547
52 | 0.98652 | -0.25786 | 0 | 0
53 | 0.98599 | -0.26811 | 0.0011175 | 0.00028007
54 | 0.98558 | -0.27614 | 0.00322 | 0.00080702
55 | 0.98709 | -0.24668 | 0.0010669 | 0.00026738
56 | 0.98647 | -0.25881 | 0.0018605 | 0.00046629
57 | 0.98541 | -0.27946 | 0 | 0
58 | 0.98537 | -0.28031 | 0.0015128 | 0.00037914
59 | 0.98758 | -0.23711 | 0.0039551 | 0.00099125
60 | 0.98536 | -0.2804 | 0.00077641 | 0.00019459
61 | 0.98812 | -0.22673 | 0 | 0
62 | 0.98857 | -0.21791 | 0.0020113 | 0.00050409
63 | 0.98792 | -0.23048 | 0 | 0
64 | 0.98998 | -0.19084 | 0.001365 | 0.00034211
65 | 0.98996 | -0.19127 | 0.0020534 | 0.00051463
66 | 0.98986 | -0.19316 | 0.00105 | 0.00026314
67 | 0.98756 | -0.23742 | 0.0018083 | 0.0004532
68 | 0.99097 | -0.17173 | 0.0027789 | 0.00069645
69 | 0.98985 | -0.19327 | 0.0010853 | 0.00027201
70 | 0.98983 | -0.19382 | 0.0021676 | 0.00054326
71 | 0.99196 | -0.15291 | 0.0027628 | 0.00069243
72 | 0.99214 | -0.14949 | 0.0033805 | 0.00084725
73 | 0.98644 | -0.25893 | 0.0023276 | 0.00058334
74 | 0.99298 | -0.13331 | 0.0028106 | 0.00070441
75 | 0.97277 | -0.52575 | 0.0010179 | 0.00025511
76 | 0.97279 | -0.52537 | 0 | 0
77 | 0.97284 | -0.52451 | 0.0019633 | 0.00049206
78 | 0.97276 | -0.52608 | 0.0030841 | 0.00077294
79 | 0.97296 | -0.52206 | 0.002594 | 0.00065012
80 | 0.97339 | -0.51364 | 0.0030844 | 0.00077302
81 | 0.97344 | -0.51248 | 0.0038747 | 0.00097109
82 | 0.97382 | -0.50499 | 0.0035684 | 0.00089433
83 | 0.97425 | -0.49657 | 0.0045871 | 0.0011496
84 | 0.99303 | -0.13245 | 0.003111 | 0.00077969
85 | 0.99412 | -0.11159 | 0.0028395 | 0.00071165
86 | 0.99523 | -0.090477 | 0.0031196 | 0.00078184
87 | 0.99643 | -0.067597 | 0 | 0
88 | 0.99714 | -0.054054 | 0.0029558 | 0.00074078
89 | 0.98608 | -0.26588 | 0.00083346 | 0.00020888
90 | 0.98601 | -0.26732 | 0.0019744 | 0.00049484
91 | 0.97793 | -0.42441 | 0.0019126 | 0.00047935
92 | 0.978 | -0.42313 | 0.0011242 | 0.00028174
93 | 0.97774 | -0.42821 | 0.0019965 | 0.00050038
94 | 0.98496 | -0.28749 | 0.0011566 | 0.00028987
95 | 0.9847 | -0.29263 | 0.0048064 | 0.0012046
96 | 0.97801 | -0.42285 | 0.0012976 | 0.00032522
97 | 0.98118 | -0.36093 | 0.0017609 | 0.00044133
98 | 0.97965 | -0.39083 | 0.0019541 | 0.00048974
99 | 0.9791 | -0.40146 | 0.0017657 | 0.00044252
100 | 0.9809 | -0.36638 | 0.0019351 | 0.00048499
101 | 0.97771 | -0.42889 | 0.0017998 | 0.00045107
102 | 0.97761 | -0.43072 | 0.003108 | 0.00077893
103 | 0.97757 | -0.4315 | 0.0025263 | 0.00063315
104 | 0.97839 | -0.41538 | 0 | 0
105 | 0.98019 | -0.38028 | 0 | 0
106 | 0.98004 | -0.38321 | 0.0096135 | 0.0024094
107 | 0.97795 | -0.424 | 0.0016856 | 0.00042246
108 | 0.97793 | -0.42445 | 0.0019276 | 0.0004831
109 | 0.97708 | -0.44103 | 0.0013761 | 0.00034489
110 | 0.97681 | -0.4465 | 0.0033039 | 0.00082805
111 | 0.97623 | -0.45783 | 0.0019946 | 0.00049989
112 | 0.97535 | -0.47512 | 0.0023154 | 0.0005803
113 | 0.97521 | -0.47779 | 0.0021991 | 0.00055116
114 | 0.97598 | -0.46266 | 0.001987 | 0.00049798
115 | 0.97458 | -0.49034 | 0.0023164 | 0.00058054
116 | 0.97444 | -0.49312 | 0.0031735 | 0.00079536
117 | 0.97408 | -0.50016 | 0.0028321 | 0.0007098
118 | 0.97387 | -0.50433 | 0.0026498 | 0.0006641
119 | 0.97367 | -0.50823 | 0.0017935 | 0.0004495
120 | 0.97329 | -0.51575 | 0.0037561 | 0.00094138
121 | 0.97327 | -0.51618 | 0.0034519 | 0.00086513
122 | 0.97303 | -0.52083 | 0.0027237 | 0.00068263
123 | 0.99359 | -0.12152 | 0.0028914 | 0.00072466
124 | 0.99319 | -0.12922 | 0.0046075 | 0.0011548
125 | 0.9945 | -0.10426 | 0.0021375 | 0.00053571
126 | 0.99225 | -0.14723 | 0.0034752 | 0.00087096
127 | 0.99499 | -0.094919 | 0.003027 | 0.00075863
128 | 0.99634 | -0.06923 | 0.00074514 | 0.00018675
129 | 0.99696 | -0.057444 | 0.002746 | 0.00068822
130 | 0.97302 | -0.52099 | 0 | 0
131 | 0.9729 | -0.52342 | 0.0031706 | 0.00079463
132 | 0.97298 | -0.52195 | 0.001868 | 0.00046816
133 | 0.97465 | -0.48878 | 0.0028259 | 0.00070823
134 | 0.99841 | -0.030108 | 0 | 0
135 | 0.99862 | -0.026094 | 0 | 0
136 | 1 | 0 | -0.32462 | -0.082873
137 | 0.99941 | -0.011065 | 0 | 0
138 | 0.99888 | -0.021391 | 0.004538 | 0.0011373
139 | 0.99888 | -0.021428 | 0.0037768 | 0.00094657
140 | 0.99906 | -0.017968 | 0.0022859 | 0.0005729
141 | 0.99866 | -0.025228 | 0.0033261 | 0.0008336
142 | 0.99731 | -0.050892 | 0.0010764 | 0.00026976
143 | 0.99723 | -0.05247 | 0.002888 | 0.00072379
144 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0021027 | -0.00052699 | 0.0021028 | 0.00052673 | 9.2826e-08 | -2.5066e-07 | 0.0031822 | 0.0031821 | 0.0031822 | 0.98324 | -0.32072 | 0.98329 | -0.31979 | 0.87422
1 | -0.10231 | -0.025879 | 0.10242 | 0.025947 | 0.00010789 | 6.7677e-05 | 0.15492 | 0.15492 | 0.15492 | 0.98329 | -0.31979 | 0.98442 | -0.29784 | 14.1867
2 | 0.10021 | 0.025353 | -0.10005 | -0.025247 | 0.00016632 | 0.00010547 | 0.15174 | 0.15174 | 0.15174 | 0.98329 | -0.31979 | 0.98151 | -0.35444 | 20.8429
3 | -0.10561 | -0.026745 | 0.10562 | 0.026752 | 1.1893e-05 | 7.4695e-06 | 0.15973 | 0.15973 | 0.15973 | 0.98442 | -0.29784 | 0.98454 | -0.29549 | 14.6273
4 | 0.074696 | 0.018885 | -0.074611 | -0.018832 | 8.4631e-05 | 5.3276e-05 | 0.1133 | 0.1133 | 0.1133 | 0.98151 | -0.35444 | 0.98029 | -0.37809 | 15.5635
5 | 0.02535 | 0.0063619 | -0.025331 | -0.0063503 | 1.8752e-05 | 1.1574e-05 | 0.038435 | 0.038435 | 0.038435 | 0.98151 | -0.35444 | 0.98071 | -0.36997 | 10.5591
6 | -0.10783 | -0.027306 | 0.1079 | 0.027353 | 7.5711e-05 | 4.7585e-05 | 0.16307 | 0.16307 | 0.16307 | 0.98454 | -0.29549 | 0.9853 | -0.28088 | 14.933
7 | 0.0078172 | 0.0019594 | -0.0078161 | -0.0019589 | 1.1599e-06 | 4.6544e-07 | 0.011866 | 0.011866 | 0.011866 | 0.98029 | -0.37809 | 0.98013 | -0.38121 | 3.2599
8 | 0.066794 | 0.016873 | -0.066689 | -0.016806 | 0.00010491 | 6.6803e-05 | 0.10144 | 0.10144 | 0.10144 | 0.98029 | -0.37809 | 0.97861 | -0.41092 | 27.8671
9 | 0.021228 | 0.005322 | -0.021224 | -0.0053197 | 3.8581e-06 | 2.3441e-06 | 0.03221 | 0.03221 | 0.03221 | 0.98071 | -0.36997 | 0.98052 | -0.37378 | 8.8488
10 | -0.1091 | -0.027653 | 0.10911 | 0.027658 | 8.8471e-06 | 5.5626e-06 | 0.16487 | 0.16487 | 0.16487 | 0.9853 | -0.28088 | 0.98538 | -0.27919 | 15.0981
11 | 0.0022086 | 0.0005535 | -0.0022086 | -0.00055352 | 8.5567e-09 | -2.012e-08 | 0.0033524 | 0.0033524 | 0.0033524 | 0.98029 | -0.37824 | 0.98029 | -0.37832 | 0.921
12 | -0.004151 | -0.0010403 | 0.0041512 | 0.0010403 | 2.5526e-07 | -5.281e-08 | 0.0063009 | 0.0063008 | 0.0063009 | 0.98029 | -0.37824 | 0.98036 | -0.37695 | 1.731
13 | -0.0041512 | -0.0010403 | 0.0041518 | 0.0010401 | 6.2724e-07 | -1.2991e-07 | 0.0063008 | 0.0063006 | 0.0063008 | 0.98036 | -0.37695 | 0.98052 | -0.37378 | 1.731
14 | 0.063795 | 0.01608 | -0.063727 | -0.016037 | 6.8032e-05 | 4.3299e-05 | 0.097036 | 0.097036 | 0.097036 | 0.97861 | -0.41092 | 0.97747 | -0.43324 | 26.6581
15 | 0.012487 | 0.0031302 | -0.012483 | -0.0031285 | 3.2383e-06 | 1.7693e-06 | 0.01895 | 0.01895 | 0.01895 | 0.98052 | -0.37378 | 0.98024 | -0.37922 | 5.206
16 | -0.0028059 | -0.00070322 | 0.002806 | 0.0007031 | 9.3787e-08 | -1.1973e-07 | 0.0042236 | 0.0042235 | 0.0042236 | 0.98854 | -0.21837 | 0.98857 | -0.21767 | 1.1603
17 | -0.004642 | -0.001163 | 0.0046423 | 0.001163 | 2.3239e-07 | -1.4029e-08 | 0.0069871 | 0.0069871 | 0.0069871 | 0.98857 | -0.21767 | 0.98863 | -0.21662 | 1.9195
18 | 0.0018361 | 0.00045994 | -0.001836 | -0.00046015 | 5.561e-08 | -2.1334e-07 | 0.0027636 | 0.0027637 | 0.0027637 | 0.98857 | -0.21767 | 0.98854 | -0.2183 | 0.75926
19 | -0.13288 | -0.033756 | 0.13305 | 0.033867 | 0.00017478 | 0.00011052 | 0.20016 | 0.20016 | 0.20016 | 0.98863 | -0.21662 | 0.99005 | -0.18933 | 18.3299
20 | 0.12824 | 0.032593 | -0.12814 | -0.032535 | 9.2445e-05 | 5.8403e-05 | 0.19318 | 0.19318 | 0.19318 | 0.98863 | -0.21662 | 0.98785 | -0.2316 | 17.6901
21 | -0.13548 | -0.034475 | 0.1356 | 0.034551 | 0.00012059 | 7.628e-05 | 0.20381 | 0.20381 | 0.20381 | 0.99005 | -0.18933 | 0.99101 | -0.17088 | 18.664
22 | 0.12571 | 0.031925 | -0.12563 | -0.03187 | 8.6791e-05 | 5.4804e-05 | 0.18951 | 0.18951 | 0.18951 | 0.98785 | -0.2316 | 0.9871 | -0.24596 | 17.3546
23 | -0.13895 | -0.035391 | 0.13903 | 0.03544 | 7.736e-05 | 4.8962e-05 | 0.20884 | 0.20884 | 0.20884 | 0.99101 | -0.17088 | 0.99161 | -0.15935 | 19.1243
24 | 0.12339 | 0.031311 | -0.12338 | -0.031302 | 1.3643e-05 | 8.6104e-06 | 0.18615 | 0.18615 | 0.18615 | 0.9871 | -0.24596 | 0.98699 | -0.24825 | 17.0463
25 | -0.11463 | -0.029043 | 0.1147 | 0.029086 | 6.8903e-05 | 4.3396e-05 | 0.17321 | 0.17321 | 0.17321 | 0.98538 | -0.27919 | 0.98603 | -0.26669 | 15.8621
26 | 0.0055246 | 0.0013844 | -0.0055243 | -0.0013844 | 2.8458e-07 | 4.3244e-08 | 0.0083426 | 0.0083427 | 0.0083427 | 0.98538 | -0.27919 | 0.98533 | -0.28028 | 2.2919
27 | -0.11743 | -0.029771 | 0.11744 | 0.029777 | 8.829e-06 | 5.5646e-06 | 0.17734 | 0.17734 | 0.17734 | 0.98603 | -0.26669 | 0.98611 | -0.26512 | 16.24
28 | 0.0044781 | 0.0011222 | -0.0044777 | -0.0011222 | 4.1612e-07 | -4.2691e-08 | 0.0067627 | 0.0067628 | 0.0067628 | 0.98533 | -0.28028 | 0.98523 | -0.28223 | 1.8579
29 | -0.12113 | -0.0307 | 0.12122 | 0.030762 | 9.8281e-05 | 6.1999e-05 | 0.1829 | 0.1829 | 0.1829 | 0.98611 | -0.26512 | 0.98699 | -0.24825 | 16.7489
30 | 0.0026625 | 0.00066726 | -0.0026625 | -0.00066727 | 7.462e-09 | -1.0895e-08 | 0.0040212 | 0.0040212 | 0.0040212 | 0.98523 | -0.28223 | 0.98523 | -0.28228 | 1.1047
31 | -0.14381 | -0.036639 | 0.1439 | 0.036692 | 8.4161e-05 | 5.3304e-05 | 0.21602 | 0.21602 | 0.21602 | 0.99161 | -0.15935 | 0.99225 | -0.14723 | 19.7819
32 | 0.014288 | 0.003592 | -0.014269 | -0.0035812 | 1.8789e-05 | 1.0712e-05 | 0.021807 | 0.021807 | 0.021807 | 0.97514 | -0.47891 | 0.97374 | -0.50649 | 5.991
33 | -0.017199 | -0.0043216 | 0.017237 | 0.0043438 | 3.758e-05 | 2.2233e-05 | 0.026249 | 0.026248 | 0.026249 | 0.97514 | -0.47891 | 0.97747 | -0.43324 | 7.2113
34 | 0.013579 | 0.0034082 | -0.013576 | -0.0034063 | 3.402e-06 | 1.9153e-06 | 0.020752 | 0.020752 | 0.020752 | 0.97374 | -0.50649 | 0.97348 | -0.51174 | 5.7012
35 | 0.042117 | 0.010597 | -0.042085 | -0.010577 | 3.2149e-05 | 2.0314e-05 | 0.06413 | 0.06413 | 0.06413 | 0.97747 | -0.43324 | 0.97666 | -0.44922 | 17.6181
36 | 0.0125 | 0.0031367 | -0.012493 | -0.0031331 | 6.6361e-06 | 3.6449e-06 | 0.019108 | 0.019108 | 0.019108 | 0.97348 | -0.51174 | 0.97291 | -0.52288 | 5.2496
37 | 0.036945 | 0.0092889 | -0.036939 | -0.0092851 | 6.0779e-06 | 3.8259e-06 | 0.0563 | 0.0563 | 0.0563 | 0.97666 | -0.44922 | 0.97648 | -0.45267 | 15.467
38 | -0.0077743 | -0.0019487 | 0.0077764 | 0.0019496 | 2.1114e-06 | 8.5839e-07 | 0.011901 | 0.011901 | 0.011901 | 0.97204 | -0.54013 | 0.97233 | -0.53443 | 3.2695
39 | 0.0077743 | 0.0019487 | -0.0077732 | -0.0019483 | 1.1053e-06 | 4.4949e-07 | 0.011901 | 0.011901 | 0.011901 | 0.97204 | -0.54013 | 0.97189 | -0.54312 | 3.2696
40 | -0.008511 | -0.0021337 | 0.0085126 | 0.0021344 | 1.6037e-06 | 7.1366e-07 | 0.013025 | 0.013025 | 0.013025 | 0.97233 | -0.53443 | 0.97253 | -0.53048 | 3.5783
41 | 0.0067912 | 0.0017022 | -0.0067894 | -0.0017016 | 1.7754e-06 | 5.9373e-07 | 0.010398 | 0.010398 | 0.010398 | 0.97189 | -0.54312 | 0.97161 | -0.5486 | 2.8566
42 | -0.010692 | -0.0026807 | 0.010695 | 0.0026819 | 2.3662e-06 | 1.2218e-06 | 0.01636 | 0.01636 | 0.01636 | 0.97253 | -0.53048 | 0.97276 | -0.52584 | 4.4945
43 | 0.028753 | 0.0072235 | -0.028746 | -0.0072192 | 6.8925e-06 | 4.2919e-06 | 0.04386 | 0.04386 | 0.04386 | 0.97562 | -0.46958 | 0.97537 | -0.47461 | 12.0494
44 | -0.032363 | -0.0081285 | 0.03239 | 0.0081449 | 2.6142e-05 | 1.6373e-05 | 0.049367 | 0.049367 | 0.049367 | 0.97562 | -0.46958 | 0.97648 | -0.45267 | 13.5624
45 | 0.026645 | 0.0066927 | -0.026627 | -0.0066816 | 1.8002e-05 | 1.1159e-05 | 0.040655 | 0.040655 | 0.040655 | 0.97537 | -0.47461 | 0.97465 | -0.48878 | 11.169
46 | -0.010695 | -0.0026819 | 0.010696 | 0.0026827 | 1.5072e-06 | 7.7816e-07 | 0.01636 | 0.01636 | 0.01636 | 0.97276 | -0.52584 | 0.97291 | -0.52288 | 4.4945
47 | 0.0078863 | 0.0019763 | -0.007886 | -0.0019762 | 3.0124e-07 | 1.2214e-07 | 0.011971 | 0.011971 | 0.011971 | 0.98024 | -0.37922 | 0.9802 | -0.38003 | 3.2889
48 | 0.0031346 | 0.0007854 | -0.0031344 | -0.00078556 | 1.9386e-07 | -1.6368e-07 | 0.0047585 | 0.0047586 | 0.0047586 | 0.9802 | -0.38003 | 0.98013 | -0.38132 | 1.3073
49 | -0.0083078 | -0.0020805 | 0.0083108 | 0.0020818 | 2.9991e-06 | 1.2693e-06 | 0.012533 | 0.012533 | 0.012533 | 0.98634 | -0.26135 | 0.98673 | -0.25377 | 3.4431
50 | 0.0066314 | 0.0016604 | -0.0066294 | -0.0016598 | 1.9851e-06 | 5.9556e-07 | 0.010004 | 0.010004 | 0.010004 | 0.98634 | -0.26135 | 0.98602 | -0.26764 | 2.7483
51 | -0.010172 | -0.0025464 | 0.010174 | 0.0025475 | 2.2504e-06 | 1.1144e-06 | 0.015338 | 0.015338 | 0.015338 | 0.98673 | -0.25377 | 0.98697 | -0.24912 | 4.2138
52 | 0.001861 | 0.00046465 | -0.0018606 | -0.00046598 | 3.6146e-07 | -1.332e-06 | 0.0028058 | 0.0028063 | 0.0028063 | 0.98673 | -0.25377 | 0.98652 | -0.25786 | 0.77096
53 | 0.0011175 | 0.00027979 | -0.0011175 | -0.00028007 | 2.4878e-08 | -2.8161e-07 | 0.0016864 | 0.0016865 | 0.0016865 | 0.98602 | -0.26764 | 0.98599 | -0.26811 | 0.46332
54 | 0.0055119 | 0.00138 | -0.0055097 | -0.0013797 | 2.2284e-06 | 3.3113e-07 | 0.0083176 | 0.008318 | 0.008318 | 0.98602 | -0.26764 | 0.98558 | -0.27614 | 2.2852
55 | -0.011393 | -0.002853 | 0.011394 | 0.0028537 | 1.3239e-06 | 6.9435e-07 | 0.017176 | 0.017176 | 0.017176 | 0.98697 | -0.24912 | 0.98709 | -0.24668 | 4.7186
56 | 0.0018606 | 0.00046598 | -0.0018605 | -0.00046629 | 8.4439e-08 | -3.1098e-07 | 0.0028063 | 0.0028064 | 0.0028064 | 0.98652 | -0.25786 | 0.98647 | -0.25881 | 0.771
57 | 0.0022897 | 0.00057264 | -0.0022893 | -0.00057344 | 3.6237e-07 | -7.9856e-07 | 0.0034565 | 0.0034568 | 0.0034568 | 0.98558 | -0.27614 | 0.98541 | -0.27946 | 0.94968
58 | -0.012461 | -0.0031211 | 0.012467 | 0.0031242 | 5.6804e-06 | 3.0864e-06 | 0.018784 | 0.018784 | 0.018784 | 0.98709 | -0.24668 | 0.98758 | -0.23711 | 5.1604
59 | 0.0022893 | 0.00057344 | -0.0022892 | -0.00057364 | 9.2493e-08 | -2.0373e-07 | 0.0034568 | 0.0034569 | 0.0034569 | 0.98541 | -0.27946 | 0.98537 | -0.28031 | 0.9497
60 | 0.00077641 | 0.0001945 | -0.00077641 | -0.00019459 | 3.4176e-09 | -8.2263e-08 | 0.0011724 | 0.0011725 | 0.0011725 | 0.98537 | -0.28031 | 0.98536 | -0.2804 | 0.32211
61 | -0.016422 | -0.0041154 | 0.01643 | 0.0041202 | 8.1285e-06 | 4.749e-06 | 0.024743 | 0.024743 | 0.024743 | 0.98758 | -0.23711 | 0.98812 | -0.22673 | 6.7975
62 | -0.01643 | -0.0041202 | 0.016437 | 0.0041242 | 6.9049e-06 | 4.0337e-06 | 0.024743 | 0.024743 | 0.024743 | 0.98812 | -0.22673 | 0.98857 | -0.21791 | 6.7975
63 | 0.089115 | 0.02267 | -0.089061 | -0.022636 | 5.3946e-05 | 3.3605e-05 | 0.13426 | 0.13426 | 0.13426 | 0.98857 | -0.21791 | 0.98792 | -0.23048 | 12.2947
64 | -0.10756 | -0.027298 | 0.1077 | 0.027386 | 0.00014026 | 8.8119e-05 | 0.16203 | 0.16203 | 0.16203 | 0.98857 | -0.21791 | 0.98998 | -0.19084 | 14.8377
65 | 0.089061 | 0.022636 | -0.089031 | -0.022618 | 2.9717e-05 | 1.8512e-05 | 0.13426 | 0.13426 | 0.13426 | 0.98792 | -0.23048 | 0.98756 | -0.23742 | 12.2947
66 | -0.11543 | -0.029321 | 0.11553 | 0.029388 | 0.00010632 | 6.6957e-05 | 0.17363 | 0.17363 | 0.17363 | 0.98998 | -0.19084 | 0.99097 | -0.17173 | 15.9005
67 | 0.0063569 | 0.0015928 | -0.0063568 | -0.0015928 | 1.2768e-07 | 3.3763e-08 | 0.0095548 | 0.0095548 | 0.0095548 | 0.98998 | -0.19084 | 0.98996 | -0.19127 | 2.625
68 | 0.0043034 | 0.0010782 | -0.004303 | -0.0010783 | 3.8799e-07 | -6.9587e-08 | 0.0064684 | 0.0064685 | 0.0064685 | 0.98996 | -0.19127 | 0.98986 | -0.19316 | 1.7771
69 | 0.0032531 | 0.00081511 | -0.003253 | -0.00081513 | 1.7439e-08 | -1.3837e-08 | 0.0048901 | 0.0048901 | 0.0048901 | 0.98986 | -0.19316 | 0.98985 | -0.19327 | 1.3434
70 | 0.087223 | 0.022165 | -0.087133 | -0.022108 | 9.0246e-05 | 5.7046e-05 | 0.13153 | 0.13153 | 0.13153 | 0.98756 | -0.23742 | 0.98644 | -0.25893 | 18.0678
71 | -0.11831 | -0.030085 | 0.11842 | 0.030152 | 0.00010736 | 6.7659e-05 | 0.17781 | 0.17781 | 0.17781 | 0.99097 | -0.17173 | 0.99196 | -0.15291 | 16.2826
72 | 0.0021677 | 0.00054312 | -0.0021676 | -0.00054326 | 5.658e-08 | -1.4643e-07 | 0.0032586 | 0.0032587 | 0.0032587 | 0.98985 | -0.19327 | 0.98983 | -0.19382 | 0.89523
73 | -0.12118 | -0.030845 | 0.1212 | 0.030858 | 1.9972e-05 | 1.2595e-05 | 0.18195 | 0.18195 | 0.18195 | 0.99196 | -0.15291 | 0.99214 | -0.14949 | 16.6621
74 | -0.12458 | -0.031705 | 0.12468 | 0.031766 | 9.7254e-05 | 6.138e-05 | 0.18702 | 0.18702 | 0.18702 | 0.99214 | -0.14949 | 0.99298 | -0.13331 | 17.1264
75 | 0.084805 | 0.021524 | -0.084777 | -0.021506 | 2.8353e-05 | 1.8087e-05 | 0.12802 | 0.12802 | 0.12802 | 0.98644 | -0.25893 | 0.98608 | -0.26588 | 35.171
76 | -0.12749 | -0.032471 | 0.12749 | 0.032474 | 5.3056e-06 | 3.3505e-06 | 0.19123 | 0.19123 | 0.19123 | 0.99298 | -0.13331 | 0.99303 | -0.13245 | 17.512
77 | -0.0010179 | -0.00025511 | 0.0010179 | 0.00025487 | 1.8465e-08 | -2.4036e-07 | 0.001557 | 0.0015569 | 0.001557 | 0.97277 | -0.52575 | 0.97279 | -0.52537 | 0.42775
78 | -0.0041021 | -0.0010277 | 0.0041022 | 0.0010277 | 1.6821e-07 | -3.3805e-08 | 0.0062745 | 0.0062745 | 0.0062745 | 0.97279 | -0.52537 | 0.97284 | -0.52451 | 1.7238
79 | 0.0030842 | 0.00077285 | -0.0030841 | -0.00077294 | 1.0452e-07 | -8.8578e-08 | 0.0047176 | 0.0047176 | 0.0047176 | 0.97279 | -0.52537 | 0.97276 | -0.52608 | 1.2961
80 | -0.0060656 | -0.0015197 | 0.0060663 | 0.0015199 | 7.0529e-07 | 1.8004e-07 | 0.0092775 | 0.0092774 | 0.0092775 | 0.97284 | -0.52451 | 0.97296 | -0.52206 | 2.5488
81 | -0.0086603 | -0.00217 | 0.0086638 | 0.0021716 | 3.4751e-06 | 1.5677e-06 | 0.013245 | 0.013244 | 0.013245 | 0.97296 | -0.52206 | 0.97339 | -0.51364 | 3.6386
82 | -0.011748 | -0.0029446 | 0.011749 | 0.002945 | 6.5305e-07 | 3.5083e-07 | 0.01796 | 0.017959 | 0.01796 | 0.97339 | -0.51364 | 0.97344 | -0.51248 | 4.9339
83 | -0.015623 | -0.0039161 | 0.015629 | 0.0039193 | 5.575e-06 | 3.2438e-06 | 0.023882 | 0.023882 | 0.023882 | 0.97344 | -0.51248 | 0.97382 | -0.50499 | 6.5611
84 | -0.019197 | -0.0048136 | 0.019205 | 0.0048183 | 7.7101e-06 | 4.6371e-06 | 0.029335 | 0.029335 | 0.029335 | 0.97382 | -0.50499 | 0.97425 | -0.49657 | 8.059
85 | -0.023792 | -0.0059679 | 0.023801 | 0.0059733 | 8.8385e-06 | 5.4343e-06 | 0.036341 | 0.036341 | 0.036341 | 0.97425 | -0.49657 | 0.97465 | -0.48878 | 9.9837
86 | -0.13061 | -0.033254 | 0.13074 | 0.033337 | 0.0001315 | 8.3097e-05 | 0.19589 | 0.19589 | 0.19589 | 0.99303 | -0.13245 | 0.99412 | -0.11159 | 17.9389
87 | -0.13358 | -0.034048 | 0.13371 | 0.034134 | 0.00013628 | 8.6159e-05 | 0.20014 | 0.20014 | 0.20014 | 0.99412 | -0.11159 | 0.99523 | -0.090477 | 18.3281
88 | -0.13683 | -0.034916 | 0.13698 | 0.035012 | 0.00015142 | 9.578e-05 | 0.20481 | 0.20481 | 0.20481 | 0.99523 | -0.090477 | 0.99643 | -0.067597 | 18.7552
89 | -0.13698 | -0.035012 | 0.13707 | 0.035069 | 8.9802e-05 | 5.6804e-05 | 0.20481 | 0.20481 | 0.20481 | 0.99643 | -0.067597 | 0.99714 | -0.054054 | 18.7551
90 | -0.14003 | -0.03581 | 0.14019 | 0.035913 | 0.00016246 | 0.00010281 | 0.20922 | 0.20922 | 0.20922 | 0.99714 | -0.054054 | 0.99841 | -0.030108 | 19.159
91 | 0.083943 | 0.021297 | -0.083937 | -0.021294 | 5.8185e-06 | 3.7115e-06 | 0.12676 | 0.12676 | 0.12676 | 0.98608 | -0.26588 | 0.98601 | -0.26732 | 34.8255
92 | 0.081963 | 0.020799 | -0.081884 | -0.020748 | 7.9436e-05 | 5.0663e-05 | 0.12379 | 0.12379 | 0.12379 | 0.98601 | -0.26732 | 0.98496 | -0.28749 | 34.0069
93 | -0.011346 | -0.0028437 | 0.011346 | 0.0028441 | 6.9214e-07 | 3.6526e-07 | 0.017264 | 0.017264 | 0.017264 | 0.97793 | -0.42441 | 0.978 | -0.42313 | 4.7428
94 | 0.0094331 | 0.0023644 | -0.0094314 | -0.0023636 | 1.7071e-06 | 8.1536e-07 | 0.014353 | 0.014354 | 0.014354 | 0.97793 | -0.42441 | 0.97774 | -0.42821 | 3.9433
95 | -0.012471 | -0.0031258 | 0.012471 | 0.0031259 | 1.6685e-07 | 9.1274e-08 | 0.018974 | 0.018974 | 0.018974 | 0.978 | -0.42313 | 0.97801 | -0.42285 | 5.2126
96 | 0.0074349 | 0.0018632 | -0.0074346 | -0.0018631 | 2.4229e-07 | 9.1775e-08 | 0.011315 | 0.011315 | 0.011315 | 0.97774 | -0.42821 | 0.97771 | -0.42889 | 3.1085
97 | 0.080727 | 0.020458 | -0.080707 | -0.020446 | 1.9921e-05 | 1.2704e-05 | 0.12204 | 0.12204 | 0.12204 | 0.98496 | -0.28749 | 0.9847 | -0.29263 | 33.5269
98 | 0.075901 | 0.019241 | -0.075652 | -0.019083 | 0.00024824 | 0.00015824 | 0.11477 | 0.11477 | 0.11477 | 0.9847 | -0.29263 | 0.98118 | -0.36093 | 31.5316
99 | -0.013768 | -0.0034511 | 0.013773 | 0.0034539 | 4.8988e-06 | 2.7615e-06 | 0.020948 | 0.020948 | 0.020948 | 0.97801 | -0.42285 | 0.97839 | -0.41538 | 5.755
100 | 0.011559 | 0.0028997 | -0.011556 | -0.0028981 | 3.0032e-06 | 1.5931e-06 | 0.017531 | 0.017532 | 0.017532 | 0.98118 | -0.36093 | 0.9809 | -0.36638 | 4.8164
101 | 0.062332 | 0.015742 | -0.062243 | -0.015685 | 8.9191e-05 | 5.6747e-05 | 0.094573 | 0.094573 | 0.094573 | 0.98118 | -0.36093 | 0.97965 | -0.39083 | 25.9816
102 | 0.060289 | 0.015195 | -0.060258 | -0.015176 | 3.0634e-05 | 1.9483e-05 | 0.091605 | 0.091605 | 0.091605 | 0.97965 | -0.39083 | 0.9791 | -0.40146 | 25.1662
103 | 0.058492 | 0.014733 | -0.058454 | -0.014708 | 3.8916e-05 | 2.4742e-05 | 0.088922 | 0.088922 | 0.088922 | 0.9791 | -0.40146 | 0.97839 | -0.41538 | 24.429
104 | 0.0096213 | 0.0024131 | -0.0096149 | -0.00241 | 6.3696e-06 | 3.0709e-06 | 0.014596 | 0.014596 | 0.014596 | 0.9809 | -0.36638 | 0.98019 | -0.38028 | 4.01
105 | 0.0056348 | 0.001412 | -0.0056344 | -0.0014119 | 4.9017e-07 | 9.0843e-08 | 0.0085758 | 0.0085759 | 0.0085759 | 0.97771 | -0.42889 | 0.97761 | -0.43072 | 2.356
106 | 0.0025264 | 0.000633 | -0.0025263 | -0.00063315 | 9.3899e-08 | -1.5222e-07 | 0.0038453 | 0.0038454 | 0.0038454 | 0.97761 | -0.43072 | 0.97757 | -0.4315 | 1.0564
107 | 0.04468 | 0.011255 | -0.044662 | -0.011243 | 1.8406e-05 | 1.1646e-05 | 0.067974 | 0.067974 | 0.067974 | 0.97839 | -0.41538 | 0.97795 | -0.424 | 18.6741
108 | 0.0096149 | 0.00241 | -0.0096135 | -0.0024094 | 1.3465e-06 | 6.4936e-07 | 0.014596 | 0.014596 | 0.014596 | 0.98019 | -0.38028 | 0.98004 | -0.38321 | 4.01
109 | 0.042976 | 0.01082 | -0.042975 | -0.01082 | 9.1517e-07 | 5.7855e-07 | 0.065409 | 0.065409 | 0.065409 | 0.97795 | -0.424 | 0.97793 | -0.42445 | 17.9694
110 | 0.041048 | 0.010337 | -0.041015 | -0.010316 | 3.2516e-05 | 2.0532e-05 | 0.062476 | 0.062476 | 0.062476 | 0.97793 | -0.42445 | 0.97708 | -0.44103 | 17.1637
111 | 0.039639 | 0.0099714 | -0.039629 | -0.0099648 | 1.0352e-05 | 6.5305e-06 | 0.06038 | 0.06038 | 0.06038 | 0.97708 | -0.44103 | 0.97681 | -0.4465 | 16.5879
112 | 0.036325 | 0.0091368 | -0.036305 | -0.0091244 | 1.9657e-05 | 1.2367e-05 | 0.055347 | 0.055347 | 0.055347 | 0.97681 | -0.4465 | 0.97623 | -0.45783 | 15.2053
113 | 0.03431 | 0.0086245 | -0.034303 | -0.0086196 | 7.9119e-06 | 4.9672e-06 | 0.052307 | 0.052307 | 0.052307 | 0.97623 | -0.45783 | 0.97598 | -0.46266 | 14.37
114 | 0.029981 | 0.0075293 | -0.029977 | -0.0075269 | 3.8207e-06 | 2.3845e-06 | 0.045745 | 0.045745 | 0.045745 | 0.97535 | -0.47512 | 0.97521 | -0.47779 | 12.5674
115 | -0.032296 | -0.0081096 | 0.032316 | 0.0081216 | 1.9209e-05 | 1.203e-05 | 0.049278 | 0.049278 | 0.049278 | 0.97535 | -0.47512 | 0.97598 | -0.46266 | 13.5378
116 | 0.027778 | 0.0069757 | -0.027761 | -0.0069654 | 1.6627e-05 | 1.0333e-05 | 0.04239 | 0.04239 | 0.04239 | 0.97521 | -0.47779 | 0.97458 | -0.49034 | 11.6455
117 | 0.025445 | 0.0063848 | -0.025442 | -0.0063828 | 3.3639e-06 | 2.0789e-06 | 0.038853 | 0.038853 | 0.038853 | 0.97458 | -0.49034 | 0.97444 | -0.49312 | 10.6739
118 | 0.022268 | 0.0055874 | -0.022261 | -0.0055828 | 7.4759e-06 | 4.5699e-06 | 0.034007 | 0.034007 | 0.034007 | 0.97444 | -0.49312 | 0.97408 | -0.50016 | 9.3426
119 | 0.019428 | 0.004873 | -0.019425 | -0.0048707 | 3.8627e-06 | 2.3266e-06 | 0.029681 | 0.029681 | 0.029681 | 0.97408 | -0.50016 | 0.97387 | -0.50433 | 8.154
120 | 0.016775 | 0.0042066 | -0.016772 | -0.0042048 | 3.1122e-06 | 1.8346e-06 | 0.025632 | 0.025632 | 0.025632 | 0.97387 | -0.50433 | 0.97367 | -0.50823 | 7.0417
121 | 0.014978 | 0.0037553 | -0.014973 | -0.0037522 | 5.3703e-06 | 3.0972e-06 | 0.022891 | 0.022891 | 0.022891 | 0.97367 | -0.50823 | 0.97329 | -0.51575 | 6.2888
122 | 0.011217 | 0.0028108 | -0.011216 | -0.0028107 | 2.3065e-07 | 1.2163e-07 | 0.017148 | 0.017148 | 0.017148 | 0.97329 | -0.51575 | 0.97327 | -0.51618 | 4.7111
123 | 0.0077645 | 0.0019455 | -0.0077628 | -0.0019448 | 1.716e-06 | 6.9481e-07 | 0.011871 | 0.011871 | 0.011871 | 0.97327 | -0.51618 | 0.97303 | -0.52083 | 3.2613
124 | 0.0050391 | 0.0012622 | -0.005039 | -0.0012622 | 4.0641e-08 | 3.3397e-09 | 0.0077058 | 0.0077058 | 0.0077058 | 0.97303 | -0.52083 | 0.97302 | -0.52099 | 2.117
125 | 0.15216 | 0.038835 | -0.15211 | -0.038799 | 5.6581e-05 | 3.5874e-05 | 0.22813 | 0.22813 | 0.22813 | 0.99359 | -0.12152 | 0.99319 | -0.12922 | 20.8912
126 | -0.15506 | -0.03956 | 0.15519 | 0.039642 | 0.00012945 | 8.2101e-05 | 0.23246 | 0.23246 | 0.23246 | 0.99359 | -0.12152 | 0.9945 | -0.10426 | 21.2878
127 | 0.1475 | 0.037644 | -0.14737 | -0.037563 | 0.00012817 | 8.1217e-05 | 0.22123 | 0.22123 | 0.22123 | 0.99319 | -0.12922 | 0.99225 | -0.14723 | 20.2591
128 | -0.15732 | -0.040177 | 0.15739 | 0.040222 | 7.1036e-05 | 4.5064e-05 | 0.23566 | 0.23566 | 0.23566 | 0.9945 | -0.10426 | 0.99499 | -0.094919 | 21.5806
129 | -0.16042 | -0.040981 | 0.16062 | 0.041108 | 0.00019952 | 0.00012661 | 0.24019 | 0.24019 | 0.24019 | 0.99499 | -0.094919 | 0.99634 | -0.06923 | 21.9952
130 | -0.16137 | -0.041294 | 0.16146 | 0.041353 | 9.2139e-05 | 5.8474e-05 | 0.2413 | 0.2413 | 0.2413 | 0.99634 | -0.06923 | 0.99696 | -0.057444 | 22.097
131 | -0.1642 | -0.042041 | 0.16424 | 0.042066 | 3.9565e-05 | 2.5116e-05 | 0.2454 | 0.2454 | 0.2454 | 0.99696 | -0.057444 | 0.99723 | -0.05247 | 22.4723
132 | 0.003171 | 0.00079434 | -0.0031706 | -0.00079463 | 3.6618e-07 | -2.8138e-07 | 0.0048491 | 0.0048493 | 0.0048493 | 0.97302 | -0.52099 | 0.9729 | -0.52342 | 1.3322
133 | 0.0018681 | 0.00046787 | -0.001868 | -0.00046816 | 8.4635e-08 | -2.8933e-07 | 0.0028566 | 0.0028568 | 0.0028568 | 0.97302 | -0.52099 | 0.97298 | -0.52195 | 0.78483
134 | -0.14019 | -0.035913 | 0.14022 | 0.03593 | 2.727e-05 | 1.7257e-05 | 0.20922 | 0.20922 | 0.20922 | 0.99841 | -0.030108 | 0.99862 | -0.026094 | 19.159
135 | -0.14022 | -0.03593 | 0.1404 | 0.036042 | 0.00017757 | 0.00011237 | 0.20922 | 0.20922 | 0.20922 | 0.99862 | -0.026094 | 1 | 0 | 19.159
136 | 0.18258 | 0.046831 | -0.18248 | -0.046769 | 9.7937e-05 | 6.2263e-05 | 0.27206 | 0.27206 | 0.27206 | 1 | 0 | 0.99941 | -0.011065 | 24.9138
137 | 0.17187 | 0.044109 | -0.17176 | -0.044035 | 0.00011803 | 7.4973e-05 | 0.25627 | 0.25627 | 0.25627 | 0.99941 | -0.011065 | 0.99866 | -0.025228 | 23.4678
138 | 0.010606 | 0.0026591 | -0.010602 | -0.0026574 | 3.4874e-06 | 1.7434e-06 | 0.015791 | 0.015791 | 0.015791 | 0.99941 | -0.011065 | 0.99906 | -0.017968 | 4.3382
139 | 0.0037769 | 0.00094656 | -0.0037768 | -0.00094657 | 6.7003e-09 | -3.1004e-09 | 0.0056263 | 0.0056263 | 0.0056263 | 0.99888 | -0.021391 | 0.99888 | -0.021428 | 1.5457
140 | -0.0083149 | -0.0020839 | 0.0083162 | 0.0020845 | 1.356e-06 | 5.5927e-07 | 0.012387 | 0.012386 | 0.012387 | 0.99888 | -0.021391 | 0.99906 | -0.017968 | 3.4029
141 | 0.16843 | 0.043201 | -0.16822 | -0.043068 | 0.00020938 | 0.00013296 | 0.25131 | 0.25131 | 0.25131 | 0.99866 | -0.025228 | 0.99731 | -0.050892 | 23.014
142 | 0.16714 | 0.042798 | -0.16713 | -0.04279 | 1.2777e-05 | 8.1132e-06 | 0.24971 | 0.24971 | 0.24971 | 0.99731 | -0.050892 | 0.99723 | -0.05247 | 22.8669

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32773 | 0.08365

## res_load
| p_mw | q_mvar
0 | 0.0021027 | 0.00052699
1 | 0.0031835 | 0.00079785
2 | 0.0022088 | 0.00055359
3 | 0.004103 | 0.0010283
4 | 0.0011944 | 0.00029934
5 | 0.0019424 | 0.00048681
6 | 0.0022086 | 0.00055352
7 | 0.0078161 | 0.0019589
8 | 0.0028941 | 0.00072533
9 | 0.0045859 | 0.0011493
10 | 0.0028059 | 0.00070322
11 | 0.001836 | 0.00046015
12 | 0.0024275 | 0.00060838
13 | 0.0024325 | 0.00060964
14 | 0.0033483 | 0.00083917
15 | 0.0022331 | 0.00055967
16 | 0.0027344 | 0.0006853
17 | 0.0010462 | 0.00026221
18 | 0.003683 | 0.00092304
19 | 0.0018153 | 0.00045495
20 | 0.0021546 | 0.00054
21 | 0.0026625 | 0.00066727
22 | 0.0047853 | 0.0011993
23 | 0.0029112 | 0.00072962
24 | 0.00069031 | 0.00017301
25 | 0.0043732 | 0.001096
26 | 0.0010756 | 0.00026957
27 | 0.0051392 | 0.001288
28 | 0.00073457 | 0.0001841
29 | 0.00098201 | 0.00024612
30 | 0.0021797 | 0.00054629
31 | 0.0067894 | 0.0017016
32 | 0.0036108 | 0.00090496
33 | 0.0021008 | 0.00052651
34 | 0.0045497 | 0.0011403
35 | 0.0045971 | 0.0011521
36 | 0.0047514 | 0.0011908
37 | 0.0031344 | 0.00078556
38 | 0.0017971 | 0.0004504
39 | 0.0016764 | 0.00042014
40 | 0.0012188 | 0.00030547
41 | 0.0011175 | 0.00028007
42 | 0.00322 | 0.00080702
43 | 0.0010669 | 0.00026738
44 | 0.0018605 | 0.00046629
45 | 0.0015128 | 0.00037914
46 | 0.0039551 | 0.00099125
47 | 0.00077641 | 0.00019459
48 | 0.0020113 | 0.00050409
49 | 0.001365 | 0.00034211
50 | 0.0020534 | 0.00051463
51 | 0.00105 | 0.00026314
52 | 0.0018083 | 0.0004532
53 | 0.0027789 | 0.00069645
54 | 0.0010853 | 0.00027201
55 | 0.0021676 | 0.00054326
56 | 0.0027628 | 0.00069243
57 | 0.0033805 | 0.00084725
58 | 0.0023276 | 0.00058334
59 | 0.0028106 | 0.00070441
60 | 0.0010179 | 0.00025511
61 | 0.0019633 | 0.00049206
62 | 0.0030841 | 0.00077294
63 | 0.002594 | 0.00065012
64 | 0.0030844 | 0.00077302
65 | 0.0038747 | 0.00097109
66 | 0.0035684 | 0.00089433
67 | 0.0045871 | 0.0011496
68 | 0.003111 | 0.00077969
69 | 0.0028395 | 0.00071165
70 | 0.0031196 | 0.00078184
71 | 0.0029558 | 0.00074078
72 | 0.00083346 | 0.00020888
73 | 0.0019744 | 0.00049484
74 | 0.0019126 | 0.00047935
75 | 0.0011242 | 0.00028174
76 | 0.0019965 | 0.00050038
77 | 0.0011566 | 0.00028987
78 | 0.0048064 | 0.0012046
79 | 0.0012976 | 0.00032522
80 | 0.0017609 | 0.00044133
81 | 0.0019541 | 0.00048974
82 | 0.0017657 | 0.00044252
83 | 0.0019351 | 0.00048499
84 | 0.0017998 | 0.00045107
85 | 0.003108 | 0.00077893
86 | 0.0025263 | 0.00063315
87 | 0.0096135 | 0.0024094
88 | 0.0016856 | 0.00042246
89 | 0.0019276 | 0.0004831
90 | 0.0013761 | 0.00034489
91 | 0.0033039 | 0.00082805
92 | 0.0019946 | 0.00049989
93 | 0.0023154 | 0.0005803
94 | 0.0021991 | 0.00055116
95 | 0.001987 | 0.00049798
96 | 0.0023164 | 0.00058054
97 | 0.0031735 | 0.00079536
98 | 0.0028321 | 0.0007098
99 | 0.0026498 | 0.0006641
100 | 0.0017935 | 0.0004495
101 | 0.0037561 | 0.00094138
102 | 0.0034519 | 0.00086513
103 | 0.0027237 | 0.00068263
104 | 0.0028914 | 0.00072466
105 | 0.0046075 | 0.0011548
106 | 0.0021375 | 0.00053571
107 | 0.0034752 | 0.00087096
108 | 0.003027 | 0.00075863
109 | 0.00074514 | 0.00018675
110 | 0.002746 | 0.00068822
111 | 0.0031706 | 0.00079463
112 | 0.001868 | 0.00046816
113 | 0.0028259 | 0.00070823
114 | 0.0031015 | 0.00077732
115 | 0.004538 | 0.0011373
116 | 0.0037768 | 0.00094657
117 | 0.0022859 | 0.0005729
118 | 0.0033261 | 0.0008336
119 | 0.0010764 | 0.00026976
120 | 0.002888 | 0.00072379

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1