## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2457-4_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2457-4_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2457-4_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2457-4_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2457-4_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2457-4_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2457-4_0_2_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_2457-4_0_2_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2457-4_0_2_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_2457-4_0_2_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_2457-4_0_2_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2457-4_0_2_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_2457-4_0_2_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2457-4_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2457-4_0_2_node_52 | 0.4 | n |  | TRUE
15 | bus_LV_2457-4_0_2_node_53 | 0.4 | n |  | TRUE
16 | bus_LV_2457-4_0_2_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2457-4_0_2_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2457-4_0_2_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_2457-4_0_2_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2457-4_0_2_node_75 | 0.4 | n |  | TRUE
21 | bus_LV_2457-4_0_2_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_2457-4_0_2_node_74 | 0.4 | n |  | TRUE
23 | bus_LV_2457-4_0_2_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_2457-4_0_2_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2457-4_0_2_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2457-4_0_2_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2457-4_0_2_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2457-4_0_2_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_2457-4_0_2_node_62 | 0.4 | n |  | TRUE
30 | bus_LV_2457-4_0_2_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_2457-4_0_2_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_2457-4_0_2_node_63 | 0.4 | n |  | TRUE
33 | bus_LV_2457-4_0_2_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_2457-4_0_2_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_2457-4_0_2_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_2457-4_0_2_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_2457-4_0_2_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_2457-4_0_2_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_2457-4_0_2_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_2457-4_0_2_node_80 | 0.4 | n |  | TRUE
41 | bus_LV_2457-4_0_2_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_2457-4_0_2_node_66 | 0.4 | n |  | TRUE
43 | bus_LV_2457-4_0_2_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_2457-4_0_2_node_76 | 0.4 | n |  | TRUE
45 | bus_LV_2457-4_0_2_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_2457-4_0_2_node_51 | 0.4 | n |  | TRUE
47 | bus_LV_2457-4_0_2_node_49 | 0.4 | n |  | TRUE
48 | bus_LV_2457-4_0_2_node_32 | 0.4 | n |  | TRUE
49 | bus_LV_2457-4_0_2_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_2457-4_0_2_node_78 | 0.4 | n |  | TRUE
51 | bus_LV_2457-4_0_2_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_2457-4_0_2_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_2457-4_0_2_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_2457-4_0_2_node_71 | 0.4 | n |  | TRUE
55 | bus_LV_2457-4_0_2_node_69 | 0.4 | n |  | TRUE
56 | bus_LV_2457-4_0_2_node_72 | 0.4 | n |  | TRUE
57 | bus_LV_2457-4_0_2_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_2457-4_0_2_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_2457-4_0_2_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_2457-4_0_2_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_2457-4_0_2_node_45 | 0.4 | n |  | TRUE
62 | bus_LV_2457-4_0_2_node_46 | 0.4 | n |  | TRUE
63 | bus_LV_2457-4_0_2_node_77 | 0.4 | n |  | TRUE
64 | bus_LV_2457-4_0_2_node_54 | 0.4 | n |  | TRUE
65 | bus_LV_2457-4_0_2_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_2457-4_0_2_node_55 | 0.4 | n |  | TRUE
67 | bus_LV_2457-4_0_2_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_2457-4_0_2_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_2457-4_0_2_node_50 | 0.4 | n |  | TRUE
70 | bus_LV_2457-4_0_2_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_2457-4_0_2_node_61 | 0.4 | n |  | TRUE
72 | bus_LV_2457-4_0_2_node_64 | 0.4 | n |  | TRUE
73 | bus_LV_2457-4_0_2_node_57 | 0.4 | n |  | TRUE
74 | bus_LV_2457-4_0_2_node_58 | 0.4 | n |  | TRUE
75 | bus_LV_2457-4_0_2_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_2457-4_0_2_node_60 | 0.4 | n |  | TRUE
77 | bus_LV_2457-4_0_2_node_79 | 0.4 | n |  | TRUE
78 | bus_LV_2457-4_0_2_node_89 | 0.4 | n |  | TRUE
79 | bus_LV_2457-4_0_2_node_68 | 0.4 | n |  | TRUE
80 | bus_LV_2457-4_0_2_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_2457-4_0_2_node_73 | 0.4 | n |  | TRUE
82 | bus_LV_2457-4_0_2_node_88 | 0.4 | n |  | TRUE
83 | bus_LV_2457-4_0_2_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_2457-4_0_2_node_82 | 0.4 | n |  | TRUE
85 | bus_LV_2457-4_0_2_node_83 | 0.4 | n |  | TRUE
86 | bus_LV_2457-4_0_2_node_84 | 0.4 | n |  | TRUE
87 | bus_LV_2457-4_0_2_node_85 | 0.4 | n |  | TRUE
88 | bus_LV_2457-4_0_2_node_87 | 0.4 | n |  | TRUE
89 | bus_LV_2457-4_0_2_node_86 | 0.4 | n |  | TRUE
90 | bus_MV_387_0_node_11 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2457-4_0_2_load_0 | 0 | 0.0013785 | 0.00034548 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2457-4_0_2_load_1 | 1 | 0.00012248 | 3.0697e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2457-4_0_2_load_3 | 3 | 0.00033259 | 8.3356e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2457-4_0_2_load_4 | 4 | 0.0024732 | 0.00061983 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2457-4_0_2_load_5 | 5 | 0.00062818 | 0.00015744 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2457-4_0_2_load_26 | 6 | 0.0021981 | 0.00055089 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2457-4_0_2_load_7 | 7 | 0.0010832 | 0.00027148 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2457-4_0_2_load_15 | 8 | 0.00089134 | 0.00022339 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2457-4_0_2_load_27 | 9 | 0.0001242 | 3.1128e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2457-4_0_2_load_6 | 10 | 0.0013458 | 0.00033728 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2457-4_0_2_load_8 | 12 | 0.00018862 | 4.7272e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2457-4_0_2_load_9 | 13 | 0.00069877 | 0.00017513 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2457-4_0_2_load_52 | 14 | 0.00061357 | 0.00015378 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2457-4_0_2_load_53 | 15 | 0.00089134 | 0.00022339 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2457-4_0_2_load_10 | 16 | 0.0023125 | 0.00057956 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2457-4_0_2_load_11 | 17 | 0.0011505 | 0.00028835 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2457-4_0_2_load_13 | 18 | 0.00052118 | 0.00013062 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2457-4_0_2_load_14 | 19 | 0.00055845 | 0.00013996 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2457-4_0_2_load_75 | 20 | 0.00082799 | 0.00020751 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2457-4_0_2_load_28 | 21 | 0.0037729 | 0.00094557 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2457-4_0_2_load_74 | 22 | 0.0058063 | 0.0014552 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2457-4_0_2_load_29 | 23 | 0.00068304 | 0.00017119 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2457-4_0_2_load_16 | 24 | 0.00097594 | 0.00024459 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2457-4_0_2_load_17 | 25 | 0.0017266 | 0.00043273 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2457-4_0_2_load_18 | 26 | 0.00047151 | 0.00011817 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2457-4_0_2_load_19 | 27 | 0.0014824 | 0.00037153 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2457-4_0_2_load_62 | 29 | 0.0017554 | 0.00043994 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2457-4_0_2_load_33 | 30 | 0.00045452 | 0.00011391 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2457-4_0_2_load_36 | 31 | 0.0017627 | 0.00044178 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2457-4_0_2_load_31 | 33 | 0.0028366 | 0.00071091 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2457-4_0_2_load_35 | 34 | 0.002779 | 0.00069648 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2457-4_0_2_load_21 | 35 | 0.00069718 | 0.00017473 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2457-4_0_2_load_22 | 36 | 0.00026274 | 6.5848e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2457-4_0_2_load_23 | 37 | 0.00014497 | 3.6334e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2457-4_0_2_load_25 | 39 | 0.000113 | 2.8321e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2457-4_0_2_load_80 | 40 | 0.00025351 | 6.3536e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2457-4_0_2_load_40 | 41 | 0.00027153 | 6.8051e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2457-4_0_2_load_66 | 42 | 0.00027075 | 6.7857e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2457-4_0_2_load_41 | 43 | 0.0007251 | 0.00018173 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2457-4_0_2_load_76 | 44 | 0.0010543 | 0.00026422 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2457-4_0_2_load_30 | 45 | 8.7337e-05 | 2.1889e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2457-4_0_2_load_51 | 46 | 0.0023715 | 0.00059435 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2457-4_0_2_load_49 | 47 | 0.0010304 | 0.00025823 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2457-4_0_2_load_32 | 48 | 0.0011655 | 0.00029209 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2457-4_0_2_load_78 | 50 | 0.00051104 | 0.00012808 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2457-4_0_2_load_38 | 52 | 0.0017039 | 0.00042704 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2457-4_0_2_load_39 | 53 | 0.0045079 | 0.0011298 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2457-4_0_2_load_71 | 54 | 0.0030913 | 0.00077475 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2457-4_0_2_load_69 | 55 | 0.0024642 | 0.0006176 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2457-4_0_2_load_72 | 56 | 0.0027783 | 0.00069631 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2457-4_0_2_load_67 | 57 | 0.0044469 | 0.0011145 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2457-4_0_2_load_42 | 58 | 0.00026455 | 6.6302e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2457-4_0_2_load_43 | 59 | 0.00010054 | 2.5197e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2457-4_0_2_load_46 | 62 | 0.0001095 | 2.7444e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2457-4_0_2_load_77 | 63 | 0.0003102 | 7.7743e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2457-4_0_2_load_54 | 64 | 7.4146e-05 | 1.8583e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2457-4_0_2_load_56 | 65 | 0.0001479 | 3.7068e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2457-4_0_2_load_55 | 66 | 0.00019826 | 4.9689e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2457-4_0_2_load_47 | 67 | 0.00043883 | 0.00010998 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2457-4_0_2_load_48 | 68 | 0.00026263 | 6.582e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2457-4_0_2_load_50 | 69 | 0.00020973 | 5.2564e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2457-4_0_2_load_61 | 71 | 0.00028914 | 7.2465e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2457-4_0_2_load_64 | 72 | 0.00099495 | 0.00024936 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2457-4_0_2_load_57 | 73 | 0.00059454 | 0.000149 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2457-4_0_2_load_58 | 74 | 0.0013685 | 0.00034298 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2457-4_0_2_load_60 | 76 | 0.001035 | 0.00025939 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2457-4_0_2_load_79 | 77 | 0.0011586 | 0.00029036 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2457-4_0_2_load_89 | 78 | 0.0012861 | 0.00032231 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2457-4_0_2_load_68 | 79 | 0.0011101 | 0.00027823 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2457-4_0_2_load_70 | 80 | 0.0014824 | 0.00037153 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2457-4_0_2_load_73 | 81 | 0.00062526 | 0.0001567 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2457-4_0_2_load_88 | 82 | 0.0013842 | 0.00034692 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2457-4_0_2_load_81 | 83 | 0.00060906 | 0.00015264 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2457-4_0_2_load_82 | 84 | 0.0016493 | 0.00041334 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2457-4_0_2_load_83 | 85 | 0.0010677 | 0.0002676 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2457-4_0_2_load_84 | 86 | 0.0012335 | 0.00030914 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2457-4_0_2_load_85 | 87 | 0.0012875 | 0.00032268 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2457-4_0_2_load_87 | 88 | 0.0013987 | 0.00035054 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2457-4_0_2_load_86 | 89 | 0.00067262 | 0.00016857 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 80 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2457-4_0_2_line_0 |  | 0 | 1 | 0.016423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2457-4_0_2_line_1 |  | 0 | 2 | 0.00039893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2457-4_0_2_line_2 |  | 1 | 3 | 0.019386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2457-4_0_2_line_3 |  | 2 | 4 | 0.026019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2457-4_0_2_line_4 |  | 2 | 5 | 0.026489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2457-4_0_2_line_5 |  | 3 | 6 | 0.011375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2457-4_0_2_line_6 |  | 4 | 7 | 0.0053594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2457-4_0_2_line_7 |  | 5 | 8 | 0.032368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2457-4_0_2_line_8 |  | 6 | 9 | 0.0027441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2457-4_0_2_line_9 |  | 7 | 10 | 0.00034152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2457-4_0_2_line_10 |  | 8 | 11 | 0.0038853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2457-4_0_2_line_11 |  | 9 | 44 | 0.0017976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2457-4_0_2_line_12 |  | 10 | 12 | 0.026768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2457-4_0_2_line_13 |  | 11 | 19 | 0.016473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2457-4_0_2_line_14 |  | 11 | 16 | 0.022099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2457-4_0_2_line_15 |  | 12 | 13 | 0.00035857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2457-4_0_2_line_16 |  | 13 | 14 | 0.0040376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2457-4_0_2_line_17 |  | 14 | 15 | 0.020101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2457-4_0_2_line_18 |  | 15 | 70 | 0.0044798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2457-4_0_2_line_19 |  | 16 | 17 | 0.00096995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2457-4_0_2_line_20 |  | 17 | 18 | 0.014549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2457-4_0_2_line_21 |  | 18 | 20 | 0.0067672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2457-4_0_2_line_22 |  | 19 | 21 | 0.0028791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2457-4_0_2_line_23 |  | 20 | 22 | 0.0020623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2457-4_0_2_line_24 |  | 21 | 23 | 0.01063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2457-4_0_2_line_25 |  | 22 | 80 | 0.031426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2457-4_0_2_line_26 |  | 23 | 45 | 0.010138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2457-4_0_2_line_27 |  | 24 | 25 | 0.018821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2457-4_0_2_line_28 |  | 24 | 26 | 0.013073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2457-4_0_2_line_29 |  | 25 | 27 | 0.028209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2457-4_0_2_line_30 |  | 26 | 28 | 0.019814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2457-4_0_2_line_31 |  | 27 | 29 | 0.0045337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2457-4_0_2_line_32 |  | 28 | 30 | 0.0006163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2457-4_0_2_line_33 |  | 28 | 31 | 0.036969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2457-4_0_2_line_34 |  | 29 | 32 | 0.043757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2457-4_0_2_line_35 |  | 30 | 33 | 0.0057805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2457-4_0_2_line_36 |  | 31 | 34 | 0.016664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2457-4_0_2_line_37 |  | 32 | 77 | 0.01495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2457-4_0_2_line_38 |  | 33 | 48 | 0.040321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2457-4_0_2_line_39 |  | 34 | 51 | 0.020623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2457-4_0_2_line_40 |  | 35 | 36 | 0.0084822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2457-4_0_2_line_41 |  | 35 | 37 | 0.035711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2457-4_0_2_line_42 |  | 36 | 38 | 0.031507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2457-4_0_2_line_43 |  | 37 | 39 | 0.017496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2457-4_0_2_line_44 |  | 38 | 40 | 0.037852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2457-4_0_2_line_45 |  | 39 | 41 | 0.012726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2457-4_0_2_line_46 |  | 40 | 42 | 0.38162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2457-4_0_2_line_47 |  | 41 | 43 | 0.01134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2457-4_0_2_line_48 |  | 42 | 63 | 0.4204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2457-4_0_2_line_49 |  | 43 | 44 | 0.0073725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2457-4_0_2_line_50 |  | 45 | 46 | 0.013953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2457-4_0_2_line_51 |  | 46 | 47 | 0.019419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2457-4_0_2_line_52 |  | 47 | 67 | 0.0049043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2457-4_0_2_line_53 |  | 48 | 49 | 0.029994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2457-4_0_2_line_54 |  | 49 | 50 | 0.019502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2457-4_0_2_line_55 |  | 51 | 52 | 0.017381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2457-4_0_2_line_56 |  | 51 | 53 | 0.0018222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2457-4_0_2_line_57 |  | 52 | 54 | 0.0032759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2457-4_0_2_line_58 |  | 53 | 55 | 0.033464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2457-4_0_2_line_59 |  | 54 | 56 | 0.017062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2457-4_0_2_line_60 |  | 55 | 57 | 0.024887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2457-4_0_2_line_61 |  | 56 | 81 | 0.035671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2457-4_0_2_line_62 |  | 57 | 79 | 0.018173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2457-4_0_2_line_63 |  | 58 | 59 | 0.026188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2457-4_0_2_line_64 |  | 58 | 60 | 0.023166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2457-4_0_2_line_65 |  | 59 | 61 | 0.036639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2457-4_0_2_line_66 |  | 60 | 62 | 0.018351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2457-4_0_2_line_67 |  | 60 | 63 | 0.3753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2457-4_0_2_line_68 |  | 61 | 64 | 0.040896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2457-4_0_2_line_69 |  | 62 | 65 | 0.0025665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2457-4_0_2_line_70 |  | 65 | 66 | 0.0034051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2457-4_0_2_line_71 |  | 67 | 68 | 0.014608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2457-4_0_2_line_72 |  | 68 | 69 | 0.018234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2457-4_0_2_line_73 |  | 70 | 71 | 0.030884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2457-4_0_2_line_74 |  | 70 | 72 | 0.015154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2457-4_0_2_line_75 |  | 71 | 75 | 0.0063783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2457-4_0_2_line_76 |  | 73 | 74 | 0.004094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2457-4_0_2_line_77 |  | 73 | 75 | 0.014275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2457-4_0_2_line_78 |  | 75 | 76 | 0.004214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2457-4_0_2_line_79 |  | 77 | 78 | 0.003227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2457-4_0_2_line_80 |  | 78 | 82 | 0.015865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2457-4_0_2_line_81 |  | 79 | 80 | 0.0030066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2457-4_0_2_line_82 |  | 82 | 88 | 0.005428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2457-4_0_2_line_83 |  | 83 | 84 | 0.020383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2457-4_0_2_line_84 |  | 83 | 85 | 0.00036458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2457-4_0_2_line_85 |  | 84 | 86 | 0.0028926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2457-4_0_2_line_86 |  | 85 | 87 | 0.0024979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2457-4_0_2_line_87 |  | 86 | 88 | 0.019239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2457-4_0_2_line_88 |  | 87 | 89 | 0.0044386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2457-4_0_2_trafo_70 | 0.63 MVA 20/0.4 kV | 90 | 80 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2601755.5871 | 1218107.8127 | 2601741.2109 | 1218099.8723
1 | 2601755.9363 | 1218108.0056 | 2601755.5871 | 1218107.8127
2 | 2601741.2109 | 1218099.8723 | 2601724.2417 | 1218090.4998
3 | 2601755.9363 | 1218108.0056 | 2601747.0479 | 1218132.4594
4 | 2601755.9363 | 1218108.0056 | 2601778.9291 | 1218121.1592
5 | 2601714.2843 | 1218085 | 2601724.2417 | 1218090.4998
6 | 2601745.2171 | 1218137.4964 | 2601747.0479 | 1218132.4594
7 | 2601778.9291 | 1218121.1592 | 2601807.0246 | 1218137.2319
8 | 2601711.8822 | 1218083.6733 | 2601714.2843 | 1218085
9 | 2601745.1004 | 1218137.8174 | 2601745.2171 | 1218137.4964
10 | 2601810.397 | 1218139.1612 | 2601807.0246 | 1218137.2319
11 | 2601710.3087 | 1218082.8042 | 2601711.8822 | 1218083.6733
12 | 2601745.1004 | 1218137.8174 | 2601735.9563 | 1218162.9749
13 | 2601810.397 | 1218139.1612 | 2601817.9164 | 1218124.5045
14 | 2601810.397 | 1218139.1612 | 2601829.404 | 1218150.4342
15 | 2601735.8338 | 1218163.3119 | 2601735.9563 | 1218162.9749
16 | 2601735.8338 | 1218163.3119 | 2601734.7681 | 1218166.2439 | 2601734.8501 | 1218167.1581
17 | 2601734.8501 | 1218167.1581 | 2601735.4566 | 1218173.9151 | 2601740.8197 | 1218186.1037
18 | 2601742.624 | 1218190.2042 | 2601740.8197 | 1218186.1037
19 | 2601829.404 | 1218150.4342 | 2601830.2383 | 1218150.929
20 | 2601842.7515 | 1218158.3506 | 2601830.2383 | 1218150.929
21 | 2601848.5719 | 1218161.8027 | 2601842.7515 | 1218158.3506
22 | 2601817.9164 | 1218124.5045 | 2601819.2306 | 1218121.9429
23 | 2601850.3457 | 1218162.8547 | 2601848.5719 | 1218161.8027
24 | 2601824.0827 | 1218112.4851 | 2601819.2306 | 1218121.9429
25 | 2601878.171 | 1218177.4412 | 2601855.1442 | 1218165.7007 | 2601850.3457 | 1218162.8547
26 | 2601824.0827 | 1218112.4851 | 2601828.7105 | 1218103.4646
27 | 2602013.142 | 1218255.3707 | 2602005.9221 | 1218272.7522
28 | 2602018.1569 | 1218243.2977 | 2602013.142 | 1218255.3707
29 | 2601994.8883 | 1218298.7141 | 2602004.772 | 1218275.521 | 2602005.9221 | 1218272.7522
30 | 2602025.7578 | 1218224.999 | 2602018.1569 | 1218243.2977
31 | 2601994.8883 | 1218298.7141 | 2601993.111 | 1218302.8848
32 | 2602026.36 | 1218225.1303 | 2602025.7578 | 1218224.999
33 | 2602025.7578 | 1218224.999 | 2601989.6405 | 1218217.1078
34 | 2601975.9566 | 1218343.1391 | 2601993.111 | 1218302.8848
35 | 2602026.36 | 1218225.1303 | 2602032.0078 | 1218226.3617
36 | 2601973.361 | 1218213.5509 | 2601989.6405 | 1218217.1078
37 | 2601975.9566 | 1218343.1391 | 2601962.7444 | 1218336.1438
38 | 2602071.6732 | 1218233.5762 | 2602038.7802 | 1218227.8383 | 2602032.0078 | 1218226.3617
39 | 2601953.4974 | 1218208.0217 | 2601971.2321 | 1218213.0857 | 2601973.361 | 1218213.5509
40 | 2601643.7322 | 1218031.3366 | 2601637.8318 | 1218025.2428
41 | 2601669.6181 | 1218055.8624 | 2601658.8449 | 1218046.9442 | 2601643.7322 | 1218031.3366
42 | 2601615.9145 | 1218002.6077 | 2601637.8318 | 1218025.2428
43 | 2601683.3987 | 1218066.6184 | 2601678.6872 | 1218063.37 | 2601669.6181 | 1218055.8624
44 | 2601615.9145 | 1218002.6077 | 2601588.9763 | 1218029.1985
45 | 2601683.3987 | 1218066.6184 | 2601693.0439 | 1218073.2684 | 2601693.9288 | 1218073.7571
46 | 2601588.9763 | 1218029.1985 | 2601280.1388 | 1217805.0214
47 | 2601693.9288 | 1218073.7571 | 2601703.8551 | 1218079.2397
48 | 2601280.1388 | 1217805.0214 | 2601080.6123 | 1217434.9839
49 | 2601710.3087 | 1218082.8042 | 2601703.8551 | 1218079.2397
50 | 2601835.0797 | 1218091.0497 | 2601828.7105 | 1218103.4646
51 | 2601835.0797 | 1218091.0497 | 2601843.9437 | 1218073.772
52 | 2601846.1823 | 1218069.4085 | 2601843.9437 | 1218073.772
53 | 2602101.2977 | 1218238.2541 | 2602082.2646 | 1218235.4238 | 2602071.6732 | 1218233.5762
54 | 2602101.2977 | 1218238.2541 | 2602100.2934 | 1218257.73
55 | 2601953.4974 | 1218208.0217 | 2601960.6894 | 1218192.1982
56 | 2601953.4974 | 1218208.0217 | 2601951.7814 | 1218207.4087
57 | 2601962.0449 | 1218189.2159 | 2601960.6894 | 1218192.1982
58 | 2601951.7814 | 1218207.4087 | 2601925.2149 | 1218197.9182 | 2601920.3806 | 1218195.8613
59 | 2601962.0449 | 1218189.2159 | 2601969.1048 | 1218173.6831
60 | 2601897.4802 | 1218186.118 | 2601920.3806 | 1218195.8613
61 | 2601969.1048 | 1218173.6831 | 2601970.0842 | 1218171.5284 | 2601983.8636 | 1218141.2083
62 | 2601897.4802 | 1218186.118 | 2601883.638 | 1218180.2286 | 2601880.8495 | 1218178.8068
63 | 2601437.1521 | 1217316.7591 | 2601430.0428 | 1217291.5547
64 | 2601443.4411 | 1217339.0552 | 2601437.1521 | 1217316.7591
65 | 2601420.0963 | 1217256.2918 | 2601430.0428 | 1217291.5547
66 | 2601443.4411 | 1217339.0552 | 2601452.8668 | 1217346.3726 | 2601458.536 | 1217349.3816
67 | 2601443.4411 | 1217339.0552 | 2601080.6123 | 1217434.9839
68 | 2601420.0963 | 1217256.2918 | 2601443.7197 | 1217249.8602 | 2601458.9299 | 1217256.0273
69 | 2601458.536 | 1217349.3816 | 2601460.803 | 1217350.5848
70 | 2601463.8107 | 1217352.1812 | 2601460.803 | 1217350.5848
71 | 2601846.1823 | 1218069.4085 | 2601852.8503 | 1218056.4113
72 | 2601852.8503 | 1218056.4113 | 2601861.1735 | 1218040.1876
73 | 2601742.624 | 1218190.2042 | 2601762.7463 | 1218213.633
74 | 2601742.624 | 1218190.2042 | 2601732.6243 | 1218201.5911
75 | 2601766.902 | 1218218.4716 | 2601762.7463 | 1218213.633
76 | 2601773.4177 | 1218231.1473 | 2601774.4639 | 1218235.1054 | 2601774.4639 | 1218235.1054
77 | 2601766.902 | 1218218.4716 | 2601771.9767 | 1218227.5671 | 2601773.4177 | 1218231.1473
78 | 2601766.902 | 1218218.4716 | 2601771.0152 | 1218219.44
79 | 2601959.8924 | 1218334.6338 | 2601962.7444 | 1218336.1438
80 | 2601959.8924 | 1218334.6338 | 2601945.8715 | 1218327.2104
81 | 2601878.171 | 1218177.4412 | 2601880.8495 | 1218178.8068
82 | 2601941.0744 | 1218324.6705 | 2601945.8715 | 1218327.2104
83 | 2601905.1372 | 1218302.2104 | 2601912.31 | 1218305.531 | 2601922.4541 | 1218312.7986
84 | 2601904.8064 | 1218302.0572 | 2601905.1372 | 1218302.2104
85 | 2601924.8055 | 1218314.4832 | 2601922.4541 | 1218312.7986
86 | 2601902.5397 | 1218301.0078 | 2601904.8064 | 1218302.0572
87 | 2601924.8055 | 1218314.4832 | 2601933.2213 | 1218320.5127 | 2601941.0744 | 1218324.6705
88 | 2601898.5117 | 1218299.1431 | 2601902.5397 | 1218301.0078

## bus_geodata
| x | y | coords
0 | 2601755.5871 | 1218107.8127
1 | 2601741.2109 | 1218099.8723
2 | 2601755.9363 | 1218108.0056
3 | 2601724.2417 | 1218090.4998
4 | 2601747.0479 | 1218132.4594
5 | 2601778.9291 | 1218121.1592
6 | 2601714.2843 | 1218085
7 | 2601745.2171 | 1218137.4964
8 | 2601807.0246 | 1218137.2319
9 | 2601711.8822 | 1218083.6733
10 | 2601745.1004 | 1218137.8174
11 | 2601810.397 | 1218139.1612
12 | 2601735.9563 | 1218162.9749
13 | 2601735.8338 | 1218163.3119
14 | 2601734.8501 | 1218167.1581
15 | 2601740.8197 | 1218186.1037
16 | 2601829.404 | 1218150.4342
17 | 2601830.2383 | 1218150.929
18 | 2601842.7515 | 1218158.3506
19 | 2601817.9164 | 1218124.5045
20 | 2601848.5719 | 1218161.8027
21 | 2601819.2306 | 1218121.9429
22 | 2601850.3457 | 1218162.8547
23 | 2601824.0827 | 1218112.4851
24 | 2602013.142 | 1218255.3707
25 | 2602005.9221 | 1218272.7522
26 | 2602018.1569 | 1218243.2977
27 | 2601994.8883 | 1218298.7141
28 | 2602025.7578 | 1218224.999
29 | 2601993.111 | 1218302.8848
30 | 2602026.36 | 1218225.1303
31 | 2601989.6405 | 1218217.1078
32 | 2601975.9566 | 1218343.1391
33 | 2602032.0078 | 1218226.3617
34 | 2601973.361 | 1218213.5509
35 | 2601643.7322 | 1218031.3366
36 | 2601637.8318 | 1218025.2428
37 | 2601669.6181 | 1218055.8624
38 | 2601615.9145 | 1218002.6077
39 | 2601683.3987 | 1218066.6184
40 | 2601588.9763 | 1218029.1985
41 | 2601693.9288 | 1218073.7571
42 | 2601280.1388 | 1217805.0214
43 | 2601703.8551 | 1218079.2397
44 | 2601710.3087 | 1218082.8042
45 | 2601828.7105 | 1218103.4646
46 | 2601835.0797 | 1218091.0497
47 | 2601843.9437 | 1218073.772
48 | 2602071.6732 | 1218233.5762
49 | 2602101.2977 | 1218238.2541
50 | 2602100.2934 | 1218257.73
51 | 2601953.4974 | 1218208.0217
52 | 2601960.6894 | 1218192.1982
53 | 2601951.7814 | 1218207.4087
54 | 2601962.0449 | 1218189.2159
55 | 2601920.3806 | 1218195.8613
56 | 2601969.1048 | 1218173.6831
57 | 2601897.4802 | 1218186.118
58 | 2601437.1521 | 1217316.7591
59 | 2601430.0428 | 1217291.5547
60 | 2601443.4411 | 1217339.0552
61 | 2601420.0963 | 1217256.2918
62 | 2601458.536 | 1217349.3816
63 | 2601080.6123 | 1217434.9839
64 | 2601458.9299 | 1217256.0273
65 | 2601460.803 | 1217350.5848
66 | 2601463.8107 | 1217352.1812
67 | 2601846.1823 | 1218069.4085
68 | 2601852.8503 | 1218056.4113
69 | 2601861.1735 | 1218040.1876
70 | 2601742.624 | 1218190.2042
71 | 2601762.7463 | 1218213.633
72 | 2601732.6243 | 1218201.5911
73 | 2601773.4177 | 1218231.1473
74 | 2601774.4639 | 1218235.1054
75 | 2601766.902 | 1218218.4716
76 | 2601771.0152 | 1218219.44
77 | 2601962.7444 | 1218336.1438
78 | 2601959.8924 | 1218334.6338
79 | 2601880.8495 | 1218178.8068
80 | 2601878.171 | 1218177.4412
81 | 2601983.8636 | 1218141.2083
82 | 2601945.8715 | 1218327.2104
83 | 2601905.1372 | 1218302.2104
84 | 2601922.4541 | 1218312.7986
85 | 2601904.8064 | 1218302.0572
86 | 2601924.8055 | 1218314.4832
87 | 2601902.5397 | 1218301.0078
88 | 2601941.0744 | 1218324.6705
89 | 2601898.5117 | 1218299.1431
90 | 2601810.397 | 1218139.1612

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99616 | -0.07398 | 0.0013785 | 0.00034548
1 | 0.99604 | -0.076238 | 0.00012248 | 3.0697e-05
2 | 0.99616 | -0.073915 | 0 | 0
3 | 0.99591 | -0.078862 | 0.00033259 | 8.3356e-05
4 | 0.99589 | -0.079209 | 0.0024732 | 0.00061983
5 | 0.99666 | -0.064248 | 0.00062818 | 0.00015744
6 | 0.99583 | -0.080335 | 0.0021981 | 0.00055089
7 | 0.99585 | -0.080067 | 0.0010832 | 0.00027148
8 | 0.99729 | -0.052093 | 0.00089134 | 0.00022339
9 | 0.99582 | -0.080585 | 0.0001242 | 3.1128e-05
10 | 0.99584 | -0.080115 | 0.0013458 | 0.00033728
11 | 0.99737 | -0.050574 | 0 | 0
12 | 0.99568 | -0.083258 | 0.00018862 | 4.7272e-05
13 | 0.99568 | -0.083299 | 0.00069877 | 0.00017513
14 | 0.99566 | -0.08371 | 0.00061357 | 0.00015378
15 | 0.99556 | -0.085539 | 0.00089134 | 0.00022339
16 | 0.99801 | -0.038297 | 0.0023125 | 0.00057956
17 | 0.99804 | -0.037719 | 0.0011505 | 0.00028835
18 | 0.9985 | -0.028764 | 0.00052118 | 0.00013062
19 | 0.99723 | -0.053293 | 0.00055845 | 0.00013996
20 | 0.99872 | -0.02454 | 0.00082799 | 0.00020751
21 | 0.99721 | -0.05374 | 0.0037729 | 0.00094557
22 | 0.99879 | -0.023224 | 0.0058063 | 0.0014552
23 | 0.99716 | -0.054687 | 0.00068304 | 0.00017119
24 | 0.9946 | -0.10376 | 0.00097594 | 0.00024459
25 | 0.99432 | -0.10931 | 0.0017266 | 0.00043273
26 | 0.99482 | -0.099689 | 0.00047151 | 0.00011817
27 | 0.99393 | -0.11677 | 0.0014824 | 0.00037153
28 | 0.99514 | -0.093352 | 0 | 0
29 | 0.99388 | -0.11785 | 0.0017554 | 0.00043994
30 | 0.99514 | -0.093406 | 0.00045452 | 0.00011391
31 | 0.99592 | -0.078309 | 0.0017627 | 0.00044178
32 | 0.99341 | -0.12692 | 0 | 0
33 | 0.99512 | -0.093865 | 0.0028366 | 0.00071091
34 | 0.9963 | -0.07102 | 0.002779 | 0.00069648
35 | 0.99559 | -0.085188 | 0.00069718 | 0.00017473
36 | 0.99557 | -0.085492 | 0.00026274 | 6.5848e-05
37 | 0.99567 | -0.08347 | 0.00014497 | 3.6334e-05
38 | 0.99552 | -0.086476 | 0 | 0
39 | 0.99572 | -0.082583 | 0.000113 | 2.8321e-05
40 | 0.99546 | -0.087657 | 0.00025351 | 6.3536e-05
41 | 0.99575 | -0.081913 | 0.00027153 | 6.8051e-05
42 | 0.99495 | -0.097823 | 0.00027075 | 6.7857e-05
43 | 0.99579 | -0.081262 | 0.0007251 | 0.00018173
44 | 0.99581 | -0.080744 | 0.0010543 | 0.00026422
45 | 0.99712 | -0.05547 | 8.7337e-05 | 2.1889e-05
46 | 0.99706 | -0.056525 | 0.0023715 | 0.00059435
47 | 0.99703 | -0.057187 | 0.0010304 | 0.00025823
48 | 0.99506 | -0.095057 | 0.0011655 | 0.00029209
49 | 0.99504 | -0.095327 | 0 | 0
50 | 0.99503 | -0.095503 | 0.00051104 | 0.00012808
51 | 0.99682 | -0.061002 | 0 | 0
52 | 0.99669 | -0.063502 | 0.0017039 | 0.00042704
53 | 0.99688 | -0.059855 | 0.0045079 | 0.0011298
54 | 0.99667 | -0.063876 | 0.0030913 | 0.00077475
55 | 0.99811 | -0.036178 | 0.0024642 | 0.0006176
56 | 0.99662 | -0.064895 | 0.0027783 | 0.00069631
57 | 0.99908 | -0.017536 | 0.0044469 | 0.0011145
58 | 0.99418 | -0.11311 | 0.00026455 | 6.6302e-05
59 | 0.99417 | -0.11319 | 0.00010054 | 2.5197e-05
60 | 0.99419 | -0.11292 | 0 | 0
61 | 0.99417 | -0.11324 | 0 | 0
62 | 0.99418 | -0.11307 | 0.0001095 | 2.7444e-05
63 | 0.99449 | -0.10693 | 0.0003102 | 7.7743e-05
64 | 0.99417 | -0.11329 | 7.4146e-05 | 1.8583e-05
65 | 0.99418 | -0.11309 | 0.0001479 | 3.7068e-05
66 | 0.99418 | -0.1131 | 0.00019826 | 4.9689e-05
67 | 0.99703 | -0.057265 | 0.00043883 | 0.00010998
68 | 0.99702 | -0.057387 | 0.00026263 | 6.582e-05
69 | 0.99702 | -0.057454 | 0.00020973 | 5.2564e-05
70 | 0.99554 | -0.085877 | 0 | 0
71 | 0.99545 | -0.087663 | 0.00028914 | 7.2465e-05
72 | 0.99553 | -0.086142 | 0.00099495 | 0.00024936
73 | 0.99541 | -0.088493 | 0.00059454 | 0.000149
74 | 0.9954 | -0.088591 | 0.0013685 | 0.00034298
75 | 0.99544 | -0.088 | 0 | 0
76 | 0.99543 | -0.088076 | 0.001035 | 0.00025939
77 | 0.99325 | -0.13003 | 0.0011586 | 0.00029036
78 | 0.99321 | -0.13063 | 0.0012861 | 0.00032231
79 | 0.99987 | -0.0025374 | 0.0011101 | 0.00027823
80 | 1 | 0 | -0.092651 | -0.0229
81 | 0.9966 | -0.065287 | 0.00062526 | 0.0001567
82 | 0.99308 | -0.13324 | 0.0013842 | 0.00034692
83 | 0.99284 | -0.1378 | 0.00060906 | 0.00015264
84 | 0.99291 | -0.13649 | 0.0016493 | 0.00041334
85 | 0.99284 | -0.13782 | 0.0010677 | 0.0002676
86 | 0.99293 | -0.13622 | 0.0012335 | 0.00030914
87 | 0.99284 | -0.1379 | 0.0012875 | 0.00032268
88 | 0.99304 | -0.134 | 0.0013987 | 0.00035054
89 | 0.99284 | -0.13796 | 0.00067262 | 0.00016857
90 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0077802 | 0.0019317 | -0.0077793 | -0.0019314 | 8.3091e-07 | 3.1799e-07 | 0.011615 | 0.011615 | 0.011615 | 0.99616 | -0.07398 | 0.99604 | -0.076238 | 3.191
1 | -0.0091586 | -0.0022772 | 0.0091587 | 0.0022772 | 2.7974e-08 | 1.2709e-08 | 0.013674 | 0.013674 | 0.013674 | 0.99616 | -0.07398 | 0.99616 | -0.073915 | 3.7567
2 | 0.0076569 | 0.0019007 | -0.0076559 | -0.0019003 | 9.5013e-07 | 3.558e-07 | 0.011432 | 0.011432 | 0.011432 | 0.99604 | -0.076238 | 0.99591 | -0.078862 | 3.1408
3 | 0.011582 | 0.0029027 | -0.011579 | -0.0029011 | 2.9204e-06 | 1.5304e-06 | 0.0173 | 0.017301 | 0.017301 | 0.99616 | -0.073915 | 0.99589 | -0.079209 | 4.7529
4 | -0.020741 | -0.0051798 | 0.02075 | 0.0051856 | 9.5305e-06 | 5.7545e-06 | 0.030975 | 0.030975 | 0.030975 | 0.99616 | -0.073915 | 0.99666 | -0.064248 | 8.5095
5 | 0.0073233 | 0.001817 | -0.0073228 | -0.0018168 | 5.1012e-07 | 1.7847e-07 | 0.010936 | 0.010936 | 0.010936 | 0.99591 | -0.078862 | 0.99583 | -0.080335 | 3.0043
6 | 0.0091058 | 0.0022813 | -0.0091054 | -0.0022811 | 3.7202e-07 | 1.6836e-07 | 0.013605 | 0.013605 | 0.013605 | 0.99589 | -0.079209 | 0.99585 | -0.080067 | 3.7377
7 | -0.021378 | -0.005343 | 0.021391 | 0.0053505 | 1.2361e-05 | 7.4892e-06 | 0.031912 | 0.031912 | 0.031912 | 0.99666 | -0.064248 | 0.99729 | -0.052093 | 8.7672
8 | 0.0051247 | 0.0012659 | -0.0051247 | -0.0012659 | 6.0239e-08 | 2.8525e-09 | 0.0076511 | 0.0076511 | 0.0076511 | 0.99583 | -0.080335 | 0.99582 | -0.080585 | 2.102
9 | 0.0080222 | 0.0020097 | -0.0080222 | -0.0020097 | 1.8401e-08 | 7.3334e-09 | 0.011987 | 0.011987 | 0.011987 | 0.99585 | -0.080067 | 0.99584 | -0.080115 | 3.293
10 | -0.022282 | -0.0055739 | 0.022284 | 0.0055749 | 1.61e-06 | 9.7973e-07 | 0.033242 | 0.033242 | 0.033242 | 0.99729 | -0.052093 | 0.99737 | -0.050574 | 9.1325
11 | 0.0050005 | 0.0012348 | -0.0050004 | -0.0012348 | 3.7571e-08 | 6.5888e-10 | 0.0074655 | 0.0074656 | 0.0074656 | 0.99582 | -0.080585 | 0.99581 | -0.080744 | 2.051
12 | 0.0066764 | 0.0016724 | -0.0066754 | -0.0016721 | 9.9895e-07 | 2.9112e-07 | 0.0099758 | 0.0099759 | 0.0099759 | 0.99584 | -0.080115 | 0.99568 | -0.083258 | 2.7406
13 | 0.0094168 | 0.0023594 | -0.0094156 | -0.0023589 | 1.2193e-06 | 5.6539e-07 | 0.014049 | 0.014049 | 0.014049 | 0.99737 | -0.050574 | 0.99723 | -0.053293 | 3.8597
14 | -0.0317 | -0.0079343 | 0.031719 | 0.0079459 | 1.8534e-05 | 1.1573e-05 | 0.047291 | 0.047291 | 0.047291 | 0.99737 | -0.050574 | 0.99801 | -0.038297 | 12.9921
15 | 0.0064868 | 0.0016248 | -0.0064868 | -0.0016248 | 1.2637e-08 | 3.4233e-09 | 0.009694 | 0.009694 | 0.009694 | 0.99568 | -0.083258 | 0.99568 | -0.083299 | 2.6632
16 | 0.005788 | 0.0014497 | -0.0057879 | -0.0014497 | 1.1328e-07 | 1.9988e-08 | 0.0086497 | 0.0086498 | 0.0086498 | 0.99568 | -0.083299 | 0.99566 | -0.08371 | 2.3763
17 | 0.0051744 | 0.0012959 | -0.0051739 | -0.0012958 | 4.5073e-07 | 2.7072e-08 | 0.0077328 | 0.0077329 | 0.0077329 | 0.99566 | -0.08371 | 0.99556 | -0.085539 | 2.1244
18 | 0.0042826 | 0.0010725 | -0.0042825 | -0.0010725 | 6.8824e-08 | -1.4203e-08 | 0.0064006 | 0.0064006 | 0.0064006 | 0.99556 | -0.085539 | 0.99554 | -0.085877 | 1.7584
19 | -0.034031 | -0.0085255 | 0.034032 | 0.0085261 | 9.3641e-07 | 5.8663e-07 | 0.050739 | 0.050739 | 0.050739 | 0.99801 | -0.038297 | 0.99804 | -0.037719 | 13.9393
20 | -0.035183 | -0.0088144 | 0.035198 | 0.0088238 | 1.5011e-05 | 9.4169e-06 | 0.052454 | 0.052454 | 0.052454 | 0.99804 | -0.037719 | 0.9985 | -0.028764 | 14.4106
21 | -0.035719 | -0.0089544 | 0.035726 | 0.008959 | 7.1907e-06 | 4.5135e-06 | 0.053231 | 0.053231 | 0.053231 | 0.9985 | -0.028764 | 0.99872 | -0.02454 | 14.6239
22 | 0.0088572 | 0.0022189 | -0.008857 | -0.0022188 | 1.8857e-07 | 8.3125e-08 | 0.013216 | 0.013216 | 0.013216 | 0.99723 | -0.053293 | 0.99721 | -0.05374 | 3.6307
23 | -0.036554 | -0.0091665 | 0.036557 | 0.0091679 | 2.294e-06 | 1.4412e-06 | 0.054465 | 0.054465 | 0.054465 | 0.99872 | -0.02454 | 0.99879 | -0.023224 | 14.9628
24 | 0.0050841 | 0.0012733 | -0.0050839 | -0.0012733 | 2.294e-07 | 8.1449e-09 | 0.0075861 | 0.0075861 | 0.0075861 | 0.99721 | -0.05374 | 0.99716 | -0.054687 | 2.0841
25 | -0.042363 | -0.010623 | 0.04241 | 0.010653 | 4.6945e-05 | 2.9633e-05 | 0.063115 | 0.063115 | 0.063115 | 0.99879 | -0.023224 | 1 | 0 | 17.3393
26 | 0.0044008 | 0.0011021 | -0.0044007 | -0.0011021 | 1.6395e-07 | -2.7319e-08 | 0.0065669 | 0.0065669 | 0.0065669 | 0.99716 | -0.054687 | 0.99712 | -0.05547 | 1.8041
27 | 0.016732 | 0.0041987 | -0.016727 | -0.0041961 | 4.4232e-06 | 2.5867e-06 | 0.025034 | 0.025034 | 0.025034 | 0.9946 | -0.10376 | 0.99432 | -0.10931 | 6.8774
28 | -0.017707 | -0.0044433 | 0.017711 | 0.0044453 | 3.4411e-06 | 2.0326e-06 | 0.026494 | 0.026494 | 0.026494 | 0.9946 | -0.10376 | 0.99482 | -0.099689 | 7.2785
29 | 0.015 | 0.0037634 | -0.014995 | -0.0037604 | 5.3316e-06 | 3.0465e-06 | 0.02245 | 0.02245 | 0.02245 | 0.99432 | -0.10931 | 0.99393 | -0.11677 | 6.1676
30 | -0.018182 | -0.0045635 | 0.018188 | 0.0045668 | 5.4969e-06 | 3.2607e-06 | 0.027199 | 0.027199 | 0.027199 | 0.99482 | -0.099689 | 0.99514 | -0.093352 | 7.4723
31 | 0.013513 | 0.0033888 | -0.013512 | -0.0033884 | 6.9583e-07 | 3.8658e-07 | 0.020231 | 0.020231 | 0.020231 | 0.99393 | -0.11677 | 0.99388 | -0.11785 | 5.5579
32 | 0.0049678 | 0.0012439 | -0.0049678 | -0.0012439 | 1.2751e-08 | 1.537e-10 | 0.0074279 | 0.0074279 | 0.0074279 | 0.99514 | -0.093352 | 0.99514 | -0.093406 | 2.0406
33 | -0.023156 | -0.0058107 | 0.023172 | 0.0058208 | 1.6623e-05 | 1.0158e-05 | 0.034627 | 0.034627 | 0.034627 | 0.99514 | -0.093352 | 0.99592 | -0.078309 | 9.5129
34 | 0.011757 | 0.0029485 | -0.011752 | -0.0029458 | 5.0844e-06 | 2.6872e-06 | 0.017603 | 0.017603 | 0.017603 | 0.99388 | -0.11785 | 0.99341 | -0.12692 | 4.836
35 | 0.0045133 | 0.00113 | -0.0045132 | -0.00113 | 9.8714e-08 | -1.1922e-08 | 0.0067482 | 0.0067482 | 0.0067482 | 0.99514 | -0.093406 | 0.99512 | -0.093865 | 1.8539
36 | -0.024935 | -0.0062626 | 0.024944 | 0.0062679 | 8.6755e-06 | 5.3354e-06 | 0.03726 | 0.03726 | 0.03726 | 0.99592 | -0.078309 | 0.9963 | -0.07102 | 10.2364
37 | 0.011752 | 0.0029458 | -0.01175 | -0.0029449 | 1.7371e-06 | 9.1825e-07 | 0.017603 | 0.017603 | 0.017603 | 0.99341 | -0.12692 | 0.99325 | -0.13003 | 4.836
38 | 0.0016766 | 0.00041907 | -0.0016765 | -0.00041954 | 9.5016e-08 | -4.6299e-07 | 0.0025067 | 0.0025069 | 0.0025069 | 0.99512 | -0.093865 | 0.99506 | -0.095057 | 0.6887
39 | -0.027723 | -0.0069644 | 0.027736 | 0.0069726 | 1.3262e-05 | 8.2189e-06 | 0.041411 | 0.041411 | 0.041411 | 0.9963 | -0.07102 | 0.99682 | -0.061002 | 11.3766
40 | 0.0019938 | 0.00048208 | -0.0019937 | -0.00048217 | 2.813e-08 | -9.2296e-08 | 0.0029738 | 0.0029738 | 0.0029738 | 0.99559 | -0.085188 | 0.99557 | -0.085492 | 0.81699
41 | -0.002691 | -0.00065681 | 0.0026912 | 0.00065648 | 2.1595e-07 | -3.2621e-07 | 0.0040158 | 0.0040156 | 0.0040158 | 0.99559 | -0.085188 | 0.99567 | -0.08347 | 1.1032
42 | 0.001731 | 0.00041632 | -0.0017309 | -0.00041668 | 7.8722e-08 | -3.593e-07 | 0.0025812 | 0.0025813 | 0.0025813 | 0.99557 | -0.085492 | 0.99552 | -0.086476 | 0.70915
43 | -0.0028361 | -0.00069282 | 0.0028363 | 0.00069266 | 1.1752e-07 | -1.5235e-07 | 0.0042323 | 0.0042322 | 0.0042323 | 0.99567 | -0.08347 | 0.99572 | -0.082583 | 1.1627
44 | 0.0017309 | 0.00041668 | -0.0017308 | -0.00041711 | 9.4585e-08 | -4.3159e-07 | 0.0025813 | 0.0025815 | 0.0025815 | 0.99552 | -0.086476 | 0.99546 | -0.087657 | 0.7092
45 | -0.0029493 | -0.00072098 | 0.0029494 | 0.00072088 | 9.2438e-08 | -1.0638e-07 | 0.0044011 | 0.004401 | 0.0044011 | 0.99572 | -0.082583 | 0.99575 | -0.081913 | 1.2091
46 | 0.0014773 | 0.00035358 | -0.0014766 | -0.00035809 | 6.9477e-07 | -4.5141e-06 | 0.0022025 | 0.0022042 | 0.0022042 | 0.99546 | -0.087657 | 0.99495 | -0.097823 | 0.60556
47 | -0.0032209 | -0.00078893 | 0.003221 | 0.00078884 | 9.8252e-08 | -8.4633e-08 | 0.0048068 | 0.0048067 | 0.0048068 | 0.99575 | -0.081913 | 0.99579 | -0.081262 | 1.3205
48 | 0.0012059 | 0.00029023 | -0.0012054 | -0.00029536 | 5.1093e-07 | -5.1303e-06 | 0.0017993 | 0.0018012 | 0.0018012 | 0.99495 | -0.097823 | 0.99449 | -0.10693 | 0.49483
49 | -0.0039461 | -0.00097057 | 0.0039462 | 0.00097054 | 9.5921e-08 | -3.4522e-08 | 0.0058902 | 0.0058902 | 0.0058902 | 0.99579 | -0.081262 | 0.99581 | -0.080744 | 1.6182
50 | 0.0043133 | 0.0010802 | -0.0043131 | -0.0010802 | 2.1678e-07 | -4.3254e-08 | 0.0064366 | 0.0064366 | 0.0064366 | 0.99712 | -0.05547 | 0.99706 | -0.056525 | 1.7683
51 | 0.0019416 | 0.0004859 | -0.0019416 | -0.00048611 | 6.1135e-08 | -2.1413e-07 | 0.0028974 | 0.0028975 | 0.0028975 | 0.99706 | -0.056525 | 0.99703 | -0.057187 | 0.79602
52 | 0.00091119 | 0.00022788 | -0.00091119 | -0.00022794 | 3.4004e-09 | -6.1783e-08 | 0.0013597 | 0.0013598 | 0.0013598 | 0.99703 | -0.057187 | 0.99703 | -0.057265 | 0.37356
53 | 0.00051106 | 0.00012744 | -0.00051105 | -0.00012783 | 6.5666e-09 | -3.8541e-07 | 0.00076401 | 0.00076415 | 0.00076415 | 0.99506 | -0.095057 | 0.99504 | -0.095327 | 0.20993
54 | 0.00051105 | 0.00012783 | -0.00051104 | -0.00012808 | 4.2709e-09 | -2.5058e-07 | 0.00076415 | 0.00076424 | 0.00076424 | 0.99504 | -0.095327 | 0.99503 | -0.095503 | 0.20996
55 | 0.0082 | 0.0020547 | -0.0081991 | -0.0020543 | 9.766e-07 | 3.9847e-07 | 0.012241 | 0.012241 | 0.012241 | 0.99682 | -0.061002 | 0.99669 | -0.063502 | 3.3628
56 | -0.035936 | -0.0090273 | 0.035938 | 0.0090285 | 1.9669e-06 | 1.2351e-06 | 0.053651 | 0.053651 | 0.053651 | 0.99682 | -0.061002 | 0.99688 | -0.059855 | 14.7394
57 | 0.0064952 | 0.0016272 | -0.006495 | -0.0016272 | 1.1551e-07 | 3.1233e-08 | 0.0096967 | 0.0096968 | 0.0096968 | 0.99669 | -0.063502 | 0.99667 | -0.063876 | 2.6639
58 | -0.040446 | -0.010158 | 0.040492 | 0.010187 | 4.5751e-05 | 2.8844e-05 | 0.06038 | 0.06038 | 0.06038 | 0.99688 | -0.059855 | 0.99811 | -0.036178 | 16.5879
59 | 0.0034037 | 0.00085244 | -0.0034036 | -0.00085255 | 1.6521e-07 | -1.166e-07 | 0.0050815 | 0.0050816 | 0.0050816 | 0.99667 | -0.063876 | 0.99662 | -0.064895 | 1.396
60 | -0.042956 | -0.010805 | 0.042994 | 0.010829 | 3.829e-05 | 2.418e-05 | 0.064054 | 0.064054 | 0.064054 | 0.99811 | -0.036178 | 0.99908 | -0.017536 | 17.5972
61 | 0.00062527 | 0.00015625 | -0.00062526 | -0.0001567 | 1.1656e-08 | -4.5735e-07 | 0.00093341 | 0.00093357 | 0.00093357 | 0.99662 | -0.064895 | 0.9966 | -0.065287 | 0.25648
62 | -0.047441 | -0.011943 | 0.047475 | 0.011965 | 3.4042e-05 | 2.1549e-05 | 0.070677 | 0.070677 | 0.070677 | 0.99908 | -0.017536 | 0.99987 | -0.0025374 | 19.4167
63 | 0.00017468 | 4.2435e-05 | -0.00017468 | -4.2774e-05 | 6.6921e-10 | -3.3915e-07 | 0.00026099 | 0.0002611 | 0.0002611 | 0.99418 | -0.11311 | 0.99417 | -0.11319 | 0.071731
64 | -0.00043923 | -0.00010874 | 0.00043924 | 0.00010844 | 3.7486e-09 | -2.98e-07 | 0.00065694 | 0.00065684 | 0.00065694 | 0.99418 | -0.11311 | 0.99419 | -0.11292 | 0.18048
65 | 7.4146e-05 | 1.7578e-05 | -7.4146e-05 | -1.8053e-05 | 1.6841e-10 | -4.7498e-07 | 0.00011063 | 0.00011079 | 0.00011079 | 0.99417 | -0.11319 | 0.99417 | -0.11324 | 0.030438
66 | 0.00045567 | 0.00011389 | -0.00045567 | -0.00011412 | 3.2003e-09 | -2.3591e-07 | 0.0006819 | 0.00068199 | 0.00068199 | 0.99419 | -0.11292 | 0.99418 | -0.11307 | 0.18736
67 | -0.00089491 | -0.00022233 | 0.00089516 | 0.00021762 | 2.5191e-07 | -4.7068e-06 | 0.0013387 | 0.0013371 | 0.0013387 | 0.99419 | -0.11292 | 0.99449 | -0.10693 | 0.36778
68 | 7.4146e-05 | 1.8053e-05 | -7.4146e-05 | -1.8583e-05 | 1.8856e-10 | -5.3017e-07 | 0.00011079 | 0.00011098 | 0.00011098 | 0.99417 | -0.11324 | 0.99417 | -0.11329 | 0.030488
69 | 0.00034617 | 8.668e-05 | -0.00034617 | -8.6713e-05 | 2.5832e-10 | -3.3114e-08 | 0.00051809 | 0.0005181 | 0.0005181 | 0.99418 | -0.11307 | 0.99418 | -0.11309 | 0.14234
70 | 0.00019826 | 4.9645e-05 | -0.00019826 | -4.9689e-05 | 1.1242e-10 | -4.4082e-08 | 0.00029673 | 0.00029674 | 0.00029674 | 0.99418 | -0.11309 | 0.99418 | -0.1131 | 0.081523
71 | 0.00047236 | 0.00011796 | -0.00047236 | -0.00011815 | 2.7216e-09 | -1.8876e-07 | 0.00070483 | 0.0007049 | 0.0007049 | 0.99703 | -0.057265 | 0.99702 | -0.057387 | 0.19365
72 | 0.00020973 | 5.2327e-05 | -0.00020973 | -5.2564e-05 | 6.6981e-10 | -2.3737e-07 | 0.00031294 | 0.00031302 | 0.00031302 | 0.99702 | -0.057387 | 0.99702 | -0.057454 | 0.085995
73 | 0.0032875 | 0.0008233 | -0.0032872 | -0.00082353 | 2.7962e-07 | -2.2258e-07 | 0.0049136 | 0.0049137 | 0.0049137 | 0.99554 | -0.085877 | 0.99545 | -0.087663 | 1.3499
74 | 0.00099496 | 0.00024917 | -0.00099495 | -0.00024936 | 1.2568e-08 | -1.89e-07 | 0.0014871 | 0.0014872 | 0.0014872 | 0.99554 | -0.085877 | 0.99553 | -0.086142 | 0.40856
75 | 0.0029981 | 0.00075106 | -0.0029981 | -0.00075111 | 4.8038e-08 | -5.2173e-08 | 0.0044815 | 0.0044815 | 0.0044815 | 0.99545 | -0.087663 | 0.99544 | -0.088 | 1.2312
76 | 0.0013685 | 0.00034293 | -0.0013685 | -0.00034298 | 6.4251e-09 | -4.9107e-08 | 0.0020457 | 0.0020457 | 0.0020457 | 0.99541 | -0.088493 | 0.9954 | -0.088591 | 0.56202
77 | -0.001963 | -0.00049193 | 0.0019631 | 0.00049178 | 4.6095e-08 | -1.5606e-07 | 0.0029345 | 0.0029344 | 0.0029345 | 0.99541 | -0.088493 | 0.99544 | -0.088 | 0.80618
78 | 0.001035 | 0.00025934 | -0.001035 | -0.00025939 | 3.7824e-09 | -5.236e-08 | 0.0015471 | 0.0015471 | 0.0015471 | 0.99544 | -0.088 | 0.99543 | -0.088076 | 0.42503
79 | 0.010591 | 0.0026545 | -0.010591 | -0.0026544 | 3.0467e-07 | 1.5323e-07 | 0.015867 | 0.015867 | 0.015867 | 0.99325 | -0.13003 | 0.99321 | -0.13063 | 4.3591
80 | 0.009305 | 0.0023321 | -0.0093038 | -0.0023315 | 1.1562e-06 | 5.3467e-07 | 0.013941 | 0.013941 | 0.013941 | 0.99321 | -0.13063 | 0.99308 | -0.13324 | 3.8298
81 | -0.048585 | -0.012243 | 0.048591 | 0.012247 | 5.8982e-06 | 3.7354e-06 | 0.072329 | 0.072329 | 0.072329 | 0.99987 | -0.0025374 | 1 | 0 | 19.8705
82 | 0.0079196 | 0.0019846 | -0.0079193 | -0.0019845 | 2.8663e-07 | 1.1322e-07 | 0.011867 | 0.011867 | 0.011867 | 0.99308 | -0.13324 | 0.99304 | -0.134 | 3.26
83 | -0.0036369 | -0.00091141 | 0.0036372 | 0.00091129 | 2.271e-07 | -1.1827e-07 | 0.0054508 | 0.0054507 | 0.0054508 | 0.99284 | -0.1378 | 0.99291 | -0.13649 | 1.4975
84 | 0.0030279 | 0.00075877 | -0.0030279 | -0.00075877 | 2.8149e-09 | -2.9129e-09 | 0.004538 | 0.004538 | 0.004538 | 0.99284 | -0.1378 | 0.99284 | -0.13782 | 1.2467
85 | -0.0052864 | -0.0013246 | 0.0052865 | 0.0013246 | 6.808e-08 | 6.1582e-09 | 0.0079223 | 0.0079223 | 0.0079223 | 0.99291 | -0.13649 | 0.99293 | -0.13622 | 2.1765
86 | 0.0019601 | 0.00049117 | -0.0019601 | -0.0004912 | 8.0839e-09 | -2.7129e-08 | 0.0029377 | 0.0029377 | 0.0029377 | 0.99284 | -0.13782 | 0.99284 | -0.1379 | 0.80707
87 | -0.00652 | -0.0016338 | 0.0065206 | 0.001634 | 6.8875e-07 | 1.9193e-07 | 0.0097708 | 0.0097707 | 0.0097708 | 0.99293 | -0.13622 | 0.99304 | -0.134 | 2.6843
88 | 0.00067262 | 0.00016852 | -0.00067262 | -0.00016857 | 1.6915e-09 | -5.6318e-08 | 0.0010081 | 0.0010081 | 0.0010081 | 0.99284 | -0.1379 | 0.99284 | -0.13796 | 0.27695

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.094133 | 0.023271

## res_load
| p_mw | q_mvar
0 | 0.0013785 | 0.00034548
1 | 0.00012248 | 3.0697e-05
2 | 0.00033259 | 8.3356e-05
3 | 0.0024732 | 0.00061983
4 | 0.00062818 | 0.00015744
5 | 0.0021981 | 0.00055089
6 | 0.0010832 | 0.00027148
7 | 0.00089134 | 0.00022339
8 | 0.0001242 | 3.1128e-05
9 | 0.0013458 | 0.00033728
10 | 0.00018862 | 4.7272e-05
11 | 0.00069877 | 0.00017513
12 | 0.00061357 | 0.00015378
13 | 0.00089134 | 0.00022339
14 | 0.0023125 | 0.00057956
15 | 0.0011505 | 0.00028835
16 | 0.00052118 | 0.00013062
17 | 0.00055845 | 0.00013996
18 | 0.00082799 | 0.00020751
19 | 0.0037729 | 0.00094557
20 | 0.0058063 | 0.0014552
21 | 0.00068304 | 0.00017119
22 | 0.00097594 | 0.00024459
23 | 0.0017266 | 0.00043273
24 | 0.00047151 | 0.00011817
25 | 0.0014824 | 0.00037153
26 | 0.0017554 | 0.00043994
27 | 0.00045452 | 0.00011391
28 | 0.0017627 | 0.00044178
29 | 0.0028366 | 0.00071091
30 | 0.002779 | 0.00069648
31 | 0.00069718 | 0.00017473
32 | 0.00026274 | 6.5848e-05
33 | 0.00014497 | 3.6334e-05
34 | 0.000113 | 2.8321e-05
35 | 0.00025351 | 6.3536e-05
36 | 0.00027153 | 6.8051e-05
37 | 0.00027075 | 6.7857e-05
38 | 0.0007251 | 0.00018173
39 | 0.0010543 | 0.00026422
40 | 8.7337e-05 | 2.1889e-05
41 | 0.0023715 | 0.00059435
42 | 0.0010304 | 0.00025823
43 | 0.0011655 | 0.00029209
44 | 0.00051104 | 0.00012808
45 | 0.0017039 | 0.00042704
46 | 0.0045079 | 0.0011298
47 | 0.0030913 | 0.00077475
48 | 0.0024642 | 0.0006176
49 | 0.0027783 | 0.00069631
50 | 0.0044469 | 0.0011145
51 | 0.00026455 | 6.6302e-05
52 | 0.00010054 | 2.5197e-05
53 | 0.0001095 | 2.7444e-05
54 | 0.0003102 | 7.7743e-05
55 | 7.4146e-05 | 1.8583e-05
56 | 0.0001479 | 3.7068e-05
57 | 0.00019826 | 4.9689e-05
58 | 0.00043883 | 0.00010998
59 | 0.00026263 | 6.582e-05
60 | 0.00020973 | 5.2564e-05
61 | 0.00028914 | 7.2465e-05
62 | 0.00099495 | 0.00024936
63 | 0.00059454 | 0.000149
64 | 0.0013685 | 0.00034298
65 | 0.001035 | 0.00025939
66 | 0.0011586 | 0.00029036
67 | 0.0012861 | 0.00032231
68 | 0.0011101 | 0.00027823
69 | 0.0014824 | 0.00037153
70 | 0.00062526 | 0.0001567
71 | 0.0013842 | 0.00034692
72 | 0.00060906 | 0.00015264
73 | 0.0016493 | 0.00041334
74 | 0.0010677 | 0.0002676
75 | 0.0012335 | 0.00030914
76 | 0.0012875 | 0.00032268
77 | 0.0013987 | 0.00035054
78 | 0.00067262 | 0.00016857

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1