## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2465-1_1_5_node_344 | 0.4 | n |  | TRUE
1 | bus_LV_2465-1_1_5_node_416 | 0.4 | n |  | TRUE
2 | bus_LV_2465-1_1_5_node_413 | 0.4 | n |  | TRUE
3 | bus_LV_2465-1_1_5_node_347 | 0.4 | n |  | TRUE
4 | bus_LV_2465-1_1_5_node_348 | 0.4 | n |  | TRUE
5 | bus_LV_2465-1_1_5_node_349 | 0.4 | n |  | TRUE
6 | bus_LV_2465-1_1_5_node_350 | 0.4 | n |  | TRUE
7 | bus_LV_2465-1_1_5_node_351 | 0.4 | n |  | TRUE
8 | bus_LV_2465-1_1_5_node_353 | 0.4 | n |  | TRUE
9 | bus_LV_2465-1_1_5_node_354 | 0.4 | n |  | TRUE
10 | bus_LV_2465-1_1_5_node_400 | 0.4 | n |  | TRUE
11 | bus_LV_2465-1_1_5_node_352 | 0.4 | n |  | TRUE
12 | bus_LV_2465-1_1_5_node_367 | 0.4 | n |  | TRUE
13 | bus_LV_2465-1_1_5_node_466 | 0.4 | n |  | TRUE
14 | bus_LV_2465-1_1_5_node_359 | 0.4 | n |  | TRUE
15 | bus_LV_2465-1_1_5_node_449 | 0.4 | n |  | TRUE
16 | bus_LV_2465-1_1_5_node_434 | 0.4 | n |  | TRUE
17 | bus_LV_2465-1_1_5_node_355 | 0.4 | n |  | TRUE
18 | bus_LV_2465-1_1_5_node_356 | 0.4 | n |  | TRUE
19 | bus_LV_2465-1_1_5_node_357 | 0.4 | n |  | TRUE
20 | bus_LV_2465-1_1_5_node_358 | 0.4 | n |  | TRUE
21 | bus_LV_2465-1_1_5_node_361 | 0.4 | n |  | TRUE
22 | bus_LV_2465-1_1_5_node_369 | 0.4 | n |  | TRUE
23 | bus_LV_2465-1_1_5_node_360 | 0.4 | n |  | TRUE
24 | bus_LV_2465-1_1_5_node_502 | 0.4 | n |  | TRUE
25 | bus_LV_2465-1_1_5_node_364 | 0.4 | n |  | TRUE
26 | bus_LV_2465-1_1_5_node_467 | 0.4 | n |  | TRUE
27 | bus_LV_2465-1_1_5_node_362 | 0.4 | n |  | TRUE
28 | bus_LV_2465-1_1_5_node_365 | 0.4 | n |  | TRUE
29 | bus_LV_2465-1_1_5_node_409 | 0.4 | n |  | TRUE
30 | bus_LV_2465-1_1_5_node_368 | 0.4 | n |  | TRUE
31 | bus_LV_2465-1_1_5_node_370 | 0.4 | n |  | TRUE
32 | bus_LV_2465-1_1_5_node_371 | 0.4 | n |  | TRUE
33 | bus_LV_2465-1_1_5_node_454 | 0.4 | n |  | TRUE
34 | bus_LV_2465-1_1_5_node_372 | 0.4 | n |  | TRUE
35 | bus_LV_2465-1_1_5_node_373 | 0.4 | n |  | TRUE
36 | bus_LV_2465-1_1_5_node_374 | 0.4 | n |  | TRUE
37 | bus_LV_2465-1_1_5_node_375 | 0.4 | n |  | TRUE
38 | bus_LV_2465-1_1_5_node_376 | 0.4 | n |  | TRUE
39 | bus_LV_2465-1_1_5_node_377 | 0.4 | n |  | TRUE
40 | bus_LV_2465-1_1_5_node_448 | 0.4 | n |  | TRUE
41 | bus_LV_2465-1_1_5_node_423 | 0.4 | n |  | TRUE
42 | bus_LV_2465-1_1_5_node_385 | 0.4 | n |  | TRUE
43 | bus_LV_2465-1_1_5_node_378 | 0.4 | n |  | TRUE
44 | bus_LV_2465-1_1_5_node_379 | 0.4 | n |  | TRUE
45 | bus_LV_2465-1_1_5_node_380 | 0.4 | n |  | TRUE
46 | bus_LV_2465-1_1_5_node_381 | 0.4 | n |  | TRUE
47 | bus_LV_2465-1_1_5_node_382 | 0.4 | n |  | TRUE
48 | bus_LV_2465-1_1_5_node_425 | 0.4 | n |  | TRUE
49 | bus_LV_2465-1_1_5_node_398 | 0.4 | n |  | TRUE
50 | bus_LV_2465-1_1_5_node_383 | 0.4 | n |  | TRUE
51 | bus_LV_2465-1_1_5_node_384 | 0.4 | n |  | TRUE
52 | bus_LV_2465-1_1_5_node_386 | 0.4 | n |  | TRUE
53 | bus_LV_2465-1_1_5_node_388 | 0.4 | n |  | TRUE
54 | bus_LV_2465-1_1_5_node_451 | 0.4 | n |  | TRUE
55 | bus_LV_2465-1_1_5_node_468 | 0.4 | n |  | TRUE
56 | bus_LV_2465-1_1_5_node_389 | 0.4 | n |  | TRUE
57 | bus_LV_2465-1_1_5_node_390 | 0.4 | n |  | TRUE
58 | bus_LV_2465-1_1_5_node_392 | 0.4 | n |  | TRUE
59 | bus_LV_2465-1_1_5_node_427 | 0.4 | n |  | TRUE
60 | bus_LV_2465-1_1_5_node_393 | 0.4 | n |  | TRUE
61 | bus_LV_2465-1_1_5_node_442 | 0.4 | n |  | TRUE
62 | bus_LV_2465-1_1_5_node_481 | 0.4 | n |  | TRUE
63 | bus_LV_2465-1_1_5_node_395 | 0.4 | n |  | TRUE
64 | bus_LV_2465-1_1_5_node_396 | 0.4 | n |  | TRUE
65 | bus_LV_2465-1_1_5_node_397 | 0.4 | n |  | TRUE
66 | bus_LV_2465-1_1_5_node_399 | 0.4 | n |  | TRUE
67 | bus_LV_2465-1_1_5_node_465 | 0.4 | n |  | TRUE
68 | bus_LV_2465-1_1_5_node_453 | 0.4 | n |  | TRUE
69 | bus_LV_2465-1_1_5_node_401 | 0.4 | n |  | TRUE
70 | bus_LV_2465-1_1_5_node_402 | 0.4 | n |  | TRUE
71 | bus_LV_2465-1_1_5_node_403 | 0.4 | n |  | TRUE
72 | bus_LV_2465-1_1_5_node_404 | 0.4 | n |  | TRUE
73 | bus_LV_2465-1_1_5_node_405 | 0.4 | n |  | TRUE
74 | bus_LV_2465-1_1_5_node_406 | 0.4 | n |  | TRUE
75 | bus_LV_2465-1_1_5_node_407 | 0.4 | n |  | TRUE
76 | bus_LV_2465-1_1_5_node_408 | 0.4 | n |  | TRUE
77 | bus_LV_2465-1_1_5_node_476 | 0.4 | n |  | TRUE
78 | bus_LV_2465-1_1_5_node_482 | 0.4 | n |  | TRUE
79 | bus_LV_2465-1_1_5_node_436 | 0.4 | n |  | TRUE
80 | bus_LV_2465-1_1_5_node_480 | 0.4 | n |  | TRUE
81 | bus_LV_2465-1_1_5_node_490 | 0.4 | n |  | TRUE
82 | bus_LV_2465-1_1_5_node_462 | 0.4 | n |  | TRUE
83 | bus_LV_2465-1_1_5_node_410 | 0.4 | n |  | TRUE
84 | bus_LV_2465-1_1_5_node_411 | 0.4 | n |  | TRUE
85 | bus_LV_2465-1_1_5_node_412 | 0.4 | n |  | TRUE
86 | bus_LV_2465-1_1_5_node_433 | 0.4 | n |  | TRUE
87 | bus_LV_2465-1_1_5_node_494 | 0.4 | n |  | TRUE
88 | bus_LV_2465-1_1_5_node_414 | 0.4 | n |  | TRUE
89 | bus_LV_2465-1_1_5_node_415 | 0.4 | n |  | TRUE
90 | bus_LV_2465-1_1_5_node_417 | 0.4 | n |  | TRUE
91 | bus_LV_2465-1_1_5_node_432 | 0.4 | n |  | TRUE
92 | bus_LV_2465-1_1_5_node_464 | 0.4 | n |  | TRUE
93 | bus_LV_2465-1_1_5_node_418 | 0.4 | n |  | TRUE
94 | bus_LV_2465-1_1_5_node_419 | 0.4 | n |  | TRUE
95 | bus_LV_2465-1_1_5_node_420 | 0.4 | n |  | TRUE
96 | bus_LV_2465-1_1_5_node_421 | 0.4 | n |  | TRUE
97 | bus_LV_2465-1_1_5_node_422 | 0.4 | n |  | TRUE
98 | bus_LV_2465-1_1_5_node_446 | 0.4 | n |  | TRUE
99 | bus_LV_2465-1_1_5_node_463 | 0.4 | n |  | TRUE
100 | bus_LV_2465-1_1_5_node_424 | 0.4 | n |  | TRUE
101 | bus_LV_2465-1_1_5_node_447 | 0.4 | n |  | TRUE
102 | bus_LV_2465-1_1_5_node_426 | 0.4 | n |  | TRUE
103 | bus_LV_2465-1_1_5_node_428 | 0.4 | n |  | TRUE
104 | bus_LV_2465-1_1_5_node_429 | 0.4 | n |  | TRUE
105 | bus_LV_2465-1_1_5_node_430 | 0.4 | n |  | TRUE
106 | bus_LV_2465-1_1_5_node_431 | 0.4 | n |  | TRUE
107 | bus_LV_2465-1_1_5_node_441 | 0.4 | n |  | TRUE
108 | bus_LV_2465-1_1_5_node_461 | 0.4 | n |  | TRUE
109 | bus_LV_2465-1_1_5_node_435 | 0.4 | n |  | TRUE
110 | bus_LV_2465-1_1_5_node_473 | 0.4 | n |  | TRUE
111 | bus_LV_2465-1_1_5_node_437 | 0.4 | n |  | TRUE
112 | bus_LV_2465-1_1_5_node_438 | 0.4 | n |  | TRUE
113 | bus_LV_2465-1_1_5_node_439 | 0.4 | n |  | TRUE
114 | bus_LV_2465-1_1_5_node_443 | 0.4 | n |  | TRUE
115 | bus_LV_2465-1_1_5_node_444 | 0.4 | n |  | TRUE
116 | bus_LV_2465-1_1_5_node_445 | 0.4 | n |  | TRUE
117 | bus_LV_2465-1_1_5_node_452 | 0.4 | n |  | TRUE
118 | bus_LV_2465-1_1_5_node_450 | 0.4 | n |  | TRUE
119 | bus_LV_2465-1_1_5_node_471 | 0.4 | n |  | TRUE
120 | bus_LV_2465-1_1_5_node_458 | 0.4 | n |  | TRUE
121 | bus_LV_2465-1_1_5_node_455 | 0.4 | n |  | TRUE
122 | bus_LV_2465-1_1_5_node_456 | 0.4 | n |  | TRUE
123 | bus_LV_2465-1_1_5_node_457 | 0.4 | n |  | TRUE
124 | bus_LV_2465-1_1_5_node_477 | 0.4 | n |  | TRUE
125 | bus_LV_2465-1_1_5_node_459 | 0.4 | n |  | TRUE
126 | bus_LV_2465-1_1_5_node_460 | 0.4 | n |  | TRUE
127 | bus_LV_2465-1_1_5_node_472 | 0.4 | n |  | TRUE
128 | bus_LV_2465-1_1_5_node_469 | 0.4 | n |  | TRUE
129 | bus_LV_2465-1_1_5_node_470 | 0.4 | n |  | TRUE
130 | bus_LV_2465-1_1_5_node_478 | 0.4 | n |  | TRUE
131 | bus_LV_2465-1_1_5_node_474 | 0.4 | n |  | TRUE
132 | bus_LV_2465-1_1_5_node_479 | 0.4 | n |  | TRUE
133 | bus_LV_2465-1_1_5_node_491 | 0.4 | n |  | TRUE
134 | bus_LV_2465-1_1_5_node_492 | 0.4 | n |  | TRUE
135 | bus_LV_2465-1_1_5_node_493 | 0.4 | n |  | TRUE
136 | bus_MV_387_2_node_206 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2465-1_1_5_load_416 | 1 | 0.00068891 | 0.00017266 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2465-1_1_5_load_413 | 2 | 0.0020402 | 0.00051132 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2465-1_1_5_load_347 | 3 | 0.0033858 | 0.00084857 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2465-1_1_5_load_350 | 6 | 0.0020255 | 0.00050763 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2465-1_1_5_load_353 | 8 | 0.0071473 | 0.0017913 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2465-1_1_5_load_354 | 9 | 0.0035855 | 0.00089861 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2465-1_1_5_load_400 | 10 | 0.0034643 | 0.00086824 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2465-1_1_5_load_367 | 12 | 0.00043142 | 0.00010812 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2465-1_1_5_load_466 | 13 | 0.00031287 | 7.8413e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2465-1_1_5_load_359 | 14 | 0.00043433 | 0.00010885 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2465-1_1_5_load_449 | 15 | 0.0022284 | 0.00055848 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2465-1_1_5_load_355 | 17 | 0.0002847 | 7.1353e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2465-1_1_5_load_356 | 18 | 0.00030189 | 7.566e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2465-1_1_5_load_358 | 20 | 0.0007032 | 0.00017624 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2465-1_1_5_load_369 | 22 | 0.00038019 | 9.5285e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2465-1_1_5_load_502 | 24 | 0.0016488 | 0.00041323 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2465-1_1_5_load_467 | 26 | 0.0011177 | 0.00028011 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2465-1_1_5_load_362 | 27 | 0.00056295 | 0.00014109 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2465-1_1_5_load_365 | 28 | 0.00086325 | 0.00021635 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2465-1_1_5_load_409 | 29 | 0.00098291 | 0.00024634 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2465-1_1_5_load_368 | 30 | 0.0017727 | 0.00044428 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2465-1_1_5_load_370 | 31 | 0.0014713 | 0.00036875 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2465-1_1_5_load_371 | 32 | 0.00030436 | 7.628e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2465-1_1_5_load_454 | 33 | 0.0024108 | 0.00060421 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2465-1_1_5_load_372 | 34 | 0.00050151 | 0.00012569 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2465-1_1_5_load_373 | 35 | 0.00091118 | 0.00022836 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2465-1_1_5_load_375 | 37 | 0.009601 | 0.0024062 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2465-1_1_5_load_376 | 38 | 0.00058001 | 0.00014536 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2465-1_1_5_load_377 | 39 | 0.0011375 | 0.00028509 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2465-1_1_5_load_448 | 40 | 0.0011729 | 0.00029396 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2465-1_1_5_load_423 | 41 | 0.000144 | 3.6089e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2465-1_1_5_load_378 | 43 | 0.0013872 | 0.00034766 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2465-1_1_5_load_379 | 44 | 0.001692 | 0.00042406 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2465-1_1_5_load_380 | 45 | 0.0018882 | 0.00047324 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2465-1_1_5_load_381 | 46 | 0.0017488 | 0.0004383 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2465-1_1_5_load_382 | 47 | 0.0021487 | 0.00053852 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2465-1_1_5_load_425 | 48 | 0.001325 | 0.00033208 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2465-1_1_5_load_383 | 50 | 0.0006449 | 0.00016163 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2465-1_1_5_load_388 | 53 | 0.0017348 | 0.00043477 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2465-1_1_5_load_451 | 54 | 0.0011087 | 0.00027787 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2465-1_1_5_load_468 | 55 | 0.00039063 | 9.7901e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2465-1_1_5_load_389 | 56 | 0.00119 | 0.00029823 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2465-1_1_5_load_390 | 57 | 0.0029659 | 0.00074333 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2465-1_1_5_load_392 | 58 | 0.00038686 | 9.6955e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2465-1_1_5_load_442 | 61 | 0.00026752 | 6.7047e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2465-1_1_5_load_481 | 62 | 0.001322 | 0.00033132 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2465-1_1_5_load_395 | 63 | 0.00066188 | 0.00016588 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2465-1_1_5_load_396 | 64 | 0.0018038 | 0.00045206 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2465-1_1_5_load_397 | 65 | 0.0019884 | 0.00049835 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2465-1_1_5_load_453 | 68 | 0.0017061 | 0.00042758 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2465-1_1_5_load_401 | 69 | 0.0032526 | 0.00081518 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2465-1_1_5_load_404 | 72 | 0.0019068 | 0.00047788 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2465-1_1_5_load_405 | 73 | 0.0005975 | 0.00014975 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2465-1_1_5_load_406 | 74 | 0.00099262 | 0.00024878 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2465-1_1_5_load_407 | 75 | 0.0020702 | 0.00051885 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2465-1_1_5_load_476 | 77 | 0.00033937 | 8.5055e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2465-1_1_5_load_482 | 78 | 0.00058281 | 0.00014607 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2465-1_1_5_load_436 | 79 | 0.001237 | 0.00031002 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2465-1_1_5_load_480 | 80 | 0.0021175 | 0.0005307 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2465-1_1_5_load_490 | 81 | 0.0004221 | 0.00010579 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2465-1_1_5_load_462 | 82 | 0.00042566 | 0.00010668 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2465-1_1_5_load_411 | 84 | 0.0011364 | 0.00028482 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2465-1_1_5_load_412 | 85 | 0.00091516 | 0.00022936 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2465-1_1_5_load_433 | 86 | 0.0025123 | 0.00062964 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2465-1_1_5_load_494 | 87 | 0.00028247 | 7.0793e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2465-1_1_5_load_414 | 88 | 0.0016508 | 0.00041374 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2465-1_1_5_load_415 | 89 | 0.00036197 | 9.0719e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2465-1_1_5_load_432 | 91 | 0.00093974 | 0.00023552 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2465-1_1_5_load_418 | 93 | 0.0033239 | 0.00083304 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2465-1_1_5_load_419 | 94 | 0.0022352 | 0.00056019 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2465-1_1_5_load_420 | 95 | 0.0025725 | 0.00064473 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2465-1_1_5_load_421 | 96 | 0.0021492 | 0.00053865 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2465-1_1_5_load_422 | 97 | 0.0012541 | 0.0003143 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2465-1_1_5_load_463 | 99 | 0.0047296 | 0.0011853 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2465-1_1_5_load_424 | 100 | 0.00048826 | 0.00012237 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2465-1_1_5_load_447 | 101 | 0.006025 | 0.00151 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2465-1_1_5_load_426 | 102 | 0.0005048 | 0.00012651 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2465-1_1_5_load_429 | 104 | 0.0015416 | 0.00038637 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2465-1_1_5_load_430 | 105 | 0.00059076 | 0.00014806 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2465-1_1_5_load_431 | 106 | 0.00053364 | 0.00013374 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2465-1_1_5_load_441 | 107 | 0.00079787 | 0.00019996 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2465-1_1_5_load_461 | 108 | 0.0016715 | 0.00041892 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2465-1_1_5_load_435 | 109 | 0.00042139 | 0.00010561 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2465-1_1_5_load_473 | 110 | 0.0012992 | 0.0003256 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2465-1_1_5_load_437 | 111 | 0.00087842 | 0.00022015 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2465-1_1_5_load_438 | 112 | 0.0036004 | 0.00090234 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2465-1_1_5_load_439 | 113 | 0.0021867 | 0.00054803 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2465-1_1_5_load_443 | 114 | 0.0013755 | 0.00034474 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2465-1_1_5_load_452 | 117 | 0.00054395 | 0.00013633 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2465-1_1_5_load_450 | 118 | 0.0016847 | 0.00042222 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2465-1_1_5_load_471 | 119 | 0.0012106 | 0.00030341 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2465-1_1_5_load_458 | 120 | 0.0018901 | 0.0004737 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2465-1_1_5_load_455 | 121 | 0.0015988 | 0.00040069 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2465-1_1_5_load_456 | 122 | 0.00147 | 0.00036841 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2465-1_1_5_load_457 | 123 | 0.0014301 | 0.00035841 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2465-1_1_5_load_459 | 125 | 0.0026419 | 0.00066212 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2465-1_1_5_load_460 | 126 | 0.0011794 | 0.0002956 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2465-1_1_5_load_472 | 127 | 0.0021981 | 0.00055088 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2465-1_1_5_load_469 | 128 | 0.0019741 | 0.00049475 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2465-1_1_5_load_470 | 129 | 0.0023778 | 0.00059594 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2465-1_1_5_load_478 | 130 | 0.0029162 | 0.00073087 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2465-1_1_5_load_474 | 131 | 0.0008948 | 0.00022426 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2465-1_1_5_load_479 | 132 | 0.0023269 | 0.00058317 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2465-1_1_5_load_491 | 133 | 0.0011805 | 0.00029587 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2465-1_1_5_load_492 | 134 | 0.00040985 | 0.00010272 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2465-1_1_5_load_493 | 135 | 0.002136 | 0.00053533 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 67 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2465-1_1_5_line_0 |  | 0 | 1 | 0.042073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2465-1_1_5_line_1 |  | 0 | 2 | 0.028723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2465-1_1_5_line_2 |  | 1 | 91 | 0.010468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2465-1_1_5_line_3 |  | 2 | 88 | 0.029065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2465-1_1_5_line_4 |  | 3 | 4 | 0.015364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2465-1_1_5_line_5 |  | 3 | 5 | 0.010798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2465-1_1_5_line_6 |  | 4 | 6 | 0.02189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2465-1_1_5_line_7 |  | 4 | 7 | 0.031078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2465-1_1_5_line_8 |  | 5 | 8 | 0.022977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2465-1_1_5_line_9 |  | 5 | 9 | 0.019861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2465-1_1_5_line_10 |  | 6 | 10 | 0.021941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2465-1_1_5_line_11 |  | 7 | 11 | 0.03522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_2465-1_1_5_line_12 |  | 7 | 12 | 0.0099781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2465-1_1_5_line_13 |  | 8 | 15 | 0.016339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2465-1_1_5_line_14 |  | 9 | 16 | 0.013131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2465-1_1_5_line_15 |  | 11 | 13 | 0.014313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2465-1_1_5_line_16 |  | 11 | 14 | 0.019871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2465-1_1_5_line_17 |  | 12 | 25 | 0.0050538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2465-1_1_5_line_18 |  | 13 | 77 | 0.014916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_2465-1_1_5_line_19 |  | 14 | 19 | 0.0029478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2465-1_1_5_line_20 |  | 15 | 40 | 0.010732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2465-1_1_5_line_21 |  | 16 | 109 | 0.057094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2465-1_1_5_line_22 |  | 16 | 86 | 0.025153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2465-1_1_5_line_23 |  | 17 | 18 | 0.020045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2465-1_1_5_line_24 |  | 17 | 19 | 0.015845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2465-1_1_5_line_25 |  | 18 | 20 | 0.053224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2465-1_1_5_line_26 |  | 19 | 21 | 0.017462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2465-1_1_5_line_27 |  | 20 | 22 | 0.0021041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2465-1_1_5_line_28 |  | 21 | 26 | 0.0014094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2465-1_1_5_line_29 |  | 22 | 30 | 0.024301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2465-1_1_5_line_30 |  | 23 | 24 | 0.010365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2465-1_1_5_line_31 |  | 23 | 25 | 0.017307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2465-1_1_5_line_32 |  | 25 | 27 | 0.032125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2465-1_1_5_line_33 |  | 28 | 29 | 0.0019184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2465-1_1_5_line_34 |  | 29 | 83 | 0.01696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2465-1_1_5_line_35 |  | 30 | 31 | 0.0037822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2465-1_1_5_line_36 |  | 31 | 32 | 0.014264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2465-1_1_5_line_37 |  | 32 | 33 | 0.036213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2465-1_1_5_line_38 |  | 34 | 35 | 0.019466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2465-1_1_5_line_39 |  | 34 | 36 | 0.017831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2465-1_1_5_line_40 |  | 35 | 37 | 0.0015457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2465-1_1_5_line_41 |  | 36 | 38 | 0.015492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2465-1_1_5_line_42 |  | 36 | 39 | 0.019372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2465-1_1_5_line_43 |  | 37 | 40 | 0.014778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2465-1_1_5_line_44 |  | 38 | 41 | 0.011607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2465-1_1_5_line_45 |  | 39 | 42 | 0.010612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_2465-1_1_5_line_46 |  | 41 | 100 | 0.0023638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2465-1_1_5_line_47 |  | 42 | 53 | 0.019293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2465-1_1_5_line_48 |  | 42 | 50 | 0.035845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_2465-1_1_5_line_49 |  | 43 | 44 | 0.011144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2465-1_1_5_line_50 |  | 43 | 45 | 0.009965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2465-1_1_5_line_51 |  | 44 | 46 | 0.004129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2465-1_1_5_line_52 |  | 45 | 47 | 0.016695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2465-1_1_5_line_53 |  | 46 | 48 | 0.0097524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2465-1_1_5_line_54 |  | 47 | 49 | 0.021042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2465-1_1_5_line_55 |  | 48 | 101 | 0.01522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2465-1_1_5_line_56 |  | 49 | 67 | 0.055191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_2465-1_1_5_line_57 |  | 49 | 64 | 0.020521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2465-1_1_5_line_58 |  | 50 | 51 | 0.017011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_2465-1_1_5_line_59 |  | 51 | 52 | 0.009143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_2465-1_1_5_line_60 |  | 52 | 54 | 0.099043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_2465-1_1_5_line_61 |  | 53 | 55 | 0.014991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2465-1_1_5_line_62 |  | 54 | 118 | 0.011087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2465-1_1_5_line_63 |  | 56 | 57 | 0.028479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2465-1_1_5_line_64 |  | 57 | 58 | 0.031081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2465-1_1_5_line_65 |  | 58 | 59 | 0.034089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2465-1_1_5_line_66 |  | 59 | 104 | 0.1453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2465-1_1_5_line_67 |  | 59 | 102 | 0.0068006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2465-1_1_5_line_68 |  | 60 | 61 | 0.021977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2465-1_1_5_line_69 |  | 60 | 62 | 0.036291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2465-1_1_5_line_70 |  | 61 | 107 | 0.012523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2465-1_1_5_line_71 |  | 63 | 64 | 0.011448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_2465-1_1_5_line_72 |  | 63 | 65 | 0.020733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_2465-1_1_5_line_73 |  | 65 | 66 | 0.0067081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_2465-1_1_5_line_74 |  | 66 | 68 | 0.026425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_2465-1_1_5_line_75 |  | 67 | 128 | 0.34289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2465-1_1_5_line_76 |  | 68 | 105 | 0.037724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_2465-1_1_5_line_77 |  | 69 | 70 | 0.038905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_2465-1_1_5_line_78 |  | 69 | 71 | 0.017201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_2465-1_1_5_line_79 |  | 70 | 72 | 0.013632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_2465-1_1_5_line_80 |  | 70 | 73 | 0.03571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2465-1_1_5_line_81 |  | 71 | 74 | 0.027999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2465-1_1_5_line_82 |  | 71 | 75 | 0.014639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2465-1_1_5_line_83 |  | 71 | 76 | 0.041111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_2465-1_1_5_line_84 |  | 72 | 77 | 0.012654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_2465-1_1_5_line_85 |  | 73 | 78 | 0.015447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2465-1_1_5_line_86 |  | 74 | 79 | 0.0063181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2465-1_1_5_line_87 |  | 75 | 80 | 0.0254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2465-1_1_5_line_88 |  | 76 | 81 | 0.020378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2465-1_1_5_line_89 |  | 76 | 82 | 0.019302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2465-1_1_5_line_90 |  | 81 | 133 | 0.04925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2465-1_1_5_line_91 |  | 82 | 108 | 0.027841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_2465-1_1_5_line_92 |  | 83 | 84 | 0.0049901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2465-1_1_5_line_93 |  | 83 | 85 | 0.023207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2465-1_1_5_line_94 |  | 84 | 86 | 0.015641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2465-1_1_5_line_95 |  | 85 | 87 | 0.0096801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2465-1_1_5_line_96 |  | 88 | 89 | 9.1298e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2465-1_1_5_line_97 |  | 89 | 90 | 0.021585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2465-1_1_5_line_98 |  | 90 | 92 | 0.021472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2465-1_1_5_line_99 |  | 92 | 99 | 0.036718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2465-1_1_5_line_100 |  | 92 | 113 | 0.020014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2465-1_1_5_line_101 |  | 93 | 94 | 0.012035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2465-1_1_5_line_102 |  | 93 | 95 | 0.016444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2465-1_1_5_line_103 |  | 94 | 96 | 0.023157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2465-1_1_5_line_104 |  | 95 | 97 | 0.016316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2465-1_1_5_line_105 |  | 96 | 98 | 0.015488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2465-1_1_5_line_106 |  | 97 | 99 | 0.035922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2465-1_1_5_line_107 |  | 98 | 119 | 0.029796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2465-1_1_5_line_108 |  | 98 | 115 | 0.041006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2465-1_1_5_line_109 |  | 102 | 103 | 0.031324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2465-1_1_5_line_110 |  | 103 | 105 | 0.02072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_2465-1_1_5_line_111 |  | 103 | 106 | 0.02482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_2465-1_1_5_line_112 |  | 104 | 107 | 0.02284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2465-1_1_5_line_113 |  | 106 | 108 | 0.026733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_2465-1_1_5_line_114 |  | 109 | 110 | 0.012255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2465-1_1_5_line_115 |  | 110 | 131 | 0.013412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2465-1_1_5_line_116 |  | 111 | 112 | 0.013537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2465-1_1_5_line_117 |  | 112 | 113 | 0.018383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2465-1_1_5_line_118 |  | 114 | 115 | 0.02154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2465-1_1_5_line_119 |  | 115 | 116 | 0.009449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2465-1_1_5_line_120 |  | 116 | 117 | 0.018118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2465-1_1_5_line_121 |  | 116 | 118 | 0.041873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2465-1_1_5_line_122 |  | 117 | 120 | 0.00083776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2465-1_1_5_line_123 |  | 119 | 129 | 0.041619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2465-1_1_5_line_124 |  | 120 | 125 | 0.018111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2465-1_1_5_line_125 |  | 121 | 122 | 0.004912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2465-1_1_5_line_126 |  | 122 | 123 | 0.021457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2465-1_1_5_line_127 |  | 123 | 124 | 0.030528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2465-1_1_5_line_128 |  | 124 | 130 | 0.01744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2465-1_1_5_line_129 |  | 124 | 132 | 0.056358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2465-1_1_5_line_130 |  | 125 | 126 | 0.011814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2465-1_1_5_line_131 |  | 126 | 127 | 0.015631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2465-1_1_5_line_132 |  | 127 | 130 | 0.016772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2465-1_1_5_line_133 |  | 133 | 134 | 0.00012113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2465-1_1_5_line_134 |  | 134 | 135 | 0.019161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2465-1_1_5_trafo_465 | 0.63 MVA 20/0.4 kV | 136 | 67 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2604974.2727 | 1221147.2474 | 2604964.3758 | 1221106.3555
1 | 2604974.2727 | 1221147.2474 | 2604946.6419 | 1221155.0927
2 | 2604964.3758 | 1221106.3555 | 2604964.097 | 1221105.2037 | 2604962.4883 | 1221096.0609
3 | 2604946.6419 | 1221155.0927 | 2604918.6819 | 1221163.0315
4 | 2604311.0386 | 1221253.3992 | 2604322.9462 | 1221243.6905
5 | 2604332.3796 | 1221238.5281 | 2604324.5942 | 1221242.3469 | 2604322.9462 | 1221243.6905
6 | 2604311.0386 | 1221253.3992 | 2604327.7237 | 1221267.5695
7 | 2604287.7426 | 1221265.4562 | 2604292.1998 | 1221269.6952 | 2604305.1102 | 1221259.1094 | 2604311.0386 | 1221253.3992
8 | 2604332.3796 | 1221238.5281 | 2604341.1275 | 1221236.0551 | 2604350.4055 | 1221234.7722 | 2604354.8928 | 1221234.2311
9 | 2604332.3796 | 1221238.5281 | 2604333.1031 | 1221234.5041 | 2604333.3021 | 1221232.1028 | 2604333.7974 | 1221229.0014 | 2604334.901 | 1221223.7992 | 2604335.8973 | 1221220.1978 | 2604336.2998 | 1221219.1018
10 | 2604344.4475 | 1221281.7727 | 2604327.7237 | 1221267.5695
11 | 2604267.7942 | 1221284.8644 | 2604270.4571 | 1221284.3104 | 2604277.4988 | 1221280.9802 | 2604284.7616 | 1221276.0269 | 2604292.1998 | 1221269.6952 | 2604287.7426 | 1221265.4562
12 | 2604287.7426 | 1221265.4562 | 2604285.9991 | 1221263.7985 | 2604280.1795 | 1221258.9538
13 | 2604354.8928 | 1221234.2311 | 2604358.2876 | 1221233.8217 | 2604367.4289 | 1221232.7388 | 2604371.1187 | 1221232.31
14 | 2604341.3987 | 1221207.0053 | 2604338.3975 | 1221213.7959 | 2604336.9993 | 1221217.1969 | 2604336.2998 | 1221219.1018
15 | 2604267.7942 | 1221284.8644 | 2604267.9238 | 1221294.7035 | 2604268.8195 | 1221299.0862
16 | 2604267.7942 | 1221284.8644 | 2604260.4059 | 1221285.026 | 2604247.9686 | 1221283.983
17 | 2604276.2954 | 1221255.7203 | 2604280.1795 | 1221258.9538
18 | 2604274.1238 | 1221312.9754 | 2604269.4055 | 1221301.9532 | 2604268.8195 | 1221299.0862
19 | 2604245.0311 | 1221283.7367 | 2604247.9686 | 1221283.983
20 | 2604381.7955 | 1221231.2321 | 2604376.1757 | 1221231.7223 | 2604371.1187 | 1221232.31
21 | 2604341.3987 | 1221207.0053 | 2604343.1002 | 1221203.7046 | 2604346.2981 | 1221197.6034 | 2604347.7033 | 1221195.0029 | 2604349.1007 | 1221192.7026 | 2604356.3989 | 1221180.901 | 2604364.6008 | 1221167.8995 | 2604370.8223 | 1221158.1133
22 | 2604341.3987 | 1221207.0053 | 2604341.2856 | 1221195.3874 | 2604337.522 | 1221186.4351 | 2604333.8394 | 1221185.4088
23 | 2604229.2095 | 1221283.0701 | 2604209.1653 | 1221283.245
24 | 2604245.0311 | 1221283.7367 | 2604242.5887 | 1221283.5348 | 2604233.9796 | 1221283.0285 | 2604229.2095 | 1221283.0701
25 | 2604155.9828 | 1221284.8897 | 2604162.9637 | 1221284.2689 | 2604171.7782 | 1221283.9081 | 2604180.8202 | 1221283.6808 | 2604198.5704 | 1221283.3374 | 2604209.1653 | 1221283.245
26 | 2604245.0311 | 1221283.7367 | 2604243.8659 | 1221279.5112 | 2604244.4885 | 1221278.6667 | 2604248.0236 | 1221278.1911 | 2604248.4191 | 1221276.7461 | 2604248.5104 | 1221276.4127 | 2604250.1987 | 1221270.1992 | 2604250.3731 | 1221270.2438
27 | 2604153.8894 | 1221285.0956 | 2604154.1564 | 1221285.0522 | 2604155.9828 | 1221284.8897
28 | 2604250.3731 | 1221270.2438 | 2604251.7328 | 1221270.6149
29 | 2604129.9175 | 1221289.08 | 2604137.33 | 1221287.7867 | 2604153.8894 | 1221285.0956
30 | 2604259.1596 | 1221255.8639 | 2604256.9833 | 1221254.884 | 2604254.5501 | 1221252.4587 | 2604251.0248 | 1221249.5656
31 | 2604259.1596 | 1221255.8639 | 2604260.8279 | 1221256.6099 | 2604267.101 | 1221256.77 | 2604276.2954 | 1221255.7203
32 | 2604276.2954 | 1221255.7203 | 2604274.7034 | 1221254.3962 | 2604273.9001 | 1221253.3061 | 2604266.2969 | 1221235.3015 | 2604261.2326 | 1221227.6736
33 | 2604297.5603 | 1221175.5677 | 2604296.5375 | 1221175.2995 | 2604295.6792 | 1221175.368
34 | 2604313.9659 | 1221179.87 | 2604297.5603 | 1221175.5677
35 | 2604129.9175 | 1221289.08 | 2604128.3174 | 1221289.3592 | 2604126.2002 | 1221289.7765
36 | 2604126.2002 | 1221289.7765 | 2604112.2055 | 1221292.5346
37 | 2604077.1578 | 1221301.6083 | 2604085.5517 | 1221299.1025 | 2604091.4011 | 1221297.6056 | 2604102.1819 | 1221294.8557 | 2604111.4527 | 1221292.683 | 2604112.2055 | 1221292.5346
38 | 2604417.5677 | 1221230.7659 | 2604412.0105 | 1221230.7033 | 2604402.7713 | 1221230.6855 | 2604398.1024 | 1221230.6821
39 | 2604435.3966 | 1221230.776 | 2604429.9653 | 1221230.9055 | 2604417.5677 | 1221230.7659
40 | 2604396.5568 | 1221230.681 | 2604398.1024 | 1221230.6821
41 | 2604435.3966 | 1221230.776 | 2604438.6345 | 1221215.6262
42 | 2604435.3966 | 1221230.776 | 2604448.8453 | 1221231.3084 | 2604454.7486 | 1221231.6459
43 | 2604381.7955 | 1221231.2321 | 2604385.15 | 1221230.9395 | 2604394.2224 | 1221230.6793 | 2604396.5568 | 1221230.681
44 | 2604438.6345 | 1221215.6262 | 2604441.0604 | 1221204.2755
45 | 2604465.3355 | 1221232.3768 | 2604457.1208 | 1221231.7815 | 2604454.7486 | 1221231.6459
46 | 2604441.5544 | 1221201.964 | 2604441.0604 | 1221204.2755
47 | 2604465.3355 | 1221232.3768 | 2604465.5239 | 1221251.6683
48 | 2604465.3355 | 1221232.3768 | 2604491.9671 | 1221233.9196 | 2604501.1163 | 1221234.5143
49 | 2604439.9102 | 1221340.1546 | 2604429.6326 | 1221335.8462
50 | 2604439.9102 | 1221340.1546 | 2604449.1003 | 1221344.0072
51 | 2604429.6326 | 1221335.8462 | 2604425.8247 | 1221334.2498
52 | 2604464.4967 | 1221350.4615 | 2604449.1003 | 1221344.0072
53 | 2604425.8247 | 1221334.2498 | 2604416.8307 | 1221330.4794
54 | 2604483.9022 | 1221358.5965 | 2604464.4967 | 1221350.4615
55 | 2604402.794 | 1221324.5951 | 2604416.8307 | 1221330.4794
56 | 2604483.9022 | 1221358.5965 | 2604503.3896 | 1221306.9479
57 | 2604483.9022 | 1221358.5965 | 2604477.0557 | 1221377.9422
58 | 2604518.098 | 1221235.5177 | 2604510.217 | 1221235.0894 | 2604501.1375 | 1221234.5156 | 2604501.1163 | 1221234.5143
59 | 2604518.098 | 1221235.5177 | 2604527.238 | 1221236.2583
60 | 2604527.238 | 1221236.2583 | 2604535.8169 | 1221236.6205 | 2604544.2289 | 1221237.1605 | 2604553.3994 | 1221237.6677 | 2604562.5472 | 1221238.0637 | 2604571.2854 | 1221238.4705 | 2604580.2665 | 1221238.6774 | 2604589.1035 | 1221238.7842 | 2604598.0469 | 1221238.6909 | 2604607.2939 | 1221238.3311 | 2604616.6322 | 1221237.7157 | 2604625.7431 | 1221236.8221 | 2604626.1459 | 1221236.7686
61 | 2604465.5239 | 1221251.6683 | 2604465.5964 | 1221259.0923 | 2604465.9823 | 1221266.6488
62 | 2604637.1146 | 1221235.1706 | 2604634.6494 | 1221235.6394 | 2604626.1459 | 1221236.7686
63 | 2604491.1039 | 1221582.8073 | 2604469.5142 | 1221564.2355
64 | 2604446.7398 | 1221543.1283 | 2604450.0999 | 1221546.7021 | 2604456.1029 | 1221552.6989 | 2604469.5142 | 1221564.2355
65 | 2604422.5025 | 1221519.2994 | 2604424.7998 | 1221520.7019 | 2604429.5982 | 1221524.8967 | 2604446.7398 | 1221543.1283
66 | 2604422.5025 | 1221519.2994 | 2604419.4027 | 1221526.3012 | 2604377.8019 | 1221573.4982 | 2604350.0004 | 1221608.1981 | 2604339.8023 | 1221623.9999 | 2604332.9687 | 1221633.1962
67 | 2604422.5025 | 1221519.2994 | 2604422.697 | 1221512.6958 | 2604422.6415 | 1221512.5098
68 | 2604321.4999 | 1221687.4011 | 2604321.283 | 1221665.425
69 | 2604321.4999 | 1221687.4011 | 2604308.0994 | 1221684.401 | 2604286.6269 | 1221677.4835
70 | 2604321.8824 | 1221652.9631 | 2604321.7974 | 1221653.2039 | 2604321.4014 | 1221655.4048 | 2604321.2028 | 1221657.3058 | 2604321.283 | 1221665.425
71 | 2604473.2365 | 1221388.7339 | 2604477.0557 | 1221377.9422
72 | 2604473.2365 | 1221388.7339 | 2604470.8509 | 1221395.4748 | 2604465.4645 | 1221407.9437
73 | 2604462.8043 | 1221414.1018 | 2604465.4645 | 1221407.9437
74 | 2604462.8043 | 1221414.1018 | 2604456.4024 | 1221424.2029 | 2604448.0329 | 1221436.002
75 | 2604503.3896 | 1221306.9479 | 2604563.5999 | 1221330.6956 | 2604576.747 | 1221338.5879 | 2604709.1019 | 1221429.3974 | 2604752.3982 | 1221458.8038 | 2604793.6023 | 1221486.0965 | 2604794.011 | 1221486.4799
76 | 2604426.1615 | 1221466.7388 | 2604430.2973 | 1221461.0049 | 2604448.0329 | 1221436.002
77 | 2604284.468 | 1221337.1396 | 2604290.2018 | 1221348.806 | 2604294.8013 | 1221355.7021 | 2604302.6992 | 1221364.1014 | 2604307.3657 | 1221368.0103
78 | 2604318.1687 | 1221381.2112 | 2604315.9036 | 1221377.0961 | 2604310.0981 | 1221370.2992 | 2604307.3657 | 1221368.0103
79 | 2604284.468 | 1221337.1396 | 2604279.1035 | 1221324.608
80 | 2604284.468 | 1221337.1396 | 2604274.528 | 1221352.2413 | 2604268.2441 | 1221356.8395 | 2604262.493 | 1221358.8811 | 2604258.7542 | 1221358.7398
81 | 2604318.1687 | 1221381.2112 | 2604310.5606 | 1221391.8341 | 2604303.139 | 1221396.3425 | 2604297.1698 | 1221394.495
82 | 2604318.1687 | 1221381.2112 | 2604327.4496 | 1221369.8904
83 | 2604343.2985 | 1221413.5033 | 2604332.9975 | 1221403.1011 | 2604326.0024 | 1221394.5022 | 2604318.1687 | 1221381.2112
84 | 2604274.1238 | 1221312.9754 | 2604279.1035 | 1221324.608
85 | 2604244.3141 | 1221354.3101 | 2604252.6019 | 1221358.5073 | 2604258.7542 | 1221358.7398
86 | 2604297.1698 | 1221394.495 | 2604291.1342 | 1221392.6268
87 | 2604340.9786 | 1221348.3975 | 2604327.7422 | 1221369.5335 | 2604327.4496 | 1221369.8904
88 | 2604343.2985 | 1221413.5033 | 2604346.0024 | 1221408.6025 | 2604355.8723 | 1221397.6006
89 | 2604343.2985 | 1221413.5033 | 2604357.3876 | 1221426.6969
90 | 2604355.8723 | 1221397.6006 | 2604373.9008 | 1221377.5046 | 2604377.4362 | 1221376.6289 | 2604381.3646 | 1221377.7213 | 2604392.1286 | 1221387.4844
91 | 2604377.7096 | 1221445.7272 | 2604357.3876 | 1221426.6969
92 | 2604313.9659 | 1221179.87 | 2604318.7729 | 1221181.2097
93 | 2604313.9659 | 1221179.87 | 2604320.3613 | 1221157.6285 | 2604320.3984 | 1221157.5766
94 | 2604333.8394 | 1221185.4088 | 2604318.7729 | 1221181.2097
95 | 2604326.0334 | 1221149.7057 | 2604320.3984 | 1221157.5766
96 | 2604918.6819 | 1221163.0315 | 2604918.5941 | 1221163.0565
97 | 2604897.9509 | 1221169.3533 | 2604910.5159 | 1221165.3501 | 2604918.5941 | 1221163.0565
98 | 2604877.1694 | 1221174.9842 | 2604897.9509 | 1221169.3533
99 | 2604877.1694 | 1221174.9842 | 2604841.9424 | 1221185.343
100 | 2604877.1694 | 1221174.9842 | 2604873.6041 | 1221165.6982 | 2604870.0305 | 1221156.2868
101 | 2604774.594 | 1221198.0624 | 2604762.6406 | 1221199.4566
102 | 2604774.594 | 1221198.0624 | 2604790.9271 | 1221196.1574
103 | 2604762.6406 | 1221199.4566 | 2604742.3296 | 1221201.8256 | 2604739.6988 | 1221202.4672
104 | 2604807.0718 | 1221193.9052 | 2604803.6797 | 1221194.67 | 2604790.9271 | 1221196.1574
105 | 2604724.6518 | 1221206.1365 | 2604739.6988 | 1221202.4672
106 | 2604841.9424 | 1221185.343 | 2604831.7362 | 1221188.3443 | 2604807.0718 | 1221193.9052
107 | 2604724.6518 | 1221206.1365 | 2604726.3993 | 1221192.8969 | 2604733.9873 | 1221178.311
108 | 2604724.6518 | 1221206.1365 | 2604686.3332 | 1221221.0263
109 | 2604413.1009 | 1221482.7048 | 2604415.1984 | 1221487.5981 | 2604422.6415 | 1221512.5098
110 | 2604413.1009 | 1221482.7048 | 2604415.0971 | 1221480.9052 | 2604417.6019 | 1221478.6057 | 2604426.1615 | 1221466.7388
111 | 2604413.1009 | 1221482.7048 | 2604411.1015 | 1221478.5009 | 2604409.2983 | 1221475.598 | 2604406.1983 | 1221472.405 | 2604397.2225 | 1221463.9997
112 | 2604332.9687 | 1221633.1962 | 2604326.5006 | 1221641.9007 | 2604322.9982 | 1221649.8028 | 2604321.8824 | 1221652.9631
113 | 2604377.7096 | 1221445.7272 | 2604397.2225 | 1221463.9997
114 | 2604377.3973 | 1221147.7711 | 2604370.8223 | 1221158.1133
115 | 2604377.3973 | 1221147.7711 | 2604379.7969 | 1221143.9967 | 2604384.8375 | 1221136.6136
116 | 2604858.6997 | 1221126.4458 | 2604863.5049 | 1221139.1007
117 | 2604863.5049 | 1221139.1007 | 2604870.0305 | 1221156.2868
118 | 2604686.3332 | 1221221.0263 | 2604668.6566 | 1221224.0589 | 2604665.1053 | 1221224.6797
119 | 2604677.5162 | 1221224.4882 | 2604686.3332 | 1221221.0263
120 | 2604677.5162 | 1221224.4882 | 2604684.4218 | 1221230.6637 | 2604691.7714 | 1221235.6012
121 | 2604677.5162 | 1221224.4882 | 2604667.1515 | 1221228.2045 | 2604659.9587 | 1221230.3447 | 2604652.4097 | 1221232.2622 | 2604637.1146 | 1221235.1706
122 | 2604692.4668 | 1221236.0684 | 2604691.7714 | 1221235.6012
123 | 2604747.6546 | 1221139.3324 | 2604747.2999 | 1221141.606 | 2604744.5972 | 1221154.0999 | 2604742.8019 | 1221160.6023 | 2604740.5982 | 1221165.6034 | 2604733.9873 | 1221178.311
124 | 2604692.4668 | 1221236.0684 | 2604700.8738 | 1221241.7162 | 2604707.0818 | 1221246.7352
125 | 2604784.4557 | 1221305.9088 | 2604781.8294 | 1221301.7579
126 | 2604769.9975 | 1221283.9058 | 2604771.6043 | 1221285.5969 | 2604781.8294 | 1221301.7579
127 | 2604742.7029 | 1221296.3026 | 2604767.1989 | 1221283.4033 | 2604769.9975 | 1221283.9058 | 2604769.9975 | 1221283.9058
128 | 2604742.7029 | 1221296.3026 | 2604734.1575 | 1221281.0995
129 | 2604742.7029 | 1221296.3026 | 2604753.702 | 1221315.4 | 2604756.1037 | 1221319.0039 | 2604762.3025 | 1221326.7021 | 2604775.7379 | 1221341.6585
130 | 2604707.0818 | 1221246.7352 | 2604712.6012 | 1221251.1975 | 2604715.9615 | 1221254.5069
131 | 2604725.8951 | 1221266.5075 | 2604720.34 | 1221258.819 | 2604715.9615 | 1221254.5069
132 | 2604725.8951 | 1221266.5075 | 2604726.1669 | 1221266.8838 | 2604734.1575 | 1221281.0995
133 | 2604392.2183 | 1221387.5658 | 2604392.1286 | 1221387.4844
134 | 2604408.5899 | 1221396.5185 | 2604399.1026 | 1221393.8101 | 2604392.2183 | 1221387.5658

## bus_geodata
| x | y | coords
0 | 2604974.2727 | 1221147.2474
1 | 2604964.3758 | 1221106.3555
2 | 2604946.6419 | 1221155.0927
3 | 2604322.9462 | 1221243.6905
4 | 2604311.0386 | 1221253.3992
5 | 2604332.3796 | 1221238.5281
6 | 2604327.7237 | 1221267.5695
7 | 2604287.7426 | 1221265.4562
8 | 2604354.8928 | 1221234.2311
9 | 2604336.2998 | 1221219.1018
10 | 2604344.4475 | 1221281.7727
11 | 2604267.7942 | 1221284.8644
12 | 2604280.1795 | 1221258.9538
13 | 2604268.8195 | 1221299.0862
14 | 2604247.9686 | 1221283.983
15 | 2604371.1187 | 1221232.31
16 | 2604341.3987 | 1221207.0053
17 | 2604229.2095 | 1221283.0701
18 | 2604209.1653 | 1221283.245
19 | 2604245.0311 | 1221283.7367
20 | 2604155.9828 | 1221284.8897
21 | 2604250.3731 | 1221270.2438
22 | 2604153.8894 | 1221285.0956
23 | 2604259.1597 | 1221255.8639
24 | 2604251.0248 | 1221249.5656
25 | 2604276.2954 | 1221255.7203
26 | 2604251.7328 | 1221270.6149
27 | 2604261.2326 | 1221227.6736
28 | 2604295.6792 | 1221175.368
29 | 2604297.5603 | 1221175.5677
30 | 2604129.9175 | 1221289.08
31 | 2604126.2002 | 1221289.7765
32 | 2604112.2055 | 1221292.5346
33 | 2604077.1578 | 1221301.6083
34 | 2604417.5678 | 1221230.7659
35 | 2604398.1024 | 1221230.6821
36 | 2604435.3966 | 1221230.776
37 | 2604396.5568 | 1221230.681
38 | 2604438.6345 | 1221215.6262
39 | 2604454.7486 | 1221231.6459
40 | 2604381.7955 | 1221231.2321
41 | 2604441.0604 | 1221204.2755
42 | 2604465.3355 | 1221232.3768
43 | 2604439.9102 | 1221340.1546
44 | 2604429.6326 | 1221335.8462
45 | 2604449.1003 | 1221344.0072
46 | 2604425.8247 | 1221334.2498
47 | 2604464.4967 | 1221350.4615
48 | 2604416.8307 | 1221330.4794
49 | 2604483.9022 | 1221358.5965
50 | 2604501.1163 | 1221234.5143
51 | 2604518.098 | 1221235.5177
52 | 2604527.238 | 1221236.2583
53 | 2604465.5239 | 1221251.6683
54 | 2604626.1459 | 1221236.7686
55 | 2604465.9823 | 1221266.6488
56 | 2604491.1039 | 1221582.8073
57 | 2604469.5142 | 1221564.2355
58 | 2604446.7398 | 1221543.1283
59 | 2604422.5025 | 1221519.2994
60 | 2604321.4999 | 1221687.4011
61 | 2604321.283 | 1221665.425
62 | 2604286.6269 | 1221677.4835
63 | 2604473.2365 | 1221388.7339
64 | 2604477.0557 | 1221377.9422
65 | 2604465.4645 | 1221407.9437
66 | 2604462.8043 | 1221414.1018
67 | 2604503.3896 | 1221306.9479
68 | 2604448.0329 | 1221436.002
69 | 2604307.3657 | 1221368.0103
70 | 2604284.468 | 1221337.1396
71 | 2604318.1687 | 1221381.2112
72 | 2604279.1035 | 1221324.608
73 | 2604258.7542 | 1221358.7398
74 | 2604297.1698 | 1221394.495
75 | 2604327.4496 | 1221369.8904
76 | 2604343.2985 | 1221413.5033
77 | 2604274.1238 | 1221312.9754
78 | 2604244.3141 | 1221354.3101
79 | 2604291.1342 | 1221392.6268
80 | 2604340.9786 | 1221348.3975
81 | 2604355.8723 | 1221397.6006
82 | 2604357.3876 | 1221426.6969
83 | 2604313.9659 | 1221179.87
84 | 2604318.7729 | 1221181.2097
85 | 2604320.3984 | 1221157.5766
86 | 2604333.8394 | 1221185.4088
87 | 2604326.0334 | 1221149.7057
88 | 2604918.6819 | 1221163.0315
89 | 2604918.5941 | 1221163.0565
90 | 2604897.9509 | 1221169.3533
91 | 2604962.4883 | 1221096.0609
92 | 2604877.1694 | 1221174.9842
93 | 2604774.594 | 1221198.0624
94 | 2604762.6406 | 1221199.4566
95 | 2604790.9271 | 1221196.1574
96 | 2604739.6988 | 1221202.4672
97 | 2604807.0718 | 1221193.9052
98 | 2604724.6518 | 1221206.1365
99 | 2604841.9424 | 1221185.343
100 | 2604441.5544 | 1221201.964
101 | 2604402.794 | 1221324.5951
102 | 2604422.6415 | 1221512.5098
103 | 2604413.1009 | 1221482.7048
104 | 2604332.9687 | 1221633.1962
105 | 2604426.1615 | 1221466.7388
106 | 2604397.2225 | 1221463.9997
107 | 2604321.8824 | 1221652.9631
108 | 2604377.7096 | 1221445.7272
109 | 2604370.8223 | 1221158.1133
110 | 2604377.3973 | 1221147.7711
111 | 2604858.6997 | 1221126.4458
112 | 2604863.5049 | 1221139.1007
113 | 2604870.0305 | 1221156.2868
114 | 2604665.1053 | 1221224.6797
115 | 2604686.3332 | 1221221.0263
116 | 2604677.5162 | 1221224.4882
117 | 2604691.7714 | 1221235.6012
118 | 2604637.1146 | 1221235.1706
119 | 2604733.9873 | 1221178.311
120 | 2604692.4668 | 1221236.0684
121 | 2604784.4557 | 1221305.9088
122 | 2604781.8294 | 1221301.7579
123 | 2604769.9975 | 1221283.9058
124 | 2604742.7029 | 1221296.3026
125 | 2604707.0818 | 1221246.7352
126 | 2604715.9615 | 1221254.5069
127 | 2604725.8951 | 1221266.5075
128 | 2604794.011 | 1221486.4799
129 | 2604747.6546 | 1221139.3324
130 | 2604734.1575 | 1221281.0995
131 | 2604384.8375 | 1221136.6136
132 | 2604775.7379 | 1221341.6585
133 | 2604392.1286 | 1221387.4844
134 | 2604392.2183 | 1221387.5658
135 | 2604408.5899 | 1221396.5185
136 | 2604483.9022 | 1221358.5965

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97074 | -0.56601 | 0 | 0
1 | 0.97068 | -0.56728 | 0.00068891 | 0.00017266
2 | 0.97079 | -0.56515 | 0.0020402 | 0.00051132
3 | 0.9837 | -0.31212 | 0.0033858 | 0.00084857
4 | 0.98405 | -0.30537 | 0 | 0
5 | 0.98347 | -0.3167 | 0 | 0
6 | 0.98394 | -0.30754 | 0.0020255 | 0.00050763
7 | 0.98479 | -0.29097 | 0 | 0
8 | 0.98303 | -0.32512 | 0.0071473 | 0.0017913
9 | 0.98323 | -0.32132 | 0.0035855 | 0.00089861
10 | 0.98387 | -0.30891 | 0.0034643 | 0.00086824
11 | 0.98565 | -0.27425 | 0 | 0
12 | 0.98477 | -0.29144 | 0.00043142 | 0.00010812
13 | 0.98604 | -0.26688 | 0.00031287 | 7.8413e-05
14 | 0.98549 | -0.27753 | 0.00043433 | 0.00010885
15 | 0.98275 | -0.33059 | 0.0022284 | 0.00055848
16 | 0.98312 | -0.32353 | 0 | 0
17 | 0.98535 | -0.28016 | 0.0002847 | 7.1353e-05
18 | 0.98522 | -0.28281 | 0.00030189 | 7.566e-05
19 | 0.98546 | -0.27799 | 0 | 0
20 | 0.98487 | -0.28954 | 0.0007032 | 0.00017624
21 | 0.98545 | -0.27834 | 0 | 0
22 | 0.98486 | -0.28978 | 0.00038019 | 9.5285e-05
23 | 0.98473 | -0.29216 | 0 | 0
24 | 0.98472 | -0.29246 | 0.0016488 | 0.00041323
25 | 0.98476 | -0.29164 | 0 | 0
26 | 0.98544 | -0.27837 | 0.0011177 | 0.00028011
27 | 0.98474 | -0.29197 | 0.00056295 | 0.00014109
28 | 0.98286 | -0.32861 | 0.00086325 | 0.00021635
29 | 0.98286 | -0.32858 | 0.00098291 | 0.00024634
30 | 0.98473 | -0.29239 | 0.0017727 | 0.00044428
31 | 0.98471 | -0.29267 | 0.0014713 | 0.00036875
32 | 0.98468 | -0.29337 | 0.00030436 | 7.628e-05
33 | 0.9846 | -0.29494 | 0.0024108 | 0.00060421
34 | 0.98203 | -0.34452 | 0.00050151 | 0.00012569
35 | 0.98231 | -0.33922 | 0.00091118 | 0.00022836
36 | 0.98179 | -0.34933 | 0 | 0
37 | 0.98233 | -0.33879 | 0.009601 | 0.0024062
38 | 0.98177 | -0.34967 | 0.00058001 | 0.00014536
39 | 0.98152 | -0.35445 | 0.0011375 | 0.00028509
40 | 0.98257 | -0.33407 | 0.0011729 | 0.00029396
41 | 0.98176 | -0.3498 | 0.000144 | 3.6089e-05
42 | 0.98138 | -0.35721 | 0 | 0
43 | 0.99724 | -0.052496 | 0.0013872 | 0.00034766
44 | 0.99713 | -0.054604 | 0.001692 | 0.00042406
45 | 0.99735 | -0.050369 | 0.0018882 | 0.00047324
46 | 0.99709 | -0.055263 | 0.0017488 | 0.0004383
47 | 0.99756 | -0.046255 | 0.0021487 | 0.00053852
48 | 0.99703 | -0.05652 | 0.001325 | 0.00033208
49 | 0.99787 | -0.04028 | 0 | 0
50 | 0.98092 | -0.36617 | 0.0006449 | 0.00016163
51 | 0.9807 | -0.37038 | 0 | 0
52 | 0.98059 | -0.37264 | 0 | 0
53 | 0.98134 | -0.35795 | 0.0017348 | 0.00043477
54 | 0.97807 | -0.42177 | 0.0011087 | 0.00027787
55 | 0.98134 | -0.35806 | 0.00039063 | 9.7901e-05
56 | 0.99238 | -0.14505 | 0.00119 | 0.00029823
57 | 0.99241 | -0.14445 | 0.0029659 | 0.00074333
58 | 0.99253 | -0.14216 | 0.00038686 | 9.6955e-05
59 | 0.99267 | -0.13942 | 0 | 0
60 | 0.99205 | -0.15137 | 0 | 0
61 | 0.99208 | -0.15086 | 0.00026752 | 6.7047e-05
62 | 0.99201 | -0.15223 | 0.001322 | 0.00033132
63 | 0.99676 | -0.061325 | 0.00066188 | 0.00016588
64 | 0.99716 | -0.053842 | 0.0018038 | 0.00045206
65 | 0.99605 | -0.074833 | 0.0019884 | 0.00049835
66 | 0.99582 | -0.079149 | 0 | 0
67 | 1 | 0 | -0.17325 | -0.043972
68 | 0.99493 | -0.096169 | 0.0017061 | 0.00042758
69 | 0.98821 | -0.22484 | 0.0032526 | 0.00081518
70 | 0.98714 | -0.24546 | 0 | 0
71 | 0.9887 | -0.21549 | 0 | 0
72 | 0.98677 | -0.25263 | 0.0019068 | 0.00047788
73 | 0.98711 | -0.24622 | 0.0005975 | 0.00014975
74 | 0.98864 | -0.2166 | 0.00099262 | 0.00024878
75 | 0.98864 | -0.21658 | 0.0020702 | 0.00051885
76 | 0.98992 | -0.19199 | 0 | 0
77 | 0.98643 | -0.25918 | 0.00033937 | 8.5055e-05
78 | 0.9871 | -0.24638 | 0.00058281 | 0.00014607
79 | 0.98863 | -0.21674 | 0.001237 | 0.00031002
80 | 0.98859 | -0.21754 | 0.0021175 | 0.0005307
81 | 0.98984 | -0.1935 | 0.0004221 | 0.00010579
82 | 0.99051 | -0.18063 | 0.00042566 | 0.00010668
83 | 0.98289 | -0.32802 | 0 | 0
84 | 0.9829 | -0.32775 | 0.0011364 | 0.00028482
85 | 0.98286 | -0.32852 | 0.00091516 | 0.00022936
86 | 0.98296 | -0.32657 | 0.0025123 | 0.00062964
87 | 0.98286 | -0.32857 | 0.00028247 | 7.0793e-05
88 | 0.97088 | -0.56317 | 0.0016508 | 0.00041374
89 | 0.97089 | -0.56317 | 0.00036197 | 9.0719e-05
90 | 0.971 | -0.5609 | 0 | 0
91 | 0.97067 | -0.56746 | 0.00093974 | 0.00023552
92 | 0.97111 | -0.55864 | 0 | 0
93 | 0.97271 | -0.52708 | 0.0033239 | 0.00083304
94 | 0.97298 | -0.52171 | 0.0022352 | 0.00056019
95 | 0.97239 | -0.53342 | 0.0025725 | 0.00064473
96 | 0.97355 | -0.51043 | 0.0021492 | 0.00053865
97 | 0.97211 | -0.53893 | 0.0012541 | 0.0003143
98 | 0.97397 | -0.50228 | 0 | 0
99 | 0.97154 | -0.55026 | 0.0047296 | 0.0011853
100 | 0.98176 | -0.34982 | 0.00048826 | 0.00012237
101 | 0.99695 | -0.058128 | 0.006025 | 0.00151
102 | 0.99272 | -0.1384 | 0.0005048 | 0.00012651
103 | 0.99298 | -0.13342 | 0 | 0
104 | 0.99215 | -0.14954 | 0.0015416 | 0.00038637
105 | 0.99367 | -0.12023 | 0.00059076 | 0.00014806
106 | 0.9922 | -0.14826 | 0.00053364 | 0.00013374
107 | 0.9921 | -0.15051 | 0.00079787 | 0.00019996
108 | 0.99137 | -0.1642 | 0.0016715 | 0.00041892
109 | 0.98298 | -0.32622 | 0.00042139 | 0.00010561
110 | 0.98295 | -0.32671 | 0.0012992 | 0.0003256
111 | 0.9709 | -0.56285 | 0.00087842 | 0.00022015
112 | 0.97091 | -0.56263 | 0.0036004 | 0.00090234
113 | 0.97099 | -0.56111 | 0.0021867 | 0.00054803
114 | 0.97517 | -0.47858 | 0.0013755 | 0.00034474
115 | 0.9752 | -0.47804 | 0 | 0
116 | 0.97549 | -0.47222 | 0 | 0
117 | 0.97519 | -0.47827 | 0.00054395 | 0.00013633
118 | 0.97752 | -0.43258 | 0.0016847 | 0.00042222
119 | 0.97387 | -0.50424 | 0.0012106 | 0.00030341
120 | 0.97517 | -0.47854 | 0.0018901 | 0.0004737
121 | 0.97413 | -0.4991 | 0.0015988 | 0.00040069
122 | 0.97414 | -0.49896 | 0.00147 | 0.00036841
123 | 0.9742 | -0.49775 | 0.0014301 | 0.00035841
124 | 0.97433 | -0.49523 | 0 | 0
125 | 0.97491 | -0.48377 | 0.0026419 | 0.00066212
126 | 0.97476 | -0.48662 | 0.0011794 | 0.0002956
127 | 0.97459 | -0.49004 | 0.0021981 | 0.00055088
128 | 0.99939 | -0.01184 | 0.0019741 | 0.00049475
129 | 0.97378 | -0.50606 | 0.0023778 | 0.00059594
130 | 0.97444 | -0.49304 | 0.0029162 | 0.00073087
131 | 0.98294 | -0.32692 | 0.0008948 | 0.00022426
132 | 0.97421 | -0.49764 | 0.0023269 | 0.00058317
133 | 0.98967 | -0.19676 | 0.0011805 | 0.00029587
134 | 0.98967 | -0.19677 | 0.00040985 | 0.00010272
135 | 0.98964 | -0.1975 | 0.002136 | 0.00053533
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0016288 | 0.0004076 | -0.0016287 | -0.00040805 | 9.8334e-08 | -4.5717e-07 | 0.0024964 | 0.0024966 | 0.0024966 | 0.97074 | -0.56601 | 0.97068 | -0.56728 | 0.68589
1 | -0.0016288 | -0.0004076 | 0.0016288 | 0.00040728 | 6.7124e-08 | -3.1215e-07 | 0.0024964 | 0.0024963 | 0.0024964 | 0.97074 | -0.56601 | 0.97079 | -0.56515 | 0.68583
2 | 0.00093975 | 0.0002354 | -0.00093974 | -0.00023552 | 8.1467e-09 | -1.2419e-07 | 0.0014406 | 0.0014406 | 0.0014406 | 0.97068 | -0.56728 | 0.97067 | -0.56746 | 0.39577
3 | -0.003669 | -0.00091861 | 0.0036694 | 0.00091847 | 3.4468e-07 | -1.388e-07 | 0.0056235 | 0.0056234 | 0.0056235 | 0.97079 | -0.56515 | 0.97088 | -0.56317 | 1.5449
4 | -0.098106 | -0.024787 | 0.098137 | 0.024807 | 3.1752e-05 | 1.9541e-05 | 0.14847 | 0.14847 | 0.14847 | 0.9837 | -0.31212 | 0.98405 | -0.30537 | 10.1973
5 | 0.09472 | 0.023939 | -0.094699 | -0.023926 | 2.0802e-05 | 1.2765e-05 | 0.14335 | 0.14335 | 0.14335 | 0.9837 | -0.31212 | 0.98347 | -0.3167 | 9.8456
6 | 0.0054906 | 0.0013758 | -0.00549 | -0.0013757 | 5.6585e-07 | 8.4074e-08 | 0.0083024 | 0.0083025 | 0.0083025 | 0.98405 | -0.30537 | 0.98394 | -0.30754 | 2.2809
7 | -0.10363 | -0.026183 | 0.1037 | 0.026227 | 7.161e-05 | 4.425e-05 | 0.15678 | 0.15677 | 0.15678 | 0.98405 | -0.30537 | 0.98479 | -0.29097 | 10.7675
8 | 0.0818 | 0.020694 | -0.081767 | -0.020674 | 3.3033e-05 | 1.9976e-05 | 0.12384 | 0.12384 | 0.12384 | 0.98347 | -0.3167 | 0.98303 | -0.32512 | 8.5052
9 | 0.012899 | 0.0032322 | -0.012896 | -0.0032307 | 2.8368e-06 | 1.5636e-06 | 0.019516 | 0.019516 | 0.019516 | 0.98347 | -0.3167 | 0.98323 | -0.32132 | 5.3616
10 | 0.0034645 | 0.00086811 | -0.0034643 | -0.00086824 | 2.2587e-07 | -1.341e-07 | 0.0052394 | 0.0052395 | 0.0052395 | 0.98394 | -0.30754 | 0.98387 | -0.30891 | 1.4394
11 | -0.10634 | -0.026888 | 0.10643 | 0.026941 | 8.5341e-05 | 5.2824e-05 | 0.16077 | 0.16077 | 0.16077 | 0.98479 | -0.29097 | 0.98565 | -0.27425 | 11.0418
12 | 0.0026433 | 0.00066159 | -0.0026433 | -0.00066168 | 5.9682e-08 | -8.8754e-08 | 0.0039937 | 0.0039938 | 0.0039938 | 0.98479 | -0.29097 | 0.98477 | -0.29144 | 1.0972
13 | 0.07462 | 0.018883 | -0.0746 | -0.018871 | 1.9565e-05 | 1.1694e-05 | 0.11302 | 0.11302 | 0.11302 | 0.98303 | -0.32512 | 0.98275 | -0.33059 | 7.7622
14 | 0.0093106 | 0.002332 | -0.0093096 | -0.0023316 | 9.7757e-07 | 4.5913e-07 | 0.01409 | 0.01409 | 0.01409 | 0.98323 | -0.32132 | 0.98312 | -0.32353 | 3.8709
15 | -0.11562 | -0.029244 | 0.11566 | 0.029269 | 4.0925e-05 | 2.5462e-05 | 0.17464 | 0.17464 | 0.17464 | 0.98565 | -0.27425 | 0.98604 | -0.26688 | 11.9944
16 | 0.009188 | 0.0023027 | -0.0091865 | -0.002302 | 1.4337e-06 | 6.6434e-07 | 0.013871 | 0.013871 | 0.013871 | 0.98565 | -0.27425 | 0.98549 | -0.27753 | 3.8107
17 | 0.0022118 | 0.00055355 | -0.0022118 | -0.0005536 | 2.1166e-08 | -5.0751e-08 | 0.0033419 | 0.0033419 | 0.0033419 | 0.98477 | -0.29144 | 0.98476 | -0.29164 | 0.91811
18 | -0.11597 | -0.029348 | 0.11601 | 0.029375 | 4.2879e-05 | 2.6681e-05 | 0.17511 | 0.17511 | 0.17511 | 0.98604 | -0.26688 | 0.98643 | -0.25918 | 12.0268
19 | 0.0087522 | 0.0021931 | -0.008752 | -0.0021931 | 1.9305e-07 | 8.5996e-08 | 0.013215 | 0.013215 | 0.013215 | 0.98549 | -0.27753 | 0.98546 | -0.27799 | 3.6305
20 | 0.072372 | 0.018312 | -0.07236 | -0.018305 | 1.2095e-05 | 7.1973e-06 | 0.10964 | 0.10964 | 0.10964 | 0.98275 | -0.33059 | 0.98257 | -0.33407 | 7.5304
21 | 0.0026157 | 0.00065467 | -0.0026154 | -0.00065518 | 3.3556e-07 | -5.0909e-07 | 0.0039588 | 0.003959 | 0.003959 | 0.98312 | -0.32353 | 0.98298 | -0.32622 | 1.0877
22 | 0.0066938 | 0.0016769 | -0.0066929 | -0.0016766 | 9.6817e-07 | 3.0074e-07 | 0.010131 | 0.010131 | 0.010131 | 0.98312 | -0.32353 | 0.98296 | -0.32657 | 2.7834
23 | 0.0073488 | 0.0018415 | -0.0073479 | -0.0018412 | 9.2577e-07 | 3.372e-07 | 0.011098 | 0.011098 | 0.011098 | 0.98535 | -0.28016 | 0.98522 | -0.28281 | 3.0488
24 | -0.0076336 | -0.0019129 | 0.0076343 | 0.0019132 | 7.8958e-07 | 3.0348e-07 | 0.011528 | 0.011528 | 0.011528 | 0.98535 | -0.28016 | 0.98546 | -0.27799 | 3.1669
25 | 0.007046 | 0.0017655 | -0.0070438 | -0.0017648 | 2.2604e-06 | 7.6911e-07 | 0.010642 | 0.010642 | 0.010642 | 0.98522 | -0.28281 | 0.98487 | -0.28954 | 2.9236
26 | 0.0011177 | 0.00027988 | -0.0011177 | -0.00028009 | 1.865e-08 | -2.1054e-07 | 0.0016876 | 0.0016877 | 0.0016877 | 0.98546 | -0.27799 | 0.98545 | -0.27834 | 0.46364
27 | 0.0063406 | 0.0015885 | -0.0063405 | -0.0015885 | 7.2408e-08 | 1.9567e-08 | 0.0095796 | 0.0095796 | 0.0095796 | 0.98487 | -0.28954 | 0.98486 | -0.28978 | 2.6318
28 | 0.0011177 | 0.00028009 | -0.0011177 | -0.00028011 | 1.5053e-09 | -1.6993e-08 | 0.0016877 | 0.0016877 | 0.0016877 | 0.98545 | -0.27834 | 0.98544 | -0.27837 | 0.46364
29 | 0.0059603 | 0.0014932 | -0.0059596 | -0.001493 | 7.3901e-07 | 1.6377e-07 | 0.0090052 | 0.0090053 | 0.0090053 | 0.98486 | -0.28978 | 0.98473 | -0.29239 | 2.474
30 | 0.0016488 | 0.00041311 | -0.0016488 | -0.00041323 | 2.4128e-08 | -1.1642e-07 | 0.0024915 | 0.0024915 | 0.0024915 | 0.98473 | -0.29216 | 0.98472 | -0.29246 | 0.68449
31 | -0.0016488 | -0.00041311 | 0.0016489 | 0.00041292 | 4.0286e-08 | -1.944e-07 | 0.0024915 | 0.0024914 | 0.0024915 | 0.98473 | -0.29216 | 0.98476 | -0.29164 | 0.68447
32 | 0.00056296 | 0.00014069 | -0.00056295 | -0.00014109 | 8.7159e-09 | -4.0312e-07 | 0.00085051 | 0.00085066 | 0.00085066 | 0.98476 | -0.29164 | 0.98474 | -0.29197 | 0.2337
33 | -0.00086325 | -0.00021635 | 0.00086325 | 0.00021633 | 1.2288e-09 | -2.3526e-08 | 0.0013069 | 0.0013069 | 0.0013069 | 0.98286 | -0.32861 | 0.98286 | -0.32858 | 0.35905
34 | -0.0018462 | -0.00046267 | 0.0018462 | 0.00046248 | 4.9685e-08 | -1.8315e-07 | 0.002795 | 0.0027949 | 0.002795 | 0.98286 | -0.32858 | 0.98289 | -0.32802 | 0.76786
35 | 0.0041869 | 0.0010488 | -0.0041868 | -0.0010488 | 5.6769e-08 | -1.1782e-08 | 0.0063266 | 0.0063266 | 0.0063266 | 0.98473 | -0.29239 | 0.98471 | -0.29267 | 1.7381
36 | 0.0027155 | 0.00068003 | -0.0027154 | -0.00068015 | 9.0059e-08 | -1.2381e-07 | 0.0041032 | 0.0041033 | 0.0041033 | 0.98471 | -0.29267 | 0.98468 | -0.29337 | 1.1273
37 | 0.002411 | 0.00060387 | -0.0024108 | -0.00060421 | 1.8027e-07 | -3.4523e-07 | 0.0036433 | 0.0036435 | 0.0036435 | 0.98468 | -0.29337 | 0.9846 | -0.29494 | 1.001
38 | -0.060642 | -0.015357 | 0.060657 | 0.015366 | 1.5427e-05 | 8.888e-06 | 0.091944 | 0.091944 | 0.091944 | 0.98203 | -0.34452 | 0.98231 | -0.33922 | 6.3148
39 | 0.06014 | 0.015232 | -0.060126 | -0.015224 | 1.3899e-05 | 7.9933e-06 | 0.091184 | 0.091184 | 0.091184 | 0.98203 | -0.34452 | 0.98179 | -0.34933 | 6.2627
40 | -0.061568 | -0.015595 | 0.06157 | 0.015595 | 1.262e-06 | 7.2943e-07 | 0.093324 | 0.093324 | 0.093324 | 0.98231 | -0.33922 | 0.98233 | -0.33879 | 6.4096
41 | 0.0012123 | 0.00030346 | -0.0012123 | -0.00030365 | 1.961e-08 | -1.8335e-07 | 0.0018372 | 0.0018373 | 0.0018373 | 0.98179 | -0.34933 | 0.98177 | -0.34967 | 0.50475
42 | 0.058914 | 0.01492 | -0.0589 | -0.014912 | 1.4498e-05 | 8.2992e-06 | 0.089347 | 0.089348 | 0.089348 | 0.98179 | -0.34933 | 0.98152 | -0.35445 | 6.1365
43 | -0.071171 | -0.018002 | 0.071187 | 0.018011 | 1.612e-05 | 9.5681e-06 | 0.10787 | 0.10787 | 0.10787 | 0.98233 | -0.33879 | 0.98257 | -0.33407 | 7.4085
44 | 0.00063226 | 0.00015828 | -0.00063225 | -0.00015843 | 3.9967e-09 | -1.4421e-07 | 0.00095822 | 0.00095827 | 0.00095827 | 0.98177 | -0.34967 | 0.98176 | -0.3498 | 0.26326
45 | 0.057762 | 0.014627 | -0.057754 | -0.014622 | 7.6387e-06 | 4.3523e-06 | 0.087623 | 0.087623 | 0.087623 | 0.98152 | -0.35445 | 0.98138 | -0.35721 | 6.0181
46 | 0.00048826 | 0.00012234 | -0.00048826 | -0.00012237 | 4.8544e-10 | -2.958e-08 | 0.00074002 | 0.00074003 | 0.00074003 | 0.98176 | -0.3498 | 0.98176 | -0.34982 | 0.20331
47 | 0.0021255 | 0.00053229 | -0.0021254 | -0.00053249 | 7.5136e-08 | -1.9567e-07 | 0.0032226 | 0.0032227 | 0.0032227 | 0.98138 | -0.35721 | 0.98134 | -0.35795 | 0.88535
48 | 0.055629 | 0.01409 | -0.055605 | -0.014077 | 2.3938e-05 | 1.351e-05 | 0.084401 | 0.084401 | 0.084401 | 0.98138 | -0.35721 | 0.98092 | -0.36617 | 5.7968
49 | 0.010793 | 0.0027054 | -0.010792 | -0.0027048 | 1.0839e-06 | 5.4833e-07 | 0.016105 | 0.016105 | 0.016105 | 0.99724 | -0.052496 | 0.99713 | -0.054604 | 4.4244
50 | -0.01218 | -0.003053 | 0.012182 | 0.0030537 | 1.2344e-06 | 6.5998e-07 | 0.018175 | 0.018175 | 0.018175 | 0.99724 | -0.052496 | 0.99735 | -0.050369 | 4.9931
51 | 0.0091 | 0.0022808 | -0.0090997 | -0.0022806 | 2.8554e-07 | 1.2889e-07 | 0.01358 | 0.01358 | 0.01358 | 0.99713 | -0.054604 | 0.99709 | -0.055263 | 3.7308
52 | -0.01407 | -0.0035269 | 0.014073 | 0.0035285 | 2.7587e-06 | 1.5477e-06 | 0.020992 | 0.020992 | 0.020992 | 0.99735 | -0.050369 | 0.99756 | -0.046255 | 5.767
53 | 0.0073509 | 0.0018423 | -0.0073505 | -0.0018422 | 4.4012e-07 | 1.5448e-07 | 0.01097 | 0.01097 | 0.01097 | 0.99709 | -0.055263 | 0.99703 | -0.05652 | 3.0138
54 | -0.016221 | -0.004067 | 0.016226 | 0.0040697 | 4.6199e-06 | 2.682e-06 | 0.024197 | 0.024197 | 0.024197 | 0.99756 | -0.046255 | 0.99787 | -0.04028 | 6.6475
55 | 0.0060255 | 0.0015101 | -0.006025 | -0.00151 | 4.6157e-07 | 9.6927e-08 | 0.0089927 | 0.0089928 | 0.0089928 | 0.99703 | -0.05652 | 0.99695 | -0.058128 | 2.4705
56 | -0.1693 | -0.043272 | 0.16963 | 0.043481 | 0.00033055 | 0.00020866 | 0.25275 | 0.25275 | 0.25275 | 0.99787 | -0.04028 | 1 | 0 | 17.3595
57 | 0.15307 | 0.039203 | -0.15297 | -0.039139 | 0.0001005 | 6.3249e-05 | 0.22856 | 0.22856 | 0.22856 | 0.99787 | -0.04028 | 0.99716 | -0.053842 | 15.6976
58 | 0.05496 | 0.013915 | -0.054949 | -0.013909 | 1.1099e-05 | 6.2446e-06 | 0.083423 | 0.083423 | 0.083423 | 0.98092 | -0.36617 | 0.9807 | -0.37038 | 5.7296
59 | 0.054949 | 0.013909 | -0.054943 | -0.013905 | 5.9653e-06 | 3.3564e-06 | 0.083423 | 0.083423 | 0.083423 | 0.9807 | -0.37038 | 0.98059 | -0.37264 | 5.7296
60 | 0.054943 | 0.013905 | -0.054814 | -0.013825 | 0.00012924 | 8.0223e-05 | 0.083423 | 0.083424 | 0.083424 | 0.98059 | -0.37264 | 0.97807 | -0.42177 | 11.4594
61 | 0.00039063 | 9.7713e-05 | -0.00039063 | -9.7901e-05 | 1.972e-09 | -1.8813e-07 | 0.00059225 | 0.00059232 | 0.00059232 | 0.98134 | -0.35795 | 0.98134 | -0.35806 | 0.16272
62 | 0.053705 | 0.013547 | -0.053677 | -0.01353 | 2.7779e-05 | 1.7639e-05 | 0.081738 | 0.081738 | 0.081738 | 0.97807 | -0.42177 | 0.97752 | -0.43258 | 22.4554
63 | -0.00119 | -0.00029823 | 0.00119 | 0.00029789 | 3.3998e-08 | -3.462e-07 | 0.0017843 | 0.0017842 | 0.0017843 | 0.99238 | -0.14505 | 0.99241 | -0.14445 | 0.49019
64 | -0.0041559 | -0.0010412 | 0.0041564 | 0.0010411 | 4.5255e-07 | -1.1201e-07 | 0.0062313 | 0.0062311 | 0.0062313 | 0.99241 | -0.14445 | 0.99253 | -0.14216 | 1.7119
65 | -0.0045432 | -0.0011381 | 0.0045438 | 0.001138 | 5.9303e-07 | -6.1093e-08 | 0.0068111 | 0.0068109 | 0.0068111 | 0.99253 | -0.14216 | 0.99267 | -0.13942 | 1.8712
66 | 0.0039311 | 0.00098298 | -0.0039293 | -0.00098364 | 1.8918e-06 | -6.6664e-07 | 0.005892 | 0.0058927 | 0.0058927 | 0.99267 | -0.13942 | 0.99215 | -0.14954 | 1.6189
67 | -0.008475 | -0.002121 | 0.0084754 | 0.0021211 | 4.1152e-07 | 1.7545e-07 | 0.012703 | 0.012703 | 0.012703 | 0.99267 | -0.13942 | 0.99272 | -0.1384 | 3.4898
68 | -0.001322 | -0.00033089 | 0.0013221 | 0.00033063 | 3.2401e-08 | -2.6303e-07 | 0.0019828 | 0.0019827 | 0.0019828 | 0.99205 | -0.15137 | 0.99208 | -0.15086 | 0.54473
69 | 0.001322 | 0.00033089 | -0.001322 | -0.00033132 | 5.3511e-08 | -4.3431e-07 | 0.0019828 | 0.001983 | 0.001983 | 0.99205 | -0.15137 | 0.99201 | -0.15223 | 0.54478
70 | -0.0015896 | -0.00039767 | 0.0015896 | 0.00039753 | 2.6688e-08 | -1.4462e-07 | 0.002384 | 0.0023839 | 0.002384 | 0.99208 | -0.15086 | 0.9921 | -0.15051 | 0.65494
71 | -0.15111 | -0.038653 | 0.15117 | 0.038687 | 5.475e-05 | 3.4443e-05 | 0.22587 | 0.22587 | 0.22587 | 0.99676 | -0.061325 | 0.99716 | -0.053842 | 15.5128
72 | 0.15045 | 0.038487 | -0.15035 | -0.038425 | 9.8295e-05 | 6.1829e-05 | 0.22488 | 0.22488 | 0.22488 | 0.99676 | -0.061325 | 0.99605 | -0.074833 | 15.445
73 | 0.14836 | 0.037927 | -0.14833 | -0.037907 | 3.0968e-05 | 1.9471e-05 | 0.22191 | 0.22191 | 0.22191 | 0.99605 | -0.074833 | 0.99582 | -0.079149 | 15.2409
74 | 0.14833 | 0.037907 | -0.14821 | -0.037831 | 0.00012199 | 7.6701e-05 | 0.22191 | 0.22191 | 0.22191 | 0.99582 | -0.079149 | 0.99493 | -0.096169 | 15.241
75 | 0.0019752 | 0.00049096 | -0.0019741 | -0.00049475 | 1.1103e-06 | -3.7852e-06 | 0.0029377 | 0.0029392 | 0.0029392 | 1 | 0 | 0.99939 | -0.01184 | 0.80749
76 | 0.14651 | 0.037403 | -0.14633 | -0.037296 | 0.00017018 | 0.00010696 | 0.21936 | 0.21936 | 0.21936 | 0.99493 | -0.096169 | 0.99367 | -0.12023 | 15.0658
77 | 0.11964 | 0.030355 | -0.11952 | -0.030281 | 0.00011854 | 7.3872e-05 | 0.18028 | 0.18028 | 0.18028 | 0.98821 | -0.22484 | 0.98714 | -0.24546 | 12.3816
78 | -0.12289 | -0.03117 | 0.12294 | 0.031204 | 5.5293e-05 | 3.4505e-05 | 0.18517 | 0.18517 | 0.18517 | 0.98821 | -0.22484 | 0.9887 | -0.21549 | 12.7179
79 | 0.11834 | 0.029986 | -0.1183 | -0.02996 | 4.0717e-05 | 2.5362e-05 | 0.1785 | 0.1785 | 0.1785 | 0.98714 | -0.24546 | 0.98677 | -0.25263 | 12.2594
80 | 0.0011804 | 0.00029519 | -0.0011803 | -0.00029562 | 4.2387e-08 | -4.2938e-07 | 0.001779 | 0.0017792 | 0.0017792 | 0.98714 | -0.24546 | 0.98711 | -0.24622 | 0.48879
81 | 0.0022297 | 0.00055844 | -0.0022296 | -0.00055872 | 1.1824e-07 | -2.8337e-07 | 0.0033557 | 0.0033558 | 0.0033558 | 0.9887 | -0.21549 | 0.98864 | -0.2166 | 0.92193
82 | 0.0041881 | 0.0010492 | -0.0041879 | -0.0010493 | 2.181e-07 | -4.8144e-08 | 0.0063031 | 0.0063031 | 0.0063031 | 0.9887 | -0.21549 | 0.98864 | -0.21658 | 1.7316
83 | -0.12936 | -0.032812 | 0.12951 | 0.032904 | 0.0001463 | 9.152e-05 | 0.19483 | 0.19483 | 0.19483 | 0.9887 | -0.21549 | 0.98992 | -0.19199 | 13.3813
84 | 0.11639 | 0.029482 | -0.11635 | -0.02946 | 3.6588e-05 | 2.277e-05 | 0.17562 | 0.17562 | 0.17562 | 0.98677 | -0.25263 | 0.98643 | -0.25918 | 12.0619
85 | 0.00058281 | 0.00014587 | -0.00058281 | -0.00014607 | 4.4707e-09 | -1.9459e-07 | 0.00087849 | 0.00087856 | 0.00087856 | 0.98711 | -0.24622 | 0.9871 | -0.24638 | 0.24136
86 | 0.001237 | 0.00030994 | -0.001237 | -0.00031002 | 8.2129e-09 | -7.576e-08 | 0.0018618 | 0.0018618 | 0.0018618 | 0.98864 | -0.2166 | 0.98863 | -0.21674 | 0.51149
87 | 0.0021176 | 0.00053044 | -0.0021175 | -0.0005307 | 9.6759e-08 | -2.6376e-07 | 0.0031872 | 0.0031873 | 0.0031873 | 0.98864 | -0.21658 | 0.98859 | -0.21754 | 0.87563
88 | 0.0041494 | 0.0010392 | -0.0041491 | -0.0010392 | 2.9727e-07 | -7.1705e-08 | 0.006237 | 0.0062371 | 0.0062371 | 0.98992 | -0.19199 | 0.98984 | -0.1935 | 1.7135
89 | -0.13366 | -0.033943 | 0.13373 | 0.033989 | 7.3157e-05 | 4.5828e-05 | 0.20107 | 0.20107 | 0.20107 | 0.98992 | -0.19199 | 0.99051 | -0.18063 | 13.8096
90 | 0.003727 | 0.00093346 | -0.0037265 | -0.00093372 | 5.7973e-07 | -2.6192e-07 | 0.0056026 | 0.0056028 | 0.0056028 | 0.98984 | -0.1935 | 0.98967 | -0.19676 | 1.5392
91 | -0.13416 | -0.034095 | 0.13426 | 0.034162 | 0.00010619 | 6.6529e-05 | 0.20171 | 0.20171 | 0.20171 | 0.99051 | -0.18063 | 0.99137 | -0.1642 | 13.8535
92 | -0.0030439 | -0.00076224 | 0.0030439 | 0.0007622 | 3.9734e-08 | -3.7817e-08 | 0.0046079 | 0.0046079 | 0.0046079 | 0.98289 | -0.32802 | 0.9829 | -0.32775 | 1.2659
93 | 0.0011977 | 0.00029976 | -0.0011976 | -0.00030003 | 2.8607e-08 | -2.7581e-07 | 0.001813 | 0.0018131 | 0.0018131 | 0.98289 | -0.32802 | 0.98286 | -0.32852 | 0.49811
94 | -0.0041803 | -0.001047 | 0.0041806 | 0.001047 | 2.3489e-07 | -4.7919e-08 | 0.0063284 | 0.0063283 | 0.0063284 | 0.9829 | -0.32775 | 0.98296 | -0.32657 | 1.7386
95 | 0.00028247 | 7.0671e-05 | -0.00028247 | -7.0793e-05 | 6.638e-10 | -1.2225e-07 | 0.0004276 | 0.00042765 | 0.00042765 | 0.98286 | -0.32852 | 0.98286 | -0.32857 | 0.11749
96 | -0.0053202 | -0.0013322 | 0.0053202 | 0.0013322 | 2.2773e-09 | 3.2812e-10 | 0.0081535 | 0.0081535 | 0.0081535 | 0.97088 | -0.56317 | 0.97089 | -0.56317 | 2.24
97 | -0.0056822 | -0.0014229 | 0.0056828 | 0.0014231 | 6.1382e-07 | 1.2589e-07 | 0.0087083 | 0.0087082 | 0.0087083 | 0.97089 | -0.56317 | 0.971 | -0.5609 | 2.3924
98 | -0.0056828 | -0.0014231 | 0.0056834 | 0.0014232 | 6.106e-07 | 1.2516e-07 | 0.0087082 | 0.0087081 | 0.0087082 | 0.971 | -0.5609 | 0.97111 | -0.55864 | 2.3924
99 | -0.01235 | -0.0030938 | 0.012355 | 0.0030965 | 4.9306e-06 | 2.7011e-06 | 0.018923 | 0.018923 | 0.018923 | 0.97111 | -0.55864 | 0.97154 | -0.55026 | 5.1987
100 | 0.0066666 | 0.0016706 | -0.0066658 | -0.0016703 | 7.8315e-07 | 2.5363e-07 | 0.010215 | 0.010215 | 0.010215 | 0.97111 | -0.55864 | 0.97099 | -0.56111 | 2.8064
101 | -0.024255 | -0.0060861 | 0.024262 | 0.0060899 | 6.2142e-06 | 3.8276e-06 | 0.037108 | 0.037107 | 0.037108 | 0.97271 | -0.52708 | 0.97298 | -0.52171 | 10.1944
102 | 0.020931 | 0.005253 | -0.020925 | -0.0052492 | 6.3234e-06 | 3.8429e-06 | 0.032023 | 0.032023 | 0.032023 | 0.97271 | -0.52708 | 0.97239 | -0.53342 | 8.7975
103 | -0.026497 | -0.0066501 | 0.026511 | 0.0066589 | 1.4262e-05 | 8.8396e-06 | 0.040526 | 0.040526 | 0.040526 | 0.97298 | -0.52171 | 0.97355 | -0.51043 | 11.1335
104 | 0.018353 | 0.0046045 | -0.018348 | -0.0046016 | 4.8266e-06 | 2.8867e-06 | 0.028086 | 0.028086 | 0.028086 | 0.97239 | -0.53342 | 0.97211 | -0.53893 | 7.716
105 | -0.02866 | -0.0071976 | 0.028671 | 0.0072045 | 1.1148e-05 | 6.9418e-06 | 0.043811 | 0.043811 | 0.043811 | 0.97355 | -0.51043 | 0.97397 | -0.50228 | 12.0359
106 | 0.017094 | 0.0042873 | -0.017085 | -0.0042818 | 9.2234e-06 | 5.4579e-06 | 0.026167 | 0.026167 | 0.026167 | 0.97211 | -0.53893 | 0.97154 | -0.55026 | 7.1887
107 | 0.003589 | 0.0008988 | -0.0035886 | -0.00089896 | 3.3591e-07 | -1.5579e-07 | 0.0054829 | 0.0054831 | 0.0054831 | 0.97397 | -0.50228 | 0.97387 | -0.50424 | 1.5063
108 | -0.03226 | -0.0081033 | 0.032298 | 0.0081267 | 3.7364e-05 | 2.3402e-05 | 0.049294 | 0.049293 | 0.049294 | 0.97397 | -0.50228 | 0.9752 | -0.47804 | 13.5422
109 | -0.0089802 | -0.0022477 | 0.0089823 | 0.0022486 | 2.128e-06 | 9.5681e-07 | 0.01346 | 0.013459 | 0.01346 | 0.99272 | -0.1384 | 0.99298 | -0.13342 | 3.6977
110 | -0.14565 | -0.03709 | 0.14574 | 0.037148 | 9.2715e-05 | 5.8265e-05 | 0.21847 | 0.21847 | 0.21847 | 0.99298 | -0.13342 | 0.99367 | -0.12023 | 15.005
111 | 0.13667 | 0.034841 | -0.13657 | -0.03478 | 9.78e-05 | 6.1309e-05 | 0.20501 | 0.20501 | 0.20501 | 0.99298 | -0.13342 | 0.9922 | -0.14826 | 14.0807
112 | 0.0023876 | 0.00059727 | -0.0023875 | -0.00059749 | 1.0981e-07 | -2.2466e-07 | 0.0035805 | 0.0035806 | 0.0035806 | 0.99215 | -0.14954 | 0.9921 | -0.15051 | 0.98369
113 | 0.13604 | 0.034646 | -0.13593 | -0.034581 | 0.00010452 | 6.5511e-05 | 0.20421 | 0.20421 | 0.20421 | 0.9922 | -0.14826 | 0.99137 | -0.1642 | 14.0257
114 | 0.002194 | 0.00054957 | -0.002194 | -0.00054969 | 5.0692e-08 | -1.2291e-07 | 0.0033212 | 0.0033212 | 0.0033212 | 0.98298 | -0.32622 | 0.98295 | -0.32671 | 0.91242
115 | 0.00089481 | 0.00022409 | -0.0008948 | -0.00022426 | 9.2283e-09 | -1.641e-07 | 0.0013545 | 0.0013546 | 0.0013546 | 0.98295 | -0.32671 | 0.98294 | -0.32692 | 0.37214
116 | -0.00087842 | -0.00022015 | 0.00087843 | 0.00021999 | 9.2e-09 | -1.6152e-07 | 0.0013463 | 0.0013462 | 0.0013463 | 0.9709 | -0.56285 | 0.97091 | -0.56263 | 0.36986
117 | -0.0044788 | -0.0011223 | 0.0044791 | 0.0011223 | 3.2481e-07 | -1.9491e-08 | 0.0068642 | 0.0068641 | 0.0068642 | 0.97091 | -0.56263 | 0.97099 | -0.56111 | 1.8858
118 | -0.0013755 | -0.00034474 | 0.0013756 | 0.00034449 | 3.5583e-08 | -2.4597e-07 | 0.0020989 | 0.0020988 | 0.0020989 | 0.97517 | -0.47858 | 0.9752 | -0.47804 | 0.57662
119 | -0.033673 | -0.0084712 | 0.033683 | 0.0084771 | 9.3586e-06 | 5.8716e-06 | 0.051392 | 0.051392 | 0.051392 | 0.9752 | -0.47804 | 0.97549 | -0.47222 | 14.1187
120 | 0.018212 | 0.0045679 | -0.018206 | -0.0045648 | 5.2439e-06 | 3.13e-06 | 0.027781 | 0.027781 | 0.027781 | 0.97549 | -0.47222 | 0.97519 | -0.47827 | 7.6322
121 | -0.051894 | -0.013045 | 0.051993 | 0.013108 | 9.8429e-05 | 6.2471e-05 | 0.079173 | 0.079173 | 0.079173 | 0.97549 | -0.47222 | 0.97752 | -0.43258 | 21.7509
122 | 0.017662 | 0.0044285 | -0.017662 | -0.0044283 | 2.282e-07 | 1.3559e-07 | 0.026951 | 0.026951 | 0.026951 | 0.97519 | -0.47827 | 0.97517 | -0.47854 | 7.4042
123 | 0.002378 | 0.00059555 | -0.0023778 | -0.00059594 | 2.0604e-07 | -3.8593e-07 | 0.0036333 | 0.0036335 | 0.0036335 | 0.97387 | -0.50424 | 0.97378 | -0.50606 | 0.99822
124 | 0.015772 | 0.0039546 | -0.015768 | -0.0039524 | 3.9339e-06 | 2.2918e-06 | 0.024067 | 0.024067 | 0.024067 | 0.97517 | -0.47854 | 0.97491 | -0.48377 | 6.6119
125 | -0.0015988 | -0.00040069 | 0.0015988 | 0.00040064 | 1.0986e-08 | -5.412e-08 | 0.0024422 | 0.0024422 | 0.0024422 | 0.97413 | -0.4991 | 0.97414 | -0.49896 | 0.67093
126 | -0.0030688 | -0.00076905 | 0.0030689 | 0.00076889 | 1.768e-07 | -1.5399e-07 | 0.0046876 | 0.0046875 | 0.0046876 | 0.97414 | -0.49896 | 0.9742 | -0.49775 | 1.2878
127 | -0.004499 | -0.0011273 | 0.0044995 | 0.0011273 | 5.4058e-07 | -3.4185e-08 | 0.0068718 | 0.0068717 | 0.0068718 | 0.9742 | -0.49775 | 0.97433 | -0.49523 | 1.8879
128 | -0.0068267 | -0.0017099 | 0.0068274 | 0.0017101 | 7.1084e-07 | 2.3771e-07 | 0.010426 | 0.010425 | 0.010426 | 0.97433 | -0.49523 | 0.97444 | -0.49304 | 2.8642
129 | 0.0023272 | 0.00058264 | -0.0023269 | -0.00058317 | 2.6694e-07 | -5.3097e-07 | 0.0035539 | 0.0035541 | 0.0035541 | 0.97433 | -0.49523 | 0.97421 | -0.49764 | 0.97641
130 | 0.013126 | 0.0032902 | -0.013124 | -0.0032892 | 1.7783e-06 | 9.9082e-07 | 0.020035 | 0.020035 | 0.020035 | 0.97491 | -0.48377 | 0.97476 | -0.48662 | 5.5041
131 | 0.011945 | 0.0029936 | -0.011943 | -0.0029926 | 1.9489e-06 | 1.0525e-06 | 0.018235 | 0.018235 | 0.018235 | 0.97476 | -0.48662 | 0.97459 | -0.49004 | 5.0095
132 | 0.009745 | 0.0024417 | -0.0097436 | -0.002441 | 1.3923e-06 | 6.8212e-07 | 0.014879 | 0.014879 | 0.014879 | 0.97459 | -0.49004 | 0.97444 | -0.49304 | 4.0875
133 | 0.0025459 | 0.00063785 | -0.0025459 | -0.00063785 | 6.6561e-10 | -1.1312e-09 | 0.0038278 | 0.0038278 | 0.0038278 | 0.98967 | -0.19676 | 0.98967 | -0.19677 | 1.0516
134 | 0.0021361 | 0.00053513 | -0.002136 | -0.00053533 | 7.4113e-08 | -1.9877e-07 | 0.0032116 | 0.0032117 | 0.0032117 | 0.98967 | -0.19677 | 0.98964 | -0.1975 | 0.88233

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.17325 | 0.043972

## res_load
| p_mw | q_mvar
0 | 0.00068891 | 0.00017266
1 | 0.0020402 | 0.00051132
2 | 0.0033858 | 0.00084857
3 | 0.0020255 | 0.00050763
4 | 0.0071473 | 0.0017913
5 | 0.0035855 | 0.00089861
6 | 0.0034643 | 0.00086824
7 | 0.00043142 | 0.00010812
8 | 0.00031287 | 7.8413e-05
9 | 0.00043433 | 0.00010885
10 | 0.0022284 | 0.00055848
11 | 0.0002847 | 7.1353e-05
12 | 0.00030189 | 7.566e-05
13 | 0.0007032 | 0.00017624
14 | 0.00038019 | 9.5285e-05
15 | 0.0016488 | 0.00041323
16 | 0.0011177 | 0.00028011
17 | 0.00056295 | 0.00014109
18 | 0.00086325 | 0.00021635
19 | 0.00098291 | 0.00024634
20 | 0.0017727 | 0.00044428
21 | 0.0014713 | 0.00036875
22 | 0.00030436 | 7.628e-05
23 | 0.0024108 | 0.00060421
24 | 0.00050151 | 0.00012569
25 | 0.00091118 | 0.00022836
26 | 0.009601 | 0.0024062
27 | 0.00058001 | 0.00014536
28 | 0.0011375 | 0.00028509
29 | 0.0011729 | 0.00029396
30 | 0.000144 | 3.6089e-05
31 | 0.0013872 | 0.00034766
32 | 0.001692 | 0.00042406
33 | 0.0018882 | 0.00047324
34 | 0.0017488 | 0.0004383
35 | 0.0021487 | 0.00053852
36 | 0.001325 | 0.00033208
37 | 0.0006449 | 0.00016163
38 | 0.0017348 | 0.00043477
39 | 0.0011087 | 0.00027787
40 | 0.00039063 | 9.7901e-05
41 | 0.00119 | 0.00029823
42 | 0.0029659 | 0.00074333
43 | 0.00038686 | 9.6955e-05
44 | 0.00026752 | 6.7047e-05
45 | 0.001322 | 0.00033132
46 | 0.00066188 | 0.00016588
47 | 0.0018038 | 0.00045206
48 | 0.0019884 | 0.00049835
49 | 0.0017061 | 0.00042758
50 | 0.0032526 | 0.00081518
51 | 0.0019068 | 0.00047788
52 | 0.0005975 | 0.00014975
53 | 0.00099262 | 0.00024878
54 | 0.0020702 | 0.00051885
55 | 0.00033937 | 8.5055e-05
56 | 0.00058281 | 0.00014607
57 | 0.001237 | 0.00031002
58 | 0.0021175 | 0.0005307
59 | 0.0004221 | 0.00010579
60 | 0.00042566 | 0.00010668
61 | 0.0011364 | 0.00028482
62 | 0.00091516 | 0.00022936
63 | 0.0025123 | 0.00062964
64 | 0.00028247 | 7.0793e-05
65 | 0.0016508 | 0.00041374
66 | 0.00036197 | 9.0719e-05
67 | 0.00093974 | 0.00023552
68 | 0.0033239 | 0.00083304
69 | 0.0022352 | 0.00056019
70 | 0.0025725 | 0.00064473
71 | 0.0021492 | 0.00053865
72 | 0.0012541 | 0.0003143
73 | 0.0047296 | 0.0011853
74 | 0.00048826 | 0.00012237
75 | 0.006025 | 0.00151
76 | 0.0005048 | 0.00012651
77 | 0.0015416 | 0.00038637
78 | 0.00059076 | 0.00014806
79 | 0.00053364 | 0.00013374
80 | 0.00079787 | 0.00019996
81 | 0.0016715 | 0.00041892
82 | 0.00042139 | 0.00010561
83 | 0.0012992 | 0.0003256
84 | 0.00087842 | 0.00022015
85 | 0.0036004 | 0.00090234
86 | 0.0021867 | 0.00054803
87 | 0.0013755 | 0.00034474
88 | 0.00054395 | 0.00013633
89 | 0.0016847 | 0.00042222
90 | 0.0012106 | 0.00030341
91 | 0.0018901 | 0.0004737
92 | 0.0015988 | 0.00040069
93 | 0.00147 | 0.00036841
94 | 0.0014301 | 0.00035841
95 | 0.0026419 | 0.00066212
96 | 0.0011794 | 0.0002956
97 | 0.0021981 | 0.00055088
98 | 0.0019741 | 0.00049475
99 | 0.0023778 | 0.00059594
100 | 0.0029162 | 0.00073087
101 | 0.0008948 | 0.00022426
102 | 0.0023269 | 0.00058317
103 | 0.0011805 | 0.00029587
104 | 0.00040985 | 0.00010272
105 | 0.002136 | 0.00053533

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1