## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2465-4_1_1_node_256 | 0.4 | n |  | TRUE
1 | bus_LV_2465-4_1_1_node_255 | 0.4 | n |  | TRUE
2 | bus_LV_2465-4_1_1_node_266 | 0.4 | n |  | TRUE
3 | bus_LV_2465-4_1_1_node_257 | 0.4 | n |  | TRUE
4 | bus_LV_2465-4_1_1_node_258 | 0.4 | n |  | TRUE
5 | bus_LV_2465-4_1_1_node_259 | 0.4 | n |  | TRUE
6 | bus_LV_2465-4_1_1_node_260 | 0.4 | n |  | TRUE
7 | bus_LV_2465-4_1_1_node_261 | 0.4 | n |  | TRUE
8 | bus_LV_2465-4_1_1_node_262 | 0.4 | n |  | TRUE
9 | bus_LV_2465-4_1_1_node_247 | 0.4 | n |  | TRUE
10 | bus_LV_2465-4_1_1_node_275 | 0.4 | n |  | TRUE
11 | bus_LV_2465-4_1_1_node_274 | 0.4 | n |  | TRUE
12 | bus_LV_2465-4_1_1_node_276 | 0.4 | n |  | TRUE
13 | bus_LV_2465-4_1_1_node_263 | 0.4 | n |  | TRUE
14 | bus_LV_2465-4_1_1_node_254 | 0.4 | n |  | TRUE
15 | bus_LV_2465-4_1_1_node_264 | 0.4 | n |  | TRUE
16 | bus_LV_2465-4_1_1_node_265 | 0.4 | n |  | TRUE
17 | bus_LV_2465-4_1_1_node_252 | 0.4 | n |  | TRUE
18 | bus_LV_2465-4_1_1_node_267 | 0.4 | n |  | TRUE
19 | bus_LV_2465-4_1_1_node_284 | 0.4 | n |  | TRUE
20 | bus_LV_2465-4_1_1_node_280 | 0.4 | n |  | TRUE
21 | bus_LV_2465-4_1_1_node_268 | 0.4 | n |  | TRUE
22 | bus_LV_2465-4_1_1_node_269 | 0.4 | n |  | TRUE
23 | bus_LV_2465-4_1_1_node_253 | 0.4 | n |  | TRUE
24 | bus_LV_2465-4_1_1_node_270 | 0.4 | n |  | TRUE
25 | bus_LV_2465-4_1_1_node_273 | 0.4 | n |  | TRUE
26 | bus_LV_2465-4_1_1_node_271 | 0.4 | n |  | TRUE
27 | bus_LV_2465-4_1_1_node_279 | 0.4 | n |  | TRUE
28 | bus_LV_2465-4_1_1_node_272 | 0.4 | n |  | TRUE
29 | bus_LV_2465-4_1_1_node_283 | 0.4 | n |  | TRUE
30 | bus_LV_2465-4_1_1_node_277 | 0.4 | n |  | TRUE
31 | bus_LV_2465-4_1_1_node_278 | 0.4 | n |  | TRUE
32 | bus_LV_2465-4_1_1_node_281 | 0.4 | n |  | TRUE
33 | bus_LV_2465-4_1_1_node_90 | 0.4 | n |  | TRUE
34 | bus_LV_2465-4_1_1_node_282 | 0.4 | n |  | TRUE
35 | bus_LV_2465-4_1_1_node_60 | 0.4 | n |  | TRUE
36 | bus_LV_2465-4_1_1_node_61 | 0.4 | n |  | TRUE
37 | bus_LV_2465-4_1_1_node_62 | 0.4 | n |  | TRUE
38 | bus_LV_2465-4_1_1_node_63 | 0.4 | n |  | TRUE
39 | bus_LV_2465-4_1_1_node_64 | 0.4 | n |  | TRUE
40 | bus_LV_2465-4_1_1_node_86 | 0.4 | n |  | TRUE
41 | bus_LV_2465-4_1_1_node_83 | 0.4 | n |  | TRUE
42 | bus_LV_2465-4_1_1_node_84 | 0.4 | n |  | TRUE
43 | bus_LV_2465-4_1_1_node_123 | 0.4 | n |  | TRUE
44 | bus_LV_2465-4_1_1_node_89 | 0.4 | n |  | TRUE
45 | bus_LV_2465-4_1_1_node_91 | 0.4 | n |  | TRUE
46 | bus_LV_2465-4_1_1_node_124 | 0.4 | n |  | TRUE
47 | bus_LV_2465-4_1_1_node_250 | 0.4 | n |  | TRUE
48 | bus_LV_2465-4_1_1_node_251 | 0.4 | n |  | TRUE
49 | bus_LV_2465-4_1_1_node_249 | 0.4 | n |  | TRUE
50 | bus_LV_2465-4_1_1_node_240 | 0.4 | n |  | TRUE
51 | bus_LV_2465-4_1_1_node_241 | 0.4 | n |  | TRUE
52 | bus_LV_2465-4_1_1_node_243 | 0.4 | n |  | TRUE
53 | bus_LV_2465-4_1_1_node_244 | 0.4 | n |  | TRUE
54 | bus_LV_2465-4_1_1_node_246 | 0.4 | n |  | TRUE
55 | bus_LV_2465-4_1_1_node_245 | 0.4 | n |  | TRUE
56 | bus_LV_2465-4_1_1_node_248 | 0.4 | n |  | TRUE
57 | bus_MV_0_node_277 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2465-4_1_1_load_255 | 1 | 0.0013691 | 0.00034314 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2465-4_1_1_load_266 | 2 | 0.0023306 | 0.00058409 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2465-4_1_1_load_257 | 3 | 0.0013321 | 0.00033386 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2465-4_1_1_load_258 | 4 | 0.00058251 | 0.00014599 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2465-4_1_1_load_260 | 6 | 0.0014682 | 0.00036796 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2465-4_1_1_load_247 | 9 | 0.0014809 | 0.00037116 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2465-4_1_1_load_275 | 10 | 0.00048772 | 0.00012223 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2465-4_1_1_load_274 | 11 | 0.0015988 | 0.0004007 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2465-4_1_1_load_276 | 12 | 0.0012193 | 0.00030559 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2465-4_1_1_load_263 | 13 | 0.0019665 | 0.00049285 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2465-4_1_1_load_254 | 14 | 0.0012769 | 0.00032001 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2465-4_1_1_load_264 | 15 | 0.001817 | 0.00045538 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2465-4_1_1_load_265 | 16 | 0.0018732 | 0.00046947 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2465-4_1_1_load_284 | 19 | 0.00041018 | 0.0001028 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2465-4_1_1_load_280 | 20 | 0.00049623 | 0.00012437 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2465-4_1_1_load_268 | 21 | 0.00065543 | 0.00016427 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2465-4_1_1_load_269 | 22 | 0.0012095 | 0.00030314 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2465-4_1_1_load_271 | 26 | 0.00048876 | 0.00012249 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2465-4_1_1_load_279 | 27 | 0.00060717 | 0.00015217 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2465-4_1_1_load_283 | 29 | 0.00018975 | 4.7556e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2465-4_1_1_load_278 | 31 | 0.00058325 | 0.00014618 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2465-4_1_1_load_282 | 34 | 0.0011412 | 0.000286 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2465-4_1_1_load_60 | 35 | 0.0021685 | 0.00054347 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2465-4_1_1_load_61 | 36 | 0.00063307 | 0.00015866 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2465-4_1_1_load_62 | 37 | 0.00065014 | 0.00016294 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2465-4_1_1_load_63 | 38 | 0.00066987 | 0.00016788 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2465-4_1_1_load_83 | 41 | 0.00046437 | 0.00011638 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2465-4_1_1_load_84 | 42 | 0.00064884 | 0.00016262 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2465-4_1_1_load_89 | 44 | 0.00017953 | 4.4995e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2465-4_1_1_load_91 | 45 | 0.00070032 | 0.00017552 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2465-4_1_1_load_124 | 46 | 0.0003325 | 8.3333e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2465-4_1_1_load_251 | 48 | 0.0015624 | 0.00039156 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2465-4_1_1_load_249 | 49 | 0.00029886 | 7.4901e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2465-4_1_1_load_240 | 50 | 0.00088432 | 0.00022163 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2465-4_1_1_load_241 | 51 | 0.00064976 | 0.00016285 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2465-4_1_1_load_243 | 52 | 0.00059881 | 0.00015008 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2465-4_1_1_load_246 | 54 | 0.00089179 | 0.0002235 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2465-4_1_1_load_248 | 56 | 0.0016594 | 0.00041589 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2465-4_1_1_line_0 |  | 0 | 1 | 0.036421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2465-4_1_1_line_1 |  | 0 | 2 | 0.041592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2465-4_1_1_line_2 |  | 1 | 56 | 0.027378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2465-4_1_1_line_3 |  | 2 | 17 | 0.068102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2465-4_1_1_line_4 |  | 3 | 4 | 0.016863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2465-4_1_1_line_5 |  | 3 | 5 | 0.0092474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2465-4_1_1_line_6 |  | 4 | 6 | 0.011026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2465-4_1_1_line_7 |  | 5 | 7 | 0.045768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2465-4_1_1_line_8 |  | 5 | 8 | 0.019883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2465-4_1_1_line_9 |  | 6 | 9 | 0.067433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2465-4_1_1_line_10 |  | 7 | 10 | 0.010965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2465-4_1_1_line_11 |  | 7 | 11 | 0.030373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2465-4_1_1_line_12 |  | 8 | 12 | 0.0034661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2465-4_1_1_line_13 |  | 9 | 53 | 0.088549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2465-4_1_1_line_14 |  | 10 | 16 | 0.011529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2465-4_1_1_line_15 |  | 12 | 30 | 0.20171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2465-4_1_1_line_16 |  | 13 | 14 | 0.018697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2465-4_1_1_line_17 |  | 13 | 15 | 0.010504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2465-4_1_1_line_18 |  | 14 | 52 | 0.013826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2465-4_1_1_line_19 |  | 15 | 16 | 0.0089676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2465-4_1_1_line_20 |  | 17 | 21 | 0.030237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2465-4_1_1_line_21 |  | 17 | 47 | 0.087759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2465-4_1_1_line_22 |  | 18 | 19 | 0.015771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2465-4_1_1_line_23 |  | 18 | 20 | 0.34402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2465-4_1_1_line_24 |  | 19 | 28 | 0.038342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2465-4_1_1_line_25 |  | 20 | 32 | 0.053751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2465-4_1_1_line_26 |  | 22 | 23 | 0.072337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2465-4_1_1_line_27 |  | 22 | 24 | 0.13018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2465-4_1_1_line_28 |  | 23 | 47 | 0.084936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2465-4_1_1_line_29 |  | 23 | 26 | 0.017667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2465-4_1_1_line_30 |  | 24 | 25 | 0.045694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2465-4_1_1_line_31 |  | 25 | 28 | 0.013679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2465-4_1_1_line_32 |  | 26 | 27 | 0.010617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2465-4_1_1_line_33 |  | 27 | 31 | 0.027348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2465-4_1_1_line_34 |  | 28 | 29 | 0.023758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2465-4_1_1_line_35 |  | 29 | 34 | 0.019706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2465-4_1_1_line_36 |  | 32 | 33 | 0.5245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2465-4_1_1_line_37 |  | 33 | 45 | 0.0086855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2465-4_1_1_line_38 |  | 33 | 44 | 0.024633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2465-4_1_1_line_39 |  | 35 | 36 | 0.014768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2465-4_1_1_line_40 |  | 35 | 37 | 0.0092435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2465-4_1_1_line_41 |  | 36 | 38 | 9.015e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2465-4_1_1_line_42 |  | 37 | 39 | 0.033194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2465-4_1_1_line_43 |  | 39 | 40 | 0.067245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2465-4_1_1_line_44 |  | 40 | 43 | 0.12442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2465-4_1_1_line_45 |  | 40 | 42 | 0.032418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2465-4_1_1_line_46 |  | 41 | 42 | 0.02843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2465-4_1_1_line_47 |  | 43 | 46 | 0.057893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2465-4_1_1_line_48 |  | 45 | 46 | 0.00035504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2465-4_1_1_line_49 |  | 47 | 49 | 0.015883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2465-4_1_1_line_50 |  | 48 | 49 | 0.011993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2465-4_1_1_line_51 |  | 50 | 51 | 0.0078335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2465-4_1_1_line_52 |  | 51 | 52 | 0.0073646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2465-4_1_1_line_53 |  | 53 | 54 | 0.025219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2465-4_1_1_line_54 |  | 54 | 55 | 0.0078925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2465-4_1_1_line_55 |  | 55 | 56 | 0.029991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2465-4_1_1_trafo_277 | 0.63 MVA 20/0.4 kV | 57 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2604167.9032 | 1218957.1046 | 2604135.9978 | 1218939.5384
1 | 2604167.9032 | 1218957.1046 | 2604197.7592 | 1218974.4463 | 2604203.354 | 1218978.7598
2 | 2604112.0142 | 1218926.3337 | 2604135.9978 | 1218939.5384
3 | 2604249.1021 | 1219028.7019 | 2604225.6754 | 1218998.3349 | 2604215.1652 | 1218987.866 | 2604203.354 | 1218978.7598
4 | 2603945.0663 | 1218984.5735 | 2603945.0493 | 1218967.7106
5 | 2603945.0756 | 1218993.8209 | 2603945.0663 | 1218984.5735
6 | 2603945.0493 | 1218967.7106 | 2603945.0382 | 1218956.6842
7 | 2603945.0756 | 1218993.8209 | 2603911.7982 | 1218997.5015 | 2603899.4059 | 1218998.3384
8 | 2603942.5966 | 1219013.4305 | 2603943.8741 | 1219009.4179 | 2603944.5289 | 1219006.0387 | 2603944.8826 | 1218998.9571 | 2603945.0756 | 1218993.8209
9 | 2603972.804 | 1218910.2743 | 2603970.2558 | 1218909.8116 | 2603964.8228 | 1218909.23 | 2603961.2711 | 1218909.5945 | 2603956.9906 | 1218910.5923 | 2603953.2712 | 1218912.2241 | 2603950.181 | 1218914.7013 | 2603947.3254 | 1218918.3126 | 2603945.8359 | 1218921.6135 | 2603945.0065 | 1218925.1706 | 2603945.0382 | 1218956.6842
10 | 2603899.4059 | 1218998.3384 | 2603905.3701 | 1218989.1377
11 | 2603899.4059 | 1218998.3384 | 2603892.8455 | 1219004.5822 | 2603883.5836 | 1219011.0244 | 2603877.2545 | 1219018.8104
12 | 2603942.5966 | 1219013.4305 | 2603941.4277 | 1219016.6936
13 | 2604053.1411 | 1218903.9631 | 2604052.2433 | 1218907.4868 | 2604050.3361 | 1218911.2321 | 2604048.217 | 1218914.0434 | 2604045.3624 | 1218915.9981 | 2604042.1971 | 1218917.4302 | 2604036.1863 | 1218918.5601 | 2604030.3959 | 1218919.0677 | 2604023.4982 | 1218918.7852 | 2604013.7629 | 1218917.7114 | 2603972.804 | 1218910.2743
14 | 2603905.3701 | 1218989.1377 | 2603906.66 | 1218987.1478 | 2603910.0782 | 1218978.6524
15 | 2603838.0496 | 1219185.0393 | 2603839.5178 | 1219179.1813 | 2603841.8518 | 1219172.1121 | 2603868.476 | 1219104.8461 | 2603872.0097 | 1219096.7326 | 2603875.406 | 1219090.0087 | 2603879.0369 | 1219084.1633 | 2603882.5155 | 1219079.2182 | 2603887.3073 | 1219073.607 | 2603905.4543 | 1219056.5089 | 2603926.3499 | 1219037.0223 | 2603933.4873 | 1219030.2008 | 2603937.801 | 1219024.7783 | 2603939.9131 | 1219020.9219 | 2603941.4277 | 1219016.6936
16 | 2603916.7934 | 1218960.3966 | 2603919.8955 | 1218949.7572 | 2603920.5069 | 1218942.1675
17 | 2603916.7934 | 1218960.3966 | 2603915.1346 | 1218966.0857 | 2603913.4257 | 1218970.333
18 | 2603920.5069 | 1218942.1675 | 2603921.6169 | 1218928.3862
19 | 2603913.4257 | 1218970.333 | 2603910.0782 | 1218978.6524
20 | 2604237.2862 | 1219051.6179 | 2604234.6598 | 1219042.1217 | 2604235.7475 | 1219038.3092 | 2604249.1021 | 1219028.7019
21 | 2604249.1021 | 1219028.7019 | 2604301.2596 | 1219099.3791
22 | 2604386.998 | 1219414.8988 | 2604397.2988 | 1219409.203 | 2604400.7949 | 1219407.2582
23 | 2604386.998 | 1219414.8988 | 2604194.6518 | 1219700.1242
24 | 2604434.5623 | 1219389.1409 | 2604428.4141 | 1219391.8936 | 2604400.7949 | 1219407.2582
25 | 2604208.7017 | 1219749.1969 | 2604200.1578 | 1219738.974 | 2604196.8304 | 1219733.9799 | 2604195.2621 | 1219730.7214 | 2604194.0661 | 1219726.6071 | 2604193.7198 | 1219722.6157 | 2604193.9994 | 1219713.3995 | 2604194.6041 | 1219705.8067 | 2604194.6518 | 1219700.1242
26 | 2604351.7177 | 1219167.7987 | 2604396.0905 | 1219223.8406 | 2604396.5868 | 1219224.5373
27 | 2604462.0993 | 1219336.898 | 2604442.1 | 1219302.4969 | 2604418.9202 | 1219258.7994 | 2604405.8691 | 1219237.5667 | 2604396.5868 | 1219224.5373
28 | 2604351.7177 | 1219167.7987 | 2604301.2596 | 1219099.3791
29 | 2604351.7177 | 1219167.7987 | 2604346.0379 | 1219173.2533 | 2604338.4573 | 1219179.4514
30 | 2604462.0993 | 1219336.898 | 2604459.9024 | 1219342.2995 | 2604457.135 | 1219349.5682 | 2604453.8133 | 1219357.3814 | 2604450.5302 | 1219364.3385 | 2604446.3279 | 1219372.7624 | 2604442.8714 | 1219378.2742
31 | 2604434.5623 | 1219389.1409 | 2604438.352 | 1219384.53 | 2604440.9343 | 1219381.2189 | 2604442.8714 | 1219378.2742
32 | 2604338.4573 | 1219179.4514 | 2604330.2383 | 1219186.1715
33 | 2604309.5113 | 1219203.9928 | 2604317.6037 | 1219196.5018 | 2604330.2383 | 1219186.1715
34 | 2604434.5623 | 1219389.1409 | 2604423.4794 | 1219385.0416 | 2604418.0333 | 1219382.2805 | 2604413.2288 | 1219378.9687
35 | 2604400.4191 | 1219364.1378 | 2604407.6592 | 1219373.9015 | 2604411.7689 | 1219377.9623 | 2604413.2288 | 1219378.9687
36 | 2603759.3972 | 1220019.8011 | 2604208.7017 | 1219749.1969
37 | 2603759.3972 | 1220019.8011 | 2603756.1968 | 1220017.5978 | 2603752.0943 | 1220015.1059
38 | 2603759.3972 | 1220019.8011 | 2603766.1482 | 1220034.4136 | 2603769.7209 | 1220042.166
39 | 2603477.3887 | 1219952.5509 | 2603462.6362 | 1219953.2231
40 | 2603477.3887 | 1219952.5509 | 2603486.6226 | 1219952.1301
41 | 2603462.6362 | 1219953.2231 | 2603462.5462 | 1219953.2272
42 | 2603519.6487 | 1219949.5171 | 2603508.1758 | 1219951.4004 | 2603497.6447 | 1219951.6278 | 2603486.6226 | 1219952.1301
43 | 2603519.6487 | 1219949.5171 | 2603529.5364 | 1219946.7546 | 2603552.9014 | 1219939.5974 | 2603557.2037 | 1219938.9996 | 2603561.5968 | 1219938.702 | 2603570.3978 | 1219938.9962 | 2603578.9022 | 1219940.302 | 2603584.8568 | 1219942.6068
44 | 2603584.8568 | 1219942.6068 | 2603599.2012 | 1219947.5959 | 2603636.4759 | 1219961.9264 | 2603660.5974 | 1219971.2017 | 2603701.0423 | 1219987.0909
45 | 2603584.8568 | 1219942.6068 | 2603577.1469 | 1219974.0946
46 | 2603570.3854 | 1220001.7089 | 2603577.1469 | 1219974.0946
47 | 2603701.0423 | 1219987.0909 | 2603737.6002 | 1220006.5022 | 2603745.0025 | 1220010.7981 | 2603751.7909 | 1220014.9215
48 | 2603751.7909 | 1220014.9215 | 2603752.0943 | 1220015.1059
49 | 2604301.2596 | 1219099.3791 | 2604288.602 | 1219108.9732
50 | 2604279.0445 | 1219116.2175 | 2604288.602 | 1219108.9732
51 | 2603923.57 | 1218913.3763 | 2603922.5577 | 1218916.7067 | 2603922.2082 | 1218921.0453
52 | 2603922.2082 | 1218921.0453 | 2603921.6169 | 1218928.3862
53 | 2604053.1411 | 1218903.9631 | 2604077.1274 | 1218911.7524
54 | 2604084.634 | 1218914.1901 | 2604077.1274 | 1218911.7524
55 | 2604084.634 | 1218914.1901 | 2604105.1476 | 1218922.5532 | 2604112.0142 | 1218926.3337

## bus_geodata
| x | y | coords
0 | 2604167.9032 | 1218957.1046
1 | 2604135.9978 | 1218939.5384
2 | 2604203.354 | 1218978.7598
3 | 2603945.0663 | 1218984.5735
4 | 2603945.0493 | 1218967.7106
5 | 2603945.0756 | 1218993.8209
6 | 2603945.0382 | 1218956.6842
7 | 2603899.4059 | 1218998.3384
8 | 2603942.5966 | 1219013.4305
9 | 2603972.804 | 1218910.2743
10 | 2603905.3701 | 1218989.1377
11 | 2603877.2545 | 1219018.8104
12 | 2603941.4277 | 1219016.6936
13 | 2603916.7934 | 1218960.3966
14 | 2603920.5069 | 1218942.1675
15 | 2603913.4257 | 1218970.333
16 | 2603910.0782 | 1218978.6524
17 | 2604249.1021 | 1219028.7019
18 | 2604386.998 | 1219414.8988
19 | 2604400.7949 | 1219407.2582
20 | 2604194.6518 | 1219700.1242
21 | 2604237.2862 | 1219051.6179
22 | 2604396.5868 | 1219224.5373
23 | 2604351.7177 | 1219167.7987
24 | 2604462.0993 | 1219336.898
25 | 2604442.8714 | 1219378.2742
26 | 2604338.4573 | 1219179.4514
27 | 2604330.2383 | 1219186.1715
28 | 2604434.5623 | 1219389.1409
29 | 2604413.2288 | 1219378.9687
30 | 2603838.0496 | 1219185.0393
31 | 2604309.5113 | 1219203.9928
32 | 2604208.7017 | 1219749.1969
33 | 2603759.3972 | 1220019.8011
34 | 2604400.4191 | 1219364.1378
35 | 2603477.3887 | 1219952.5509
36 | 2603462.6362 | 1219953.2231
37 | 2603486.6226 | 1219952.1301
38 | 2603462.5462 | 1219953.2272
39 | 2603519.6487 | 1219949.5171
40 | 2603584.8568 | 1219942.6068
41 | 2603570.3854 | 1220001.7089
42 | 2603577.1469 | 1219974.0946
43 | 2603701.0423 | 1219987.0909
44 | 2603769.7209 | 1220042.166
45 | 2603752.0943 | 1220015.1059
46 | 2603751.7909 | 1220014.9215
47 | 2604301.2596 | 1219099.3791
48 | 2604279.0445 | 1219116.2175
49 | 2604288.602 | 1219108.9732
50 | 2603923.57 | 1218913.3763
51 | 2603922.2082 | 1218921.0453
52 | 2603921.6169 | 1218928.3862
53 | 2604053.1411 | 1218903.9631
54 | 2604077.1274 | 1218911.7524
55 | 2604084.634 | 1218914.1901
56 | 2604112.0142 | 1218926.3337
57 | 2603838.0496 | 1219185.0393

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98623 | -0.26458 | 0 | 0
1 | 0.98679 | -0.25382 | 0.0013691 | 0.00034314
2 | 0.9856 | -0.27687 | 0.0023306 | 0.00058409
3 | 0.99203 | -0.15254 | 0.0013321 | 0.00033386
4 | 0.99166 | -0.15969 | 0.00058251 | 0.00014599
5 | 0.99224 | -0.1484 | 0 | 0
6 | 0.99142 | -0.16426 | 0.0014682 | 0.00036796
7 | 0.99178 | -0.15744 | 0 | 0
8 | 0.99291 | -0.13558 | 0 | 0
9 | 0.99006 | -0.19048 | 0.0014809 | 0.00037116
10 | 0.99168 | -0.1593 | 0.00048772 | 0.00012223
11 | 0.99173 | -0.1583 | 0.0015988 | 0.0004007
12 | 0.99302 | -0.13335 | 0.0012193 | 0.00030559
13 | 0.99147 | -0.1633 | 0.0019665 | 0.00049285
14 | 0.99142 | -0.16443 | 0.0012769 | 0.00032001
15 | 0.99153 | -0.1623 | 0.001817 | 0.00045538
16 | 0.99158 | -0.16115 | 0.0018732 | 0.00046947
17 | 0.98471 | -0.29419 | 0 | 0
18 | 0.98015 | -0.38341 | 0 | 0
19 | 0.98025 | -0.38141 | 0.00041018 | 0.0001028
20 | 0.97793 | -0.42708 | 0.00049623 | 0.00012437
21 | 0.98469 | -0.29454 | 0.00065543 | 0.00016427
22 | 0.98204 | -0.3463 | 0.0012095 | 0.00030314
23 | 0.98271 | -0.33331 | 0 | 0
24 | 0.98099 | -0.36688 | 0 | 0
25 | 0.98062 | -0.3741 | 0 | 0
26 | 0.98268 | -0.33385 | 0.00048876 | 0.00012249
27 | 0.98267 | -0.33407 | 0.00060717 | 0.00015217
28 | 0.98051 | -0.37627 | 0 | 0
29 | 0.98048 | -0.37684 | 0.00018975 | 4.7556e-05
30 | 1 | 0 | -0.039727 | -0.0097028
31 | 0.98265 | -0.33436 | 0.00058325 | 0.00014618
32 | 0.9776 | -0.43342 | 0 | 0
33 | 0.97446 | -0.4955 | 0 | 0
34 | 0.98046 | -0.37725 | 0.0011412 | 0.000286
35 | 0.9731 | -0.52231 | 0.0021685 | 0.00054347
36 | 0.97308 | -0.52266 | 0.00063307 | 0.00015866
37 | 0.97313 | -0.52172 | 0.00065014 | 0.00016294
38 | 0.97308 | -0.52266 | 0.00066987 | 0.00016788
39 | 0.97326 | -0.5192 | 0 | 0
40 | 0.97351 | -0.5141 | 0 | 0
41 | 0.97347 | -0.51501 | 0.00046437 | 0.00011638
42 | 0.97348 | -0.51476 | 0.00064884 | 0.00016262
43 | 0.97412 | -0.50211 | 0 | 0
44 | 0.97445 | -0.49558 | 0.00017953 | 4.4995e-05
45 | 0.9744 | -0.4965 | 0.00070032 | 0.00017552
46 | 0.9744 | -0.49653 | 0.0003325 | 8.3333e-05
47 | 0.98362 | -0.3155 | 0 | 0
48 | 0.98357 | -0.31637 | 0.0015624 | 0.00039156
49 | 0.98359 | -0.31603 | 0.00029886 | 7.4901e-05
50 | 0.99137 | -0.16527 | 0.00088432 | 0.00022163
51 | 0.99138 | -0.16515 | 0.00064976 | 0.00016285
52 | 0.99139 | -0.16495 | 0.00059881 | 0.00015008
53 | 0.98839 | -0.22267 | 0 | 0
54 | 0.98792 | -0.23186 | 0.00089179 | 0.0002235
55 | 0.98778 | -0.23461 | 0 | 0
56 | 0.98724 | -0.24508 | 0.0016594 | 0.00041589
57 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.016529 | -0.0041585 | 0.016537 | 0.0041635 | 8.498e-06 | 4.9737e-06 | 0.024944 | 0.024944 | 0.024944 | 0.98623 | -0.26458 | 0.98679 | -0.25382 | 6.8527
1 | 0.016529 | 0.0041585 | -0.016519 | -0.0041528 | 9.7044e-06 | 5.6804e-06 | 0.024944 | 0.024944 | 0.024944 | 0.98623 | -0.26458 | 0.9856 | -0.27687 | 6.8528
2 | -0.017906 | -0.0045066 | 0.017914 | 0.0045111 | 7.4892e-06 | 4.4431e-06 | 0.027008 | 0.027008 | 0.027008 | 0.98679 | -0.25382 | 0.98724 | -0.24508 | 7.4199
3 | 0.014188 | 0.0035687 | -0.014177 | -0.0035621 | 1.1724e-05 | 6.6359e-06 | 0.021426 | 0.021426 | 0.021426 | 0.9856 | -0.27687 | 0.98471 | -0.29419 | 5.8862
4 | 0.024091 | 0.0060926 | -0.024082 | -0.0060875 | 8.2661e-06 | 5.0727e-06 | 0.036155 | 0.036155 | 0.036155 | 0.99203 | -0.15254 | 0.99166 | -0.15969 | 9.9327
5 | -0.025423 | -0.0064265 | 0.025428 | 0.0064296 | 5.0479e-06 | 3.1112e-06 | 0.038153 | 0.038153 | 0.038153 | 0.99203 | -0.15254 | 0.99224 | -0.1484 | 10.4816
6 | 0.0235 | 0.0059415 | -0.023495 | -0.0059384 | 5.1469e-06 | 3.1518e-06 | 0.035281 | 0.035281 | 0.035281 | 0.99166 | -0.15969 | 0.99142 | -0.16426 | 9.6926
7 | 0.01116 | 0.0027978 | -0.011156 | -0.0027953 | 4.8078e-06 | 2.4861e-06 | 0.016737 | 0.016737 | 0.016737 | 0.99224 | -0.1484 | 0.99178 | -0.15744 | 4.5981
8 | -0.036588 | -0.0092274 | 0.036611 | 0.0092415 | 2.2465e-05 | 1.4121e-05 | 0.05489 | 0.05489 | 0.05489 | 0.99224 | -0.1484 | 0.99291 | -0.13558 | 15.0796
9 | 0.022027 | 0.0055704 | -0.021999 | -0.0055536 | 2.7668e-05 | 1.6839e-05 | 0.033077 | 0.033078 | 0.033078 | 0.99142 | -0.16426 | 0.99006 | -0.19048 | 9.0873
10 | 0.0095567 | 0.002395 | -0.0095558 | -0.0023946 | 8.4533e-07 | 3.9953e-07 | 0.014338 | 0.014338 | 0.014338 | 0.99178 | -0.15744 | 0.99168 | -0.1593 | 3.9391
11 | 0.0015989 | 0.00040035 | -0.0015988 | -0.0004007 | 6.5539e-08 | -3.4998e-07 | 0.0023987 | 0.0023989 | 0.0023989 | 0.99178 | -0.15744 | 0.99173 | -0.1583 | 0.65903
12 | -0.036611 | -0.0092415 | 0.036615 | 0.009244 | 3.9161e-06 | 2.4615e-06 | 0.05489 | 0.05489 | 0.05489 | 0.99291 | -0.13558 | 0.99302 | -0.13335 | 15.0796
13 | 0.020518 | 0.0051824 | -0.020486 | -0.0051633 | 3.1607e-05 | 1.9092e-05 | 0.030852 | 0.030852 | 0.030852 | 0.99006 | -0.19048 | 0.98839 | -0.22267 | 8.4759
14 | 0.0090681 | 0.0022723 | -0.0090673 | -0.002272 | 8.0041e-07 | 3.6353e-07 | 0.013607 | 0.013607 | 0.013607 | 0.99168 | -0.1593 | 0.99158 | -0.16115 | 3.7381
15 | -0.037834 | -0.0095495 | 0.038077 | 0.0097026 | 0.00024332 | 0.0001531 | 0.056717 | 0.056716 | 0.056717 | 0.99302 | -0.13335 | 1 | 0 | 15.5816
16 | 0.00341 | 0.00085411 | -0.0034098 | -0.00085424 | 1.8363e-07 | -1.2359e-07 | 0.0051176 | 0.0051177 | 0.0051177 | 0.99147 | -0.1633 | 0.99142 | -0.16443 | 1.406
17 | -0.0053765 | -0.001347 | 0.0053767 | 0.001347 | 2.5646e-07 | 2.866e-08 | 0.0080689 | 0.0080689 | 0.0080689 | 0.99147 | -0.1633 | 0.99153 | -0.1623 | 2.2167
18 | 0.002133 | 0.00053423 | -0.0021329 | -0.00053437 | 5.3134e-08 | -1.4428e-07 | 0.0032012 | 0.0032013 | 0.0032013 | 0.99142 | -0.16443 | 0.99139 | -0.16495 | 0.87948
19 | -0.0071937 | -0.0018024 | 0.0071941 | 0.0018025 | 3.9193e-07 | 1.3516e-07 | 0.010796 | 0.010796 | 0.010796 | 0.99153 | -0.1623 | 0.99158 | -0.16115 | 2.9658
20 | 0.00065544 | 0.00016389 | -0.00065543 | -0.00016427 | 1.1122e-08 | -3.7753e-07 | 0.00099031 | 0.00099045 | 0.00099045 | 0.98471 | -0.29419 | 0.98469 | -0.29454 | 0.2721
21 | 0.013521 | 0.0033982 | -0.013507 | -0.0033905 | 1.3744e-05 | 7.6808e-06 | 0.020436 | 0.020436 | 0.020436 | 0.98471 | -0.29419 | 0.98362 | -0.3155 | 5.6143
22 | -0.0069852 | -0.0017504 | 0.0069859 | 0.0017507 | 6.6509e-07 | 2.2686e-07 | 0.010605 | 0.010605 | 0.010605 | 0.98015 | -0.38341 | 0.98025 | -0.38141 | 2.9133
23 | 0.0069852 | 0.0017504 | -0.0069707 | -0.0017455 | 1.451e-05 | 4.9603e-06 | 0.010605 | 0.010606 | 0.010606 | 0.98015 | -0.38341 | 0.97793 | -0.42708 | 2.9138
24 | -0.0073961 | -0.0018535 | 0.0073979 | 0.0018541 | 1.8123e-06 | 6.7641e-07 | 0.011227 | 0.011227 | 0.011227 | 0.98025 | -0.38141 | 0.98051 | -0.37627 | 3.0844
25 | 0.0064745 | 0.0016211 | -0.0064725 | -0.0016205 | 1.9561e-06 | 5.7775e-07 | 0.0098511 | 0.0098513 | 0.0098513 | 0.97793 | -0.42708 | 0.9776 | -0.43342 | 2.7064
26 | -0.0099509 | -0.0024959 | 0.009957 | 0.0024989 | 6.1674e-06 | 3.0313e-06 | 0.015079 | 0.015078 | 0.015079 | 0.98204 | -0.3463 | 0.98271 | -0.33331 | 4.1425
27 | 0.0087413 | 0.0021928 | -0.0087328 | -0.0021889 | 8.5653e-06 | 3.8365e-06 | 0.013246 | 0.013246 | 0.013246 | 0.98204 | -0.3463 | 0.98099 | -0.36688 | 3.6391
28 | -0.011636 | -0.0029191 | 0.011646 | 0.0029244 | 9.8891e-06 | 5.2519e-06 | 0.017621 | 0.01762 | 0.017621 | 0.98271 | -0.33331 | 0.98362 | -0.3155 | 4.8408
29 | 0.0016792 | 0.00042018 | -0.0016792 | -0.00042037 | 4.2826e-08 | -1.9641e-07 | 0.0025425 | 0.0025425 | 0.0025425 | 0.98271 | -0.33331 | 0.98268 | -0.33385 | 0.6985
30 | 0.0087328 | 0.0021889 | -0.0087298 | -0.0021876 | 3.0067e-06 | 1.3476e-06 | 0.013246 | 0.013247 | 0.013247 | 0.98099 | -0.36688 | 0.98062 | -0.3741 | 3.6392
31 | 0.0087298 | 0.0021876 | -0.0087289 | -0.0021872 | 9.0011e-07 | 4.0352e-07 | 0.013247 | 0.013247 | 0.013247 | 0.98062 | -0.3741 | 0.98051 | -0.37627 | 3.6392
32 | 0.0011904 | 0.00029788 | -0.0011904 | -0.00029801 | 1.2935e-08 | -1.2622e-07 | 0.0018024 | 0.0018025 | 0.0018025 | 0.98268 | -0.33385 | 0.98267 | -0.33407 | 0.49519
33 | 0.00058326 | 0.00014583 | -0.00058325 | -0.00014618 | 7.9985e-09 | -3.4133e-07 | 0.00088308 | 0.0008832 | 0.0008832 | 0.98267 | -0.33407 | 0.98265 | -0.33436 | 0.24264
34 | 0.001331 | 0.00033305 | -0.0013309 | -0.00033332 | 3.6343e-08 | -2.7639e-07 | 0.0020197 | 0.0020198 | 0.0020198 | 0.98051 | -0.37627 | 0.98048 | -0.37684 | 0.55488
35 | 0.0011412 | 0.00028577 | -0.0011412 | -0.000286 | 2.2164e-08 | -2.3434e-07 | 0.0017318 | 0.0017319 | 0.0017319 | 0.98048 | -0.37684 | 0.98046 | -0.37725 | 0.4758
36 | 0.0064725 | 0.0016205 | -0.0064534 | -0.0016149 | 1.9093e-05 | 5.6642e-06 | 0.0098513 | 0.0098537 | 0.0098537 | 0.9776 | -0.43342 | 0.97446 | -0.4955 | 2.707
37 | 0.0062739 | 0.0015702 | -0.0062736 | -0.0015701 | 2.989e-07 | 8.31e-08 | 0.0095796 | 0.0095797 | 0.0095797 | 0.97446 | -0.4955 | 0.9744 | -0.4965 | 2.6318
38 | 0.00017953 | 4.4688e-05 | -0.00017953 | -4.4995e-05 | 6.9397e-10 | -3.0642e-07 | 0.00027404 | 0.00027415 | 0.00027415 | 0.97446 | -0.4955 | 0.97445 | -0.49558 | 0.075315
39 | 0.001303 | 0.00032638 | -0.0013029 | -0.00032655 | 2.1983e-08 | -1.6939e-07 | 0.0019924 | 0.0019924 | 0.0019924 | 0.9731 | -0.52231 | 0.97308 | -0.52266 | 0.54737
40 | -0.0034714 | -0.00086984 | 0.0034715 | 0.00086979 | 9.7672e-08 | -5.2325e-08 | 0.0053083 | 0.0053082 | 0.0053083 | 0.9731 | -0.52231 | 0.97313 | -0.52172 | 1.4583
41 | 0.00066987 | 0.00016788 | -0.00066987 | -0.00016788 | 3.4118e-11 | -1.096e-09 | 0.0010243 | 0.0010243 | 0.0010243 | 0.97308 | -0.52266 | 0.97308 | -0.52266 | 0.28141
42 | -0.0041217 | -0.0010327 | 0.0041222 | 0.0010326 | 4.944e-07 | -9.6023e-08 | 0.0063024 | 0.0063022 | 0.0063024 | 0.97313 | -0.52172 | 0.97326 | -0.5192 | 1.7314
43 | -0.0041222 | -0.0010326 | 0.0041232 | 0.0010324 | 1.0015e-06 | -1.949e-07 | 0.0063022 | 0.0063019 | 0.0063022 | 0.97326 | -0.5192 | 0.97351 | -0.5141 | 1.7314
44 | -0.0052364 | -0.0013107 | 0.0052394 | 0.0013111 | 2.9883e-06 | 3.6456e-07 | 0.0080032 | 0.0080027 | 0.0080032 | 0.97351 | -0.5141 | 0.97412 | -0.50211 | 2.1987
45 | 0.0011132 | 0.00027827 | -0.0011132 | -0.00027865 | 3.5191e-08 | -3.8053e-07 | 0.0017013 | 0.0017015 | 0.0017015 | 0.97351 | -0.5141 | 0.97348 | -0.51476 | 0.46744
46 | -0.00046437 | -0.00011638 | 0.00046437 | 0.00011603 | 5.3706e-09 | -3.5002e-07 | 0.00070982 | 0.00070969 | 0.00070982 | 0.97347 | -0.51501 | 0.97348 | -0.51476 | 0.195
47 | -0.0052394 | -0.0013111 | 0.0052408 | 0.0013112 | 1.3903e-06 | 1.6888e-07 | 0.0080027 | 0.0080024 | 0.0080027 | 0.97412 | -0.50211 | 0.9744 | -0.49653 | 2.1985
48 | 0.0055733 | 0.0013946 | -0.0055733 | -0.0013946 | 9.6422e-09 | 1.7488e-09 | 0.0085102 | 0.0085102 | 0.0085102 | 0.9744 | -0.4965 | 0.9744 | -0.49653 | 2.338
49 | 0.0018613 | 0.00046616 | -0.0018612 | -0.00046633 | 4.722e-08 | -1.7137e-07 | 0.0028156 | 0.0028157 | 0.0028157 | 0.98362 | -0.3155 | 0.98359 | -0.31603 | 0.77355
50 | -0.0015624 | -0.00039156 | 0.0015624 | 0.00039143 | 2.5125e-08 | -1.3613e-07 | 0.0023636 | 0.0023636 | 0.0023636 | 0.98357 | -0.31637 | 0.98359 | -0.31603 | 0.64935
51 | -0.00088432 | -0.00022163 | 0.00088432 | 0.00022153 | 5.1753e-09 | -9.7693e-08 | 0.0013273 | 0.0013273 | 0.0013273 | 0.99137 | -0.16527 | 0.99138 | -0.16515 | 0.36465
52 | -0.0015341 | -0.00038438 | 0.0015341 | 0.00038429 | 1.4642e-08 | -8.559e-08 | 0.0023026 | 0.0023025 | 0.0023026 | 0.99138 | -0.16515 | 0.99139 | -0.16495 | 0.63257
53 | 0.020486 | 0.0051633 | -0.020477 | -0.0051579 | 9.0021e-06 | 5.4383e-06 | 0.030852 | 0.030852 | 0.030852 | 0.98839 | -0.22267 | 0.98792 | -0.23186 | 8.4759
54 | 0.019586 | 0.0049344 | -0.019583 | -0.0049328 | 2.5773e-06 | 1.5484e-06 | 0.029509 | 0.029509 | 0.029509 | 0.98792 | -0.23186 | 0.98778 | -0.23461 | 8.1069
55 | 0.019583 | 0.0049328 | -0.019573 | -0.004927 | 9.7937e-06 | 5.8843e-06 | 0.029509 | 0.029509 | 0.029509 | 0.98778 | -0.23461 | 0.98724 | -0.24508 | 8.107

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.039727 | 0.0097028

## res_load
| p_mw | q_mvar
0 | 0.0013691 | 0.00034314
1 | 0.0023306 | 0.00058409
2 | 0.0013321 | 0.00033386
3 | 0.00058251 | 0.00014599
4 | 0.0014682 | 0.00036796
5 | 0.0014809 | 0.00037116
6 | 0.00048772 | 0.00012223
7 | 0.0015988 | 0.0004007
8 | 0.0012193 | 0.00030559
9 | 0.0019665 | 0.00049285
10 | 0.0012769 | 0.00032001
11 | 0.001817 | 0.00045538
12 | 0.0018732 | 0.00046947
13 | 0.00041018 | 0.0001028
14 | 0.00049623 | 0.00012437
15 | 0.00065543 | 0.00016427
16 | 0.0012095 | 0.00030314
17 | 0.00048876 | 0.00012249
18 | 0.00060717 | 0.00015217
19 | 0.00018975 | 4.7556e-05
20 | 0.00058325 | 0.00014618
21 | 0.0011412 | 0.000286
22 | 0.0021685 | 0.00054347
23 | 0.00063307 | 0.00015866
24 | 0.00065014 | 0.00016294
25 | 0.00066987 | 0.00016788
26 | 0.00046437 | 0.00011638
27 | 0.00064884 | 0.00016262
28 | 0.00017953 | 4.4995e-05
29 | 0.00070032 | 0.00017552
30 | 0.0003325 | 8.3333e-05
31 | 0.0015624 | 0.00039156
32 | 0.00029886 | 7.4901e-05
33 | 0.00088432 | 0.00022163
34 | 0.00064976 | 0.00016285
35 | 0.00059881 | 0.00015008
36 | 0.00089179 | 0.0002235
37 | 0.0016594 | 0.00041589

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1