## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2493-6_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2493-6_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2493-6_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2493-6_0_5_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_2493-6_0_5_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_2493-6_0_5_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_2493-6_0_5_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_2493-6_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2493-6_0_5_node_138 | 0.4 | n |  | TRUE
9 | bus_LV_2493-6_0_5_node_118 | 0.4 | n |  | TRUE
10 | bus_LV_2493-6_0_5_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_2493-6_0_5_node_116 | 0.4 | n |  | TRUE
12 | bus_LV_2493-6_0_5_node_117 | 0.4 | n |  | TRUE
13 | bus_LV_2493-6_0_5_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2493-6_0_5_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_2493-6_0_5_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_2493-6_0_5_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_2493-6_0_5_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_2493-6_0_5_node_131 | 0.4 | n |  | TRUE
19 | bus_LV_2493-6_0_5_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_2493-6_0_5_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_2493-6_0_5_node_132 | 0.4 | n |  | TRUE
22 | bus_LV_2493-6_0_5_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_2493-6_0_5_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_2493-6_0_5_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2493-6_0_5_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_2493-6_0_5_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_2493-6_0_5_node_45 | 0.4 | n |  | TRUE
28 | bus_LV_2493-6_0_5_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_2493-6_0_5_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_2493-6_0_5_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_2493-6_0_5_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_2493-6_0_5_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_2493-6_0_5_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_2493-6_0_5_node_133 | 0.4 | n |  | TRUE
35 | bus_LV_2493-6_0_5_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_2493-6_0_5_node_148 | 0.4 | n |  | TRUE
37 | bus_LV_2493-6_0_5_node_134 | 0.4 | n |  | TRUE
38 | bus_LV_2493-6_0_5_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_2493-6_0_5_node_145 | 0.4 | n |  | TRUE
40 | bus_LV_2493-6_0_5_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_2493-6_0_5_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_2493-6_0_5_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_2493-6_0_5_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_2493-6_0_5_node_144 | 0.4 | n |  | TRUE
45 | bus_LV_2493-6_0_5_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_2493-6_0_5_node_146 | 0.4 | n |  | TRUE
47 | bus_LV_2493-6_0_5_node_46 | 0.4 | n |  | TRUE
48 | bus_LV_2493-6_0_5_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_2493-6_0_5_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_2493-6_0_5_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_2493-6_0_5_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_2493-6_0_5_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_2493-6_0_5_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_2493-6_0_5_node_99 | 0.4 | n |  | TRUE
55 | bus_LV_2493-6_0_5_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_2493-6_0_5_node_101 | 0.4 | n |  | TRUE
57 | bus_LV_2493-6_0_5_node_62 | 0.4 | n |  | TRUE
58 | bus_LV_2493-6_0_5_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_2493-6_0_5_node_104 | 0.4 | n |  | TRUE
60 | bus_LV_2493-6_0_5_node_97 | 0.4 | n |  | TRUE
61 | bus_LV_2493-6_0_5_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_2493-6_0_5_node_161 | 0.4 | n |  | TRUE
63 | bus_LV_2493-6_0_5_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_2493-6_0_5_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_2493-6_0_5_node_102 | 0.4 | n |  | TRUE
66 | bus_LV_2493-6_0_5_node_149 | 0.4 | n |  | TRUE
67 | bus_LV_2493-6_0_5_node_152 | 0.4 | n |  | TRUE
68 | bus_LV_2493-6_0_5_node_130 | 0.4 | n |  | TRUE
69 | bus_LV_2493-6_0_5_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_2493-6_0_5_node_59 | 0.4 | n |  | TRUE
71 | bus_LV_2493-6_0_5_node_158 | 0.4 | n |  | TRUE
72 | bus_LV_2493-6_0_5_node_159 | 0.4 | n |  | TRUE
73 | bus_LV_2493-6_0_5_node_42 | 0.4 | n |  | TRUE
74 | bus_LV_2493-6_0_5_node_43 | 0.4 | n |  | TRUE
75 | bus_LV_2493-6_0_5_node_51 | 0.4 | n |  | TRUE
76 | bus_LV_2493-6_0_5_node_103 | 0.4 | n |  | TRUE
77 | bus_LV_2493-6_0_5_node_56 | 0.4 | n |  | TRUE
78 | bus_LV_2493-6_0_5_node_57 | 0.4 | n |  | TRUE
79 | bus_LV_2493-6_0_5_node_58 | 0.4 | n |  | TRUE
80 | bus_LV_2493-6_0_5_node_60 | 0.4 | n |  | TRUE
81 | bus_LV_2493-6_0_5_node_147 | 0.4 | n |  | TRUE
82 | bus_LV_2493-6_0_5_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_2493-6_0_5_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_2493-6_0_5_node_71 | 0.4 | n |  | TRUE
85 | bus_LV_2493-6_0_5_node_85 | 0.4 | n |  | TRUE
86 | bus_LV_2493-6_0_5_node_66 | 0.4 | n |  | TRUE
87 | bus_LV_2493-6_0_5_node_83 | 0.4 | n |  | TRUE
88 | bus_LV_2493-6_0_5_node_129 | 0.4 | n |  | TRUE
89 | bus_LV_2493-6_0_5_node_69 | 0.4 | n |  | TRUE
90 | bus_LV_2493-6_0_5_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_2493-6_0_5_node_70 | 0.4 | n |  | TRUE
92 | bus_LV_2493-6_0_5_node_72 | 0.4 | n |  | TRUE
93 | bus_LV_2493-6_0_5_node_82 | 0.4 | n |  | TRUE
94 | bus_LV_2493-6_0_5_node_80 | 0.4 | n |  | TRUE
95 | bus_LV_2493-6_0_5_node_73 | 0.4 | n |  | TRUE
96 | bus_LV_2493-6_0_5_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_2493-6_0_5_node_76 | 0.4 | n |  | TRUE
98 | bus_LV_2493-6_0_5_node_89 | 0.4 | n |  | TRUE
99 | bus_LV_2493-6_0_5_node_90 | 0.4 | n |  | TRUE
100 | bus_LV_2493-6_0_5_node_77 | 0.4 | n |  | TRUE
101 | bus_LV_2493-6_0_5_node_78 | 0.4 | n |  | TRUE
102 | bus_LV_2493-6_0_5_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_2493-6_0_5_node_114 | 0.4 | n |  | TRUE
104 | bus_LV_2493-6_0_5_node_79 | 0.4 | n |  | TRUE
105 | bus_LV_2493-6_0_5_node_81 | 0.4 | n |  | TRUE
106 | bus_LV_2493-6_0_5_node_84 | 0.4 | n |  | TRUE
107 | bus_LV_2493-6_0_5_node_86 | 0.4 | n |  | TRUE
108 | bus_LV_2493-6_0_5_node_87 | 0.4 | n |  | TRUE
109 | bus_LV_2493-6_0_5_node_92 | 0.4 | n |  | TRUE
110 | bus_LV_2493-6_0_5_node_112 | 0.4 | n |  | TRUE
111 | bus_LV_2493-6_0_5_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_2493-6_0_5_node_94 | 0.4 | n |  | TRUE
113 | bus_LV_2493-6_0_5_node_95 | 0.4 | n |  | TRUE
114 | bus_LV_2493-6_0_5_node_125 | 0.4 | n |  | TRUE
115 | bus_LV_2493-6_0_5_node_126 | 0.4 | n |  | TRUE
116 | bus_LV_2493-6_0_5_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_2493-6_0_5_node_105 | 0.4 | n |  | TRUE
118 | bus_LV_2493-6_0_5_node_106 | 0.4 | n |  | TRUE
119 | bus_LV_2493-6_0_5_node_107 | 0.4 | n |  | TRUE
120 | bus_LV_2493-6_0_5_node_108 | 0.4 | n |  | TRUE
121 | bus_LV_2493-6_0_5_node_109 | 0.4 | n |  | TRUE
122 | bus_LV_2493-6_0_5_node_110 | 0.4 | n |  | TRUE
123 | bus_LV_2493-6_0_5_node_111 | 0.4 | n |  | TRUE
124 | bus_LV_2493-6_0_5_node_113 | 0.4 | n |  | TRUE
125 | bus_LV_2493-6_0_5_node_115 | 0.4 | n |  | TRUE
126 | bus_LV_2493-6_0_5_node_150 | 0.4 | n |  | TRUE
127 | bus_LV_2493-6_0_5_node_136 | 0.4 | n |  | TRUE
128 | bus_LV_2493-6_0_5_node_155 | 0.4 | n |  | TRUE
129 | bus_LV_2493-6_0_5_node_157 | 0.4 | n |  | TRUE
130 | bus_LV_2493-6_0_5_node_119 | 0.4 | n |  | TRUE
131 | bus_LV_2493-6_0_5_node_120 | 0.4 | n |  | TRUE
132 | bus_LV_2493-6_0_5_node_121 | 0.4 | n |  | TRUE
133 | bus_LV_2493-6_0_5_node_122 | 0.4 | n |  | TRUE
134 | bus_LV_2493-6_0_5_node_123 | 0.4 | n |  | TRUE
135 | bus_LV_2493-6_0_5_node_124 | 0.4 | n |  | TRUE
136 | bus_LV_2493-6_0_5_node_137 | 0.4 | n |  | TRUE
137 | bus_LV_2493-6_0_5_node_153 | 0.4 | n |  | TRUE
138 | bus_LV_2493-6_0_5_node_135 | 0.4 | n |  | TRUE
139 | bus_LV_2493-6_0_5_node_154 | 0.4 | n |  | TRUE
140 | bus_LV_2493-6_0_5_node_127 | 0.4 | n |  | TRUE
141 | bus_LV_2493-6_0_5_node_128 | 0.4 | n |  | TRUE
142 | bus_LV_2493-6_0_5_node_156 | 0.4 | n |  | TRUE
143 | bus_LV_2493-6_0_5_node_143 | 0.4 | n |  | TRUE
144 | bus_LV_2493-6_0_5_node_139 | 0.4 | n |  | TRUE
145 | bus_LV_2493-6_0_5_node_140 | 0.4 | n |  | TRUE
146 | bus_LV_2493-6_0_5_node_141 | 0.4 | n |  | TRUE
147 | bus_LV_2493-6_0_5_node_142 | 0.4 | n |  | TRUE
148 | bus_LV_2493-6_0_5_node_151 | 0.4 | n |  | TRUE
149 | bus_MV_291_1_node_64 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2493-6_0_5_load_0 | 0 | 0.001518 | 0.00038044 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2493-6_0_5_load_1 | 1 | 0.0011766 | 0.00029489 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2493-6_0_5_load_3 | 2 | 0.0015004 | 0.00037604 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2493-6_0_5_load_5 | 3 | 0.00097269 | 0.00024378 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2493-6_0_5_load_6 | 4 | 0.0039138 | 0.00098089 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2493-6_0_5_load_8 | 5 | 0.0017659 | 0.00044259 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2493-6_0_5_load_9 | 6 | 0.0029135 | 0.00073019 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2493-6_0_5_load_7 | 7 | 0.0032005 | 0.00080213 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2493-6_0_5_load_138 | 8 | 0.0026356 | 0.00066053 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2493-6_0_5_load_118 | 9 | 0.001798 | 0.00045061 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2493-6_0_5_load_10 | 10 | 0.0018731 | 0.00046945 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2493-6_0_5_load_11 | 13 | 0.0011159 | 0.00027967 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2493-6_0_5_load_12 | 14 | 0.0020859 | 0.00052278 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2493-6_0_5_load_13 | 15 | 0.0020077 | 0.00050318 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2493-6_0_5_load_14 | 16 | 0.0016155 | 0.00040488 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2493-6_0_5_load_131 | 18 | 0.0030881 | 0.00077394 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2493-6_0_5_load_17 | 19 | 0.0091675 | 0.0022976 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2493-6_0_5_load_27 | 20 | 0.0014053 | 0.0003522 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2493-6_0_5_load_132 | 21 | 0.0016095 | 0.00040338 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2493-6_0_5_load_16 | 22 | 0.0023162 | 0.00058049 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2493-6_0_5_load_19 | 25 | 0.0020508 | 0.00051398 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2493-6_0_5_load_20 | 26 | 0.0037286 | 0.00093449 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2493-6_0_5_load_45 | 27 | 0.0053816 | 0.0013487 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2493-6_0_5_load_22 | 29 | 0.009185 | 0.002302 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2493-6_0_5_load_21 | 30 | 0.0030414 | 0.00076225 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2493-6_0_5_load_25 | 32 | 0.0021846 | 0.0005475 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2493-6_0_5_load_133 | 34 | 0.0023608 | 0.00059168 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2493-6_0_5_load_148 | 36 | 0.010096 | 0.0025304 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2493-6_0_5_load_134 | 37 | 0.0025244 | 0.00063267 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2493-6_0_5_load_30 | 38 | 0.0019968 | 0.00050045 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2493-6_0_5_load_29 | 40 | 0.0007701 | 0.000193 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2493-6_0_5_load_34 | 42 | 0.00078436 | 0.00019658 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2493-6_0_5_load_33 | 43 | 0.0014275 | 0.00035777 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2493-6_0_5_load_146 | 46 | 0.00085574 | 0.00021447 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2493-6_0_5_load_35 | 49 | 0.0011121 | 0.00027872 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2493-6_0_5_load_101 | 56 | 0.00043675 | 0.00010946 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2493-6_0_5_load_47 | 58 | 0.0038969 | 0.00097665 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2493-6_0_5_load_104 | 59 | 0.0015692 | 0.00039329 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2493-6_0_5_load_97 | 60 | 0.00090195 | 0.00022605 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2493-6_0_5_load_161 | 62 | 0.0022071 | 0.00055314 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2493-6_0_5_load_102 | 65 | 0.00050908 | 0.00012759 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2493-6_0_5_load_152 | 67 | 0.0017129 | 0.00042929 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2493-6_0_5_load_67 | 69 | 0.0010609 | 0.00026589 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2493-6_0_5_load_158 | 71 | 0.0074587 | 0.0018693 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2493-6_0_5_load_159 | 72 | 0.0033776 | 0.0008465 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2493-6_0_5_load_42 | 73 | 0.0014689 | 0.00036814 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2493-6_0_5_load_43 | 74 | 0.0018848 | 0.00047238 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2493-6_0_5_load_51 | 75 | 0.00071141 | 0.0001783 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2493-6_0_5_load_103 | 76 | 0.00029535 | 7.4021e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2493-6_0_5_load_56 | 77 | 0.014121 | 0.003539 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2493-6_0_5_load_57 | 78 | 0.014128 | 0.0035407 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2493-6_0_5_load_60 | 80 | 0.012508 | 0.0031347 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2493-6_0_5_load_147 | 81 | 0.014295 | 0.0035827 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2493-6_0_5_load_71 | 84 | 0.0067496 | 0.0016916 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2493-6_0_5_load_66 | 86 | 0.0052181 | 0.0013078 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2493-6_0_5_load_83 | 87 | 0.010177 | 0.0025505 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2493-6_0_5_load_129 | 88 | 0.0062334 | 0.0015622 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2493-6_0_5_load_69 | 89 | 0.0018527 | 0.00046433 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2493-6_0_5_load_68 | 90 | 0.0031853 | 0.00079831 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2493-6_0_5_load_70 | 91 | 0.0023955 | 0.00060037 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2493-6_0_5_load_72 | 92 | 0.0019162 | 0.00048024 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2493-6_0_5_load_82 | 93 | 0.0028132 | 0.00070506 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2493-6_0_5_load_80 | 94 | 0.0026932 | 0.00067499 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2493-6_0_5_load_73 | 95 | 0.0015814 | 0.00039633 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2493-6_0_5_load_74 | 96 | 0.00082383 | 0.00020647 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2493-6_0_5_load_89 | 98 | 0.00081889 | 0.00020523 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2493-6_0_5_load_90 | 99 | 0.0034254 | 0.0008585 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2493-6_0_5_load_77 | 100 | 0.0025138 | 0.00063001 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2493-6_0_5_load_78 | 101 | 0.0025147 | 0.00063023 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2493-6_0_5_load_91 | 102 | 0.0033599 | 0.00084208 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2493-6_0_5_load_79 | 104 | 0.0032932 | 0.00082535 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2493-6_0_5_load_81 | 105 | 0.0028225 | 0.00070739 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2493-6_0_5_load_87 | 108 | 0.010218 | 0.0025608 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2493-6_0_5_load_92 | 109 | 0.0011091 | 0.00027796 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2493-6_0_5_load_112 | 110 | 0.0022807 | 0.0005716 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2493-6_0_5_load_93 | 111 | 0.0016453 | 0.00041236 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2493-6_0_5_load_94 | 112 | 0.001891 | 0.00047393 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2493-6_0_5_load_95 | 113 | 0.0024201 | 0.00060654 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2493-6_0_5_load_125 | 114 | 0.0030139 | 0.00075534 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2493-6_0_5_load_126 | 115 | 0.0026818 | 0.00067212 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2493-6_0_5_load_96 | 116 | 0.0010323 | 0.00025872 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2493-6_0_5_load_105 | 117 | 0.0030813 | 0.00077225 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2493-6_0_5_load_106 | 118 | 0.0015785 | 0.0003956 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2493-6_0_5_load_107 | 119 | 0.0018715 | 0.00046905 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2493-6_0_5_load_108 | 120 | 0.0042971 | 0.001077 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2493-6_0_5_load_109 | 121 | 0.002738 | 0.0006862 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2493-6_0_5_load_110 | 122 | 0.0014405 | 0.00036102 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2493-6_0_5_load_111 | 123 | 0.0019764 | 0.00049532 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2493-6_0_5_load_113 | 124 | 0.0014617 | 0.00036634 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2493-6_0_5_load_115 | 125 | 0.0018299 | 0.00045861 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2493-6_0_5_load_150 | 126 | 0.0033308 | 0.00083478 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2493-6_0_5_load_136 | 127 | 0.0017292 | 0.00043339 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2493-6_0_5_load_155 | 128 | 0.0020866 | 0.00052295 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2493-6_0_5_load_157 | 129 | 0.00069724 | 0.00017474 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2493-6_0_5_load_119 | 130 | 0.0024666 | 0.00061819 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2493-6_0_5_load_120 | 131 | 0.0019886 | 0.0004984 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2493-6_0_5_load_121 | 132 | 0.0043892 | 0.0011 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2493-6_0_5_load_122 | 133 | 0.0022469 | 0.00056312 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2493-6_0_5_load_123 | 134 | 0.0016532 | 0.00041433 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2493-6_0_5_load_124 | 135 | 0.0037259 | 0.0009338 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2493-6_0_5_load_137 | 136 | 0.0012269 | 0.00030748 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2493-6_0_5_load_153 | 137 | 0.002136 | 0.00053534 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2493-6_0_5_load_135 | 138 | 0.0012118 | 0.00030369 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2493-6_0_5_load_154 | 139 | 0.0014669 | 0.00036764 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2493-6_0_5_load_127 | 140 | 0.0033874 | 0.00084896 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2493-6_0_5_load_128 | 141 | 0.0012013 | 0.00030108 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2493-6_0_5_load_156 | 142 | 0.0014673 | 0.00036774 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2493-6_0_5_load_143 | 143 | 0.0012302 | 0.00030832 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2493-6_0_5_load_139 | 144 | 0.0018781 | 0.0004707 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2493-6_0_5_load_140 | 145 | 0.0012091 | 0.00030304 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2493-6_0_5_load_141 | 146 | 0.0012063 | 0.00030233 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2493-6_0_5_load_142 | 147 | 0.0016088 | 0.00040321 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2493-6_0_5_load_151 | 148 | 0.0019134 | 0.00047954 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 144 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2493-6_0_5_line_0 |  | 0 | 1 | 0.024468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2493-6_0_5_line_1 |  | 1 | 2 | 0.0028642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2493-6_0_5_line_2 |  | 2 | 3 | 0.019146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2493-6_0_5_line_3 |  | 3 | 4 | 0.015445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2493-6_0_5_line_4 |  | 4 | 7 | 0.026715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2493-6_0_5_line_5 |  | 5 | 6 | 0.033455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2493-6_0_5_line_6 |  | 6 | 10 | 0.037307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2493-6_0_5_line_7 |  | 7 | 8 | 0.018772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2493-6_0_5_line_8 |  | 8 | 9 | 0.045117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2493-6_0_5_line_9 |  | 9 | 11 | 0.039386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2493-6_0_5_line_10 |  | 10 | 11 | 0.023219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2493-6_0_5_line_11 |  | 11 | 12 | 0.016822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2493-6_0_5_line_12 |  | 12 | 129 | 0.021003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2493-6_0_5_line_13 |  | 12 | 21 | 0.030998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2493-6_0_5_line_14 |  | 12 | 127 | 0.022802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2493-6_0_5_line_15 |  | 13 | 14 | 0.025945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2493-6_0_5_line_16 |  | 13 | 15 | 0.011089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2493-6_0_5_line_17 |  | 14 | 16 | 0.019467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2493-6_0_5_line_18 |  | 15 | 17 | 0.0025985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2493-6_0_5_line_19 |  | 16 | 18 | 0.016291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2493-6_0_5_line_20 |  | 17 | 19 | 0.026578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_2493-6_0_5_line_21 |  | 17 | 20 | 0.016367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2493-6_0_5_line_22 |  | 18 | 21 | 0.0031598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2493-6_0_5_line_23 |  | 19 | 22 | 0.018011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2493-6_0_5_line_24 |  | 20 | 23 | 0.033382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2493-6_0_5_line_25 |  | 22 | 24 | 0.018356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2493-6_0_5_line_26 |  | 23 | 40 | 0.0047425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2493-6_0_5_line_27 |  | 24 | 25 | 0.013416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2493-6_0_5_line_28 |  | 24 | 26 | 0.00066034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2493-6_0_5_line_29 |  | 25 | 27 | 0.0056578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2493-6_0_5_line_30 |  | 26 | 28 | 0.021856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2493-6_0_5_line_31 |  | 28 | 29 | 0.031466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2493-6_0_5_line_32 |  | 29 | 30 | 0.027073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2493-6_0_5_line_33 |  | 30 | 31 | 0.019403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2493-6_0_5_line_34 |  | 31 | 32 | 0.036929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2493-6_0_5_line_35 |  | 31 | 33 | 0.013157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2493-6_0_5_line_36 |  | 32 | 34 | 0.0098795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2493-6_0_5_line_37 |  | 33 | 35 | 0.003518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2493-6_0_5_line_38 |  | 33 | 36 | 0.01683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2493-6_0_5_line_39 |  | 34 | 37 | 0.017245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2493-6_0_5_line_40 |  | 35 | 38 | 0.021936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2493-6_0_5_line_41 |  | 36 | 39 | 0.01053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_2493-6_0_5_line_42 |  | 37 | 138 | 0.0089115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2493-6_0_5_line_43 |  | 38 | 41 | 0.055249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2493-6_0_5_line_44 |  | 39 | 44 | 0.012601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2493-6_0_5_line_45 |  | 41 | 42 | 0.02681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2493-6_0_5_line_46 |  | 42 | 45 | 0.01361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2493-6_0_5_line_47 |  | 43 | 44 | 0.0067589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2493-6_0_5_line_48 |  | 44 | 46 | 0.024017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_2493-6_0_5_line_49 |  | 45 | 47 | 0.014806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2493-6_0_5_line_50 |  | 45 | 48 | 0.007925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2493-6_0_5_line_51 |  | 46 | 51 | 0.0014473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2493-6_0_5_line_52 |  | 47 | 58 | 0.015332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2493-6_0_5_line_53 |  | 48 | 49 | 0.0075255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2493-6_0_5_line_54 |  | 50 | 51 | 0.019782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_2493-6_0_5_line_55 |  | 50 | 52 | 0.021241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_2493-6_0_5_line_56 |  | 52 | 57 | 0.049017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_2493-6_0_5_line_57 |  | 53 | 54 | 0.055395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2493-6_0_5_line_58 |  | 53 | 55 | 0.039622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2493-6_0_5_line_59 |  | 53 | 56 | 0.01228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2493-6_0_5_line_60 |  | 54 | 59 | 0.030315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2493-6_0_5_line_61 |  | 54 | 60 | 0.018453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2493-6_0_5_line_62 |  | 55 | 62 | 0.026694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2493-6_0_5_line_63 |  | 55 | 64 | 0.044674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2493-6_0_5_line_64 |  | 56 | 65 | 0.013113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2493-6_0_5_line_65 |  | 57 | 69 | 0.045748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2493-6_0_5_line_66 |  | 57 | 70 | 0.025383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2493-6_0_5_line_67 |  | 58 | 64 | 0.021227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2493-6_0_5_line_68 |  | 60 | 116 | 0.014237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2493-6_0_5_line_69 |  | 61 | 62 | 0.013055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2493-6_0_5_line_70 |  | 61 | 63 | 0.027504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2493-6_0_5_line_71 |  | 63 | 75 | 0.0092816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2493-6_0_5_line_72 |  | 63 | 73 | 0.091192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2493-6_0_5_line_73 |  | 65 | 76 | 0.024217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2493-6_0_5_line_74 |  | 66 | 67 | 0.016745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2493-6_0_5_line_75 |  | 66 | 68 | 0.028268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2493-6_0_5_line_76 |  | 67 | 148 | 0.023045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2493-6_0_5_line_77 |  | 68 | 88 | 0.024544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2493-6_0_5_line_78 |  | 68 | 82 | 0.001435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2493-6_0_5_line_79 |  | 69 | 86 | 0.0024412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2493-6_0_5_line_80 |  | 70 | 78 | 0.014177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2493-6_0_5_line_81 |  | 71 | 72 | 0.003567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2493-6_0_5_line_82 |  | 72 | 82 | 0.021819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2493-6_0_5_line_83 |  | 73 | 74 | 0.0055418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2493-6_0_5_line_84 |  | 77 | 78 | 0.021014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2493-6_0_5_line_85 |  | 77 | 79 | 0.0011876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2493-6_0_5_line_86 |  | 79 | 80 | 0.022646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2493-6_0_5_line_87 |  | 80 | 81 | 0.0058242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2493-6_0_5_line_88 |  | 82 | 83 | 0.041421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2493-6_0_5_line_89 |  | 83 | 84 | 0.03588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2493-6_0_5_line_90 |  | 83 | 85 | 0.048519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2493-6_0_5_line_91 |  | 84 | 89 | 0.00087476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2493-6_0_5_line_92 |  | 85 | 87 | 0.0077371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2493-6_0_5_line_93 |  | 87 | 106 | 0.034565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2493-6_0_5_line_94 |  | 88 | 121 | 0.0090458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2493-6_0_5_line_95 |  | 89 | 90 | 0.0099604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2493-6_0_5_line_96 |  | 90 | 91 | 0.02839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2493-6_0_5_line_97 |  | 91 | 92 | 0.0029046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2493-6_0_5_line_98 |  | 92 | 93 | 0.020495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2493-6_0_5_line_99 |  | 93 | 94 | 0.015355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2493-6_0_5_line_100 |  | 94 | 105 | 0.0069169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2493-6_0_5_line_101 |  | 95 | 96 | 0.016773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2493-6_0_5_line_102 |  | 96 | 97 | 0.014732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2493-6_0_5_line_103 |  | 97 | 98 | 0.020579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_2493-6_0_5_line_104 |  | 97 | 99 | 0.037729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_2493-6_0_5_line_105 |  | 98 | 102 | 0.0066023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_2493-6_0_5_line_106 |  | 99 | 103 | 0.031652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_2493-6_0_5_line_107 |  | 100 | 101 | 0.00013346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2493-6_0_5_line_108 |  | 101 | 104 | 0.026614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2493-6_0_5_line_109 |  | 102 | 109 | 0.01474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_2493-6_0_5_line_110 |  | 103 | 110 | 0.019171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_2493-6_0_5_line_111 |  | 104 | 105 | 0.017545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2493-6_0_5_line_112 |  | 106 | 107 | 0.052759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2493-6_0_5_line_113 |  | 107 | 108 | 0.002469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2493-6_0_5_line_114 |  | 109 | 111 | 0.0076478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_2493-6_0_5_line_115 |  | 110 | 123 | 0.00061753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_2493-6_0_5_line_116 |  | 111 | 112 | 0.021658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_2493-6_0_5_line_117 |  | 112 | 113 | 0.0022289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_2493-6_0_5_line_118 |  | 113 | 114 | 0.0061981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_2493-6_0_5_line_119 |  | 114 | 115 | 0.019719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2493-6_0_5_line_120 |  | 115 | 140 | 0.0050119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2493-6_0_5_line_121 |  | 117 | 118 | 0.019687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2493-6_0_5_line_122 |  | 117 | 119 | 0.0014065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2493-6_0_5_line_123 |  | 118 | 120 | 0.0067006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2493-6_0_5_line_124 |  | 119 | 121 | 0.024767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2493-6_0_5_line_125 |  | 120 | 122 | 0.0084151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2493-6_0_5_line_126 |  | 123 | 124 | 0.030267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_2493-6_0_5_line_127 |  | 124 | 125 | 0.0042332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_2493-6_0_5_line_128 |  | 125 | 126 | 0.0065791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_2493-6_0_5_line_129 |  | 126 | 128 | 0.0093921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_2493-6_0_5_line_130 |  | 128 | 139 | 0.007685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_2493-6_0_5_line_131 |  | 130 | 131 | 0.0071498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_2493-6_0_5_line_132 |  | 130 | 132 | 0.011749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_2493-6_0_5_line_133 |  | 131 | 133 | 0.012043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_2493-6_0_5_line_134 |  | 132 | 134 | 0.0073713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_2493-6_0_5_line_135 |  | 133 | 135 | 0.00064228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
136 | LV_2493-6_0_5_line_136 |  | 134 | 136 | 0.020374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
137 | LV_2493-6_0_5_line_137 |  | 135 | 137 | 0.0023617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
138 | LV_2493-6_0_5_line_138 |  | 136 | 138 | 0.00026798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
139 | LV_2493-6_0_5_line_139 |  | 137 | 139 | 0.013568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
140 | LV_2493-6_0_5_line_140 |  | 140 | 141 | 0.0092731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
141 | LV_2493-6_0_5_line_141 |  | 141 | 142 | 0.033757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
142 | LV_2493-6_0_5_line_142 |  | 142 | 143 | 0.0077487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
143 | LV_2493-6_0_5_line_143 |  | 143 | 146 | 0.00011246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
144 | LV_2493-6_0_5_line_144 |  | 144 | 145 | 0.01717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2493-6_0_5_line_145 |  | 144 | 146 | 0.0089125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
146 | LV_2493-6_0_5_line_146 |  | 145 | 147 | 0.0017842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2493-6_0_5_line_147 |  | 147 | 148 | 0.0044341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2493-6_0_5_trafo_139 | 0.63 MVA 20/0.4 kV | 149 | 144 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2638856.8907 | 1247917.7897 | 2638849.0677 | 1247913.2211 | 2638835.6859 | 1247905.5819
1 | 2638835.6859 | 1247905.5819 | 2638833.1985 | 1247904.1619
2 | 2638833.1985 | 1247904.1619 | 2638816.5712 | 1247894.6698
3 | 2638816.5712 | 1247894.6698 | 2638803.4965 | 1247887.2059 | 2638803.1563 | 1247887.0148
4 | 2638803.1563 | 1247887.0148 | 2638779.8639 | 1247873.9322
5 | 2638808.5131 | 1247953.8798 | 2638780.6985 | 1247948.275 | 2638775.7064 | 1247947.3248
6 | 2638739.5887 | 1247938.2404 | 2638748.3239 | 1247941.3701 | 2638765.576 | 1247945.3965 | 2638775.7064 | 1247947.3248
7 | 2638763.4971 | 1247864.7395 | 2638779.8639 | 1247873.9322
8 | 2638735.9385 | 1247891.112 | 2638744.3349 | 1247874.5666 | 2638749.2402 | 1247864.681 | 2638754.0232 | 1247861.9659 | 2638760.1946 | 1247862.8846 | 2638763.4971 | 1247864.7395
9 | 2638719.9544 | 1247927.0978 | 2638733.1043 | 1247896.6968 | 2638735.9385 | 1247891.112
10 | 2638719.9544 | 1247927.0978 | 2638722.9399 | 1247931.3423 | 2638734.8905 | 1247936.557 | 2638739.5887 | 1247938.2404
11 | 2638719.9544 | 1247927.0978 | 2638716.7126 | 1247925.1086 | 2638710.0106 | 1247922.1852 | 2638704.6395 | 1247920.1377
12 | 2638704.6395 | 1247920.1377 | 2638714.0297 | 1247901.3506
13 | 2638704.6395 | 1247920.1377 | 2638694.9681 | 1247915.138 | 2638679.0669 | 1247902.8253
14 | 2638704.6395 | 1247920.1377 | 2638695.827 | 1247941.168
15 | 2638629.557 | 1247860.9294 | 2638644.357 | 1247873.2362 | 2638649.4153 | 1247877.6254
16 | 2638629.557 | 1247860.9294 | 2638629.0342 | 1247860.4947 | 2638620.3633 | 1247854.735
17 | 2638649.4153 | 1247877.6254 | 2638660.0816 | 1247886.8809 | 2638664.1554 | 1247890.3408
18 | 2638618.1988 | 1247853.2972 | 2638620.3633 | 1247854.735
19 | 2638676.572 | 1247900.8865 | 2638664.1554 | 1247890.3408
20 | 2638618.1988 | 1247853.2972 | 2638611.9242 | 1247849.6651 | 2638594.8959 | 1247840.5221
21 | 2638618.1988 | 1247853.2972 | 2638622.8098 | 1247843.3428 | 2638624.9897 | 1247838.4056
22 | 2638676.572 | 1247900.8865 | 2638676.6643 | 1247900.9649 | 2638679.0669 | 1247902.8253
23 | 2638579.1657 | 1247831.7502 | 2638594.4422 | 1247840.2785 | 2638594.8959 | 1247840.5221
24 | 2638638.4167 | 1247807.8432 | 2638635.2577 | 1247815.1497 | 2638624.9897 | 1247838.4056
25 | 2638563.0711 | 1247822.9298 | 2638566.0294 | 1247824.4167 | 2638579.1657 | 1247831.7502
26 | 2638638.4167 | 1247807.8432 | 2638640.2979 | 1247803.4897
27 | 2638563.0711 | 1247822.9298 | 2638569.7105 | 1247811.2716
28 | 2638562.4815 | 1247822.6325 | 2638563.0711 | 1247822.9298
29 | 2638572.5105 | 1247806.3552 | 2638569.7105 | 1247811.2716
30 | 2638542.9658 | 1247812.7925 | 2638562.4815 | 1247822.6325
31 | 2638542.9658 | 1247812.7925 | 2638536.8228 | 1247823.7599 | 2638535.184 | 1247826.0952 | 2638531.4175 | 1247830.4403 | 2638527.7482 | 1247833.7965 | 2638523.6262 | 1247837.1581
32 | 2638501.5393 | 1247852.79 | 2638508.9959 | 1247847.8952 | 2638517.1217 | 1247842.0775 | 2638520.9988 | 1247839.3008 | 2638523.6262 | 1247837.1581
33 | 2638485.6697 | 1247863.9434 | 2638494.6692 | 1247857.3196 | 2638498.9999 | 1247854.457 | 2638501.5393 | 1247852.79
34 | 2638485.6697 | 1247863.9434 | 2638491.2032 | 1247868.9048 | 2638493.1035 | 1247870.496 | 2638503.8 | 1247877.003 | 2638516.1856 | 1247884.5392
35 | 2638476.5161 | 1247873.3681 | 2638480.208 | 1247868.8668 | 2638485.6697 | 1247863.9434
36 | 2638524.6255 | 1247889.6746 | 2638516.1856 | 1247884.5392
37 | 2638476.5161 | 1247873.3681 | 2638473.7969 | 1247871.1268
38 | 2638476.5161 | 1247873.3681 | 2638468.9054 | 1247883.6033 | 2638467.1158 | 1247887.2651
39 | 2638524.6255 | 1247889.6746 | 2638539.3575 | 1247898.6385
40 | 2638473.7969 | 1247871.1268 | 2638469.965 | 1247865.7873 | 2638464.4277 | 1247855.578 | 2638462.6181 | 1247852.2943
41 | 2638462.4919 | 1247896.726 | 2638467.1158 | 1247887.2651
42 | 2638539.3575 | 1247898.6385 | 2638543.3814 | 1247901.0869 | 2638546.995 | 1247903.2299
43 | 2638431.7193 | 1247806.8117 | 2638438.4034 | 1247813.704 | 2638450.4997 | 1247830.3044 | 2638462.6181 | 1247852.2943
44 | 2638462.4919 | 1247896.726 | 2638453.3776 | 1247894.2875 | 2638450.3407 | 1247893.2783
45 | 2638431.7193 | 1247806.8117 | 2638424.1692 | 1247814.6903 | 2638413.3274 | 1247826.3177
46 | 2638403.942 | 1247836.1735 | 2638406.4741 | 1247833.4993 | 2638411.051 | 1247828.7591 | 2638413.3274 | 1247826.3177
47 | 2638450.3407 | 1247893.2783 | 2638451.8711 | 1247886.695
48 | 2638450.3407 | 1247893.2783 | 2638444.3037 | 1247893.7617 | 2638428.5996 | 1247902.4779
49 | 2638403.942 | 1247836.1735 | 2638397.9328 | 1247833.5107 | 2638394.9812 | 1247832.1574 | 2638390.2033 | 1247830.6032
50 | 2638403.942 | 1247836.1735 | 2638398.565 | 1247842.0093
51 | 2638427.3341 | 1247903.1803 | 2638428.5996 | 1247902.4779
52 | 2638390.2033 | 1247830.6032 | 2638382.7922 | 1247829.8548 | 2638377.6799 | 1247829.7995 | 2638374.9308 | 1247830.1455
53 | 2638398.565 | 1247842.0093 | 2638401.1934 | 1247849.0608
54 | 2638410.8078 | 1247914.125 | 2638427.3341 | 1247903.1803
55 | 2638410.8078 | 1247914.125 | 2638393.0007 | 1247925.7842
56 | 2638393.0007 | 1247925.7842 | 2638386.9867 | 1247929.7257 | 2638377.43 | 1247937.2911 | 2638356.361 | 1247958.2465
57 | 2638282.5833 | 1247932.064 | 2638287.1028 | 1247928.0016 | 2638295.8418 | 1247921.9206 | 2638304.2727 | 1247914.4145 | 2638314.4039 | 1247904.4066 | 2638319.2898 | 1247899.7573 | 2638317.4006 | 1247897.5993 | 2638314.8184 | 1247895.1921
58 | 2638314.8184 | 1247895.1921 | 2638324.6505 | 1247885.8939 | 2638334.0066 | 1247876.6482 | 2638343.7206 | 1247868.1053
59 | 2638314.8184 | 1247895.1921 | 2638311.8684 | 1247892.4268 | 2638304.5129 | 1247888.72
60 | 2638282.5833 | 1247932.064 | 2638272.8016 | 1247932.4012 | 2638267.9009 | 1247933.5036 | 2638259.8471 | 1247935.2306 | 2638252.769 | 1247936.8778
61 | 2638282.5833 | 1247932.064 | 2638276.9823 | 1247938.7101 | 2638270.4763 | 1247945.9869
62 | 2638343.7206 | 1247868.1053 | 2638324.9713 | 1247849.105
63 | 2638343.7206 | 1247868.1053 | 2638350.8415 | 1247861.1801 | 2638353.4031 | 1247851.6014 | 2638352.3402 | 1247845.4571 | 2638346.8327 | 1247838.7838 | 2638348.1327 | 1247837.458 | 2638353.7811 | 1247831.6796
64 | 2638304.5129 | 1247888.72 | 2638302.4818 | 1247887.6964 | 2638292.56 | 1247883.3348
65 | 2638356.361 | 1247958.2465 | 2638347.1012 | 1247967.8041 | 2638328.0976 | 1247988.206 | 2638325.068 | 1247991.6134
66 | 2638379.6829 | 1247968.4262 | 2638356.361 | 1247958.2465
67 | 2638353.7811 | 1247831.6796 | 2638355.2552 | 1247831.4445 | 2638359.5753 | 1247831.3835 | 2638363.9186 | 1247831.2337 | 2638371.1271 | 1247830.6243 | 2638374.9308 | 1247830.1455
68 | 2638260.8685 | 1247956.4934 | 2638267.8695 | 1247948.9025 | 2638270.4763 | 1247945.9869
69 | 2638315.5035 | 1247858.0943 | 2638324.9713 | 1247849.105
70 | 2638295.8574 | 1247838.7881 | 2638315.5035 | 1247858.0943
71 | 2638295.8574 | 1247838.7881 | 2638289.5614 | 1247845.6078
72 | 2638295.8574 | 1247838.7881 | 2638278.2407 | 1247749.3138
73 | 2638292.56 | 1247883.3348 | 2638291.8036 | 1247883.0022 | 2638280.6418 | 1247878.3383 | 2638269.7507 | 1247875.3518
74 | 2638450.7501 | 1247934.9752 | 2638465.801 | 1247942.3149
75 | 2638450.7501 | 1247934.9752 | 2638445.3905 | 1247953.2859 | 2638442.811 | 1247962.1084
76 | 2638465.801 | 1247942.3149 | 2638478.6864 | 1247948.5986 | 2638486.4773 | 1247952.4905
77 | 2638442.811 | 1247962.1084 | 2638464.7643 | 1247973.0838
78 | 2638442.811 | 1247962.1084 | 2638442.4019 | 1247963.4844
79 | 2638325.068 | 1247991.6134 | 2638323.446 | 1247993.4378
80 | 2638379.6829 | 1247968.4262 | 2638374.7881 | 1247981.7313
81 | 2638418.9341 | 1247953.8039 | 2638422.2316 | 1247955.1641
82 | 2638442.4019 | 1247963.4844 | 2638422.2316 | 1247955.1641
83 | 2638278.2407 | 1247749.3138 | 2638282.1359 | 1247745.3719
84 | 2638367.5326 | 1248001.4531 | 2638374.7881 | 1247981.7313
85 | 2638367.1225 | 1248002.5676 | 2638367.5326 | 1248001.4531
86 | 2638367.1225 | 1248002.5676 | 2638388.2526 | 1248010.7142
87 | 2638393.6869 | 1248012.8093 | 2638388.2526 | 1248010.7142
88 | 2638433.4782 | 1248003.8866 | 2638434.2177 | 1247999.3106 | 2638435.6806 | 1247990.3142 | 2638439.5831 | 1247973.1169 | 2638442.4019 | 1247963.4844
89 | 2638433.4782 | 1248003.8866 | 2638446.8832 | 1248009.5995 | 2638466.2859 | 1248018.4087
90 | 2638428.6044 | 1248052.1425 | 2638429.5085 | 1248041.975 | 2638430.8044 | 1248027.2737 | 2638431.2444 | 1248022.3066 | 2638432.1568 | 1248012.0279 | 2638433.4782 | 1248003.8866
91 | 2638466.2859 | 1248018.4087 | 2638467.0824 | 1248018.7704
92 | 2638428.6044 | 1248052.1425 | 2638427.9158 | 1248059.8489
93 | 2638424.7369 | 1248094.2676 | 2638425.999 | 1248081.3005 | 2638427.9158 | 1248059.8489
94 | 2638472.8552 | 1247977.1288 | 2638464.7643 | 1247973.0838
95 | 2638476.1517 | 1248022.8881 | 2638467.0824 | 1248018.7704
96 | 2638476.1517 | 1248022.8881 | 2638502.0019 | 1248034.6247
97 | 2638504.6467 | 1248035.8255 | 2638502.0019 | 1248034.6247
98 | 2638523.1255 | 1248044.6592 | 2638518.8801 | 1248042.2879 | 2638504.6467 | 1248035.8255
99 | 2638523.1255 | 1248044.6592 | 2638536.5313 | 1248052.1475
100 | 2638536.5313 | 1248052.1475 | 2638542.57 | 1248055.5206
101 | 2638637.1016 | 1248072.9009 | 2638643.9899 | 1248057.6074
102 | 2638650.0398 | 1248044.1751 | 2638643.9899 | 1248057.6074
103 | 2638650.0398 | 1248044.1751 | 2638632.347 | 1248033.6649
104 | 2638650.0398 | 1248044.1751 | 2638653.9009 | 1248035.728 | 2638666.2086 | 1248010.0873
105 | 2638632.347 | 1248033.6649 | 2638626.6707 | 1248030.2929
106 | 2638679.1692 | 1247981.2232 | 2638673.3998 | 1247995.1059 | 2638666.2086 | 1248010.0873
107 | 2638577.6459 | 1248082.2678 | 2638577.761 | 1248082.3353
108 | 2638577.6459 | 1248082.2678 | 2638573.8823 | 1248080.0589 | 2638559.651 | 1248069.0703 | 2638556.3251 | 1248066.3917
109 | 2638613.9982 | 1248022.765 | 2638626.6707 | 1248030.2929
110 | 2638679.1692 | 1247981.2232 | 2638662.5855 | 1247971.6047
111 | 2638542.57 | 1248055.5206 | 2638543.4094 | 1248055.9895 | 2638556.3251 | 1248066.3917
112 | 2638424.7369 | 1248094.2676 | 2638438.3447 | 1248098.9588 | 2638473.7234 | 1248114.1425
113 | 2638473.7234 | 1248114.1425 | 2638475.9924 | 1248115.116
114 | 2638607.423 | 1248018.8591 | 2638613.9982 | 1248022.765
115 | 2638662.0513 | 1247971.2948 | 2638662.5855 | 1247971.6047
116 | 2638607.423 | 1248018.8591 | 2638588.803 | 1248007.7981
117 | 2638586.8868 | 1248006.6598 | 2638588.803 | 1248007.7981
118 | 2638581.558 | 1248003.4943 | 2638586.8868 | 1248006.6598
119 | 2638581.558 | 1248003.4943 | 2638581.118 | 1248003.2329 | 2638564.3406 | 1247993.8828
120 | 2638559.9627 | 1247991.443 | 2638564.3406 | 1247993.8828
121 | 2638496.2661 | 1247988.833 | 2638513.875 | 1247997.6365
122 | 2638496.2661 | 1247988.833 | 2638495.0081 | 1247988.2041
123 | 2638519.8684 | 1248000.6328 | 2638513.875 | 1247997.6365
124 | 2638472.8552 | 1247977.1288 | 2638495.0081 | 1247988.2041
125 | 2638527.3953 | 1248004.3958 | 2638519.8684 | 1248000.6328
126 | 2638662.0513 | 1247971.2948 | 2638642.0417 | 1247959.6893 | 2638635.909 | 1247956.0427
127 | 2638635.909 | 1247956.0427 | 2638632.2705 | 1247953.8791
128 | 2638626.6156 | 1247950.5166 | 2638632.2705 | 1247953.8791
129 | 2638618.5429 | 1247945.7163 | 2638626.6156 | 1247950.5166
130 | 2638618.5429 | 1247945.7163 | 2638611.9374 | 1247941.7886
131 | 2638581.1954 | 1247923.5125 | 2638583.6434 | 1247924.9643 | 2638587.3426 | 1247927.1639
132 | 2638571.0899 | 1247917.5194 | 2638581.1954 | 1247923.5125
133 | 2638597.6937 | 1247933.3189 | 2638587.3426 | 1247927.1639
134 | 2638571.0899 | 1247917.5194 | 2638564.7497 | 1247913.7594
135 | 2638597.6937 | 1247933.3189 | 2638598.2457 | 1247933.6472
136 | 2638547.2255 | 1247903.3666 | 2638564.7497 | 1247913.7594
137 | 2638598.2457 | 1247933.6472 | 2638600.2756 | 1247934.8542
138 | 2638546.995 | 1247903.2299 | 2638547.2255 | 1247903.3666
139 | 2638611.9374 | 1247941.7886 | 2638600.2756 | 1247934.8542
140 | 2638559.9627 | 1247991.443 | 2638551.8626 | 1247986.9288
141 | 2638551.8626 | 1247986.9288 | 2638522.3755 | 1247970.4956
142 | 2638515.4738 | 1247966.9757 | 2638521.1255 | 1247969.799 | 2638522.3755 | 1247970.4956
143 | 2638515.3732 | 1247966.9254 | 2638515.4738 | 1247966.9757
144 | 2638507.4002 | 1247962.9425 | 2638492.0402 | 1247955.2694
145 | 2638507.4002 | 1247962.9425 | 2638515.3732 | 1247966.9254
146 | 2638490.444 | 1247954.4721 | 2638492.0402 | 1247955.2694
147 | 2638490.444 | 1247954.4721 | 2638486.4773 | 1247952.4905

## bus_geodata
| x | y | coords
0 | 2638856.8907 | 1247917.7897
1 | 2638835.6859 | 1247905.5819
2 | 2638833.1985 | 1247904.1619
3 | 2638816.5712 | 1247894.6698
4 | 2638803.1563 | 1247887.0148
5 | 2638808.5131 | 1247953.8798
6 | 2638775.7064 | 1247947.3248
7 | 2638779.8639 | 1247873.9322
8 | 2638763.4971 | 1247864.7395
9 | 2638735.9385 | 1247891.112
10 | 2638739.5887 | 1247938.2404
11 | 2638719.9544 | 1247927.0978
12 | 2638704.6395 | 1247920.1377
13 | 2638629.557 | 1247860.9294
14 | 2638649.4153 | 1247877.6254
15 | 2638620.3633 | 1247854.735
16 | 2638664.1554 | 1247890.3408
17 | 2638618.1988 | 1247853.2972
18 | 2638676.572 | 1247900.8865
19 | 2638594.8959 | 1247840.5221
20 | 2638624.9897 | 1247838.4056
21 | 2638679.0669 | 1247902.8253
22 | 2638579.1657 | 1247831.7502
23 | 2638638.4167 | 1247807.8432
24 | 2638563.0711 | 1247822.9298
25 | 2638569.7105 | 1247811.2716
26 | 2638562.4815 | 1247822.6325
27 | 2638572.5105 | 1247806.3552
28 | 2638542.9658 | 1247812.7925
29 | 2638523.6262 | 1247837.1581
30 | 2638501.5393 | 1247852.79
31 | 2638485.6697 | 1247863.9434
32 | 2638516.1856 | 1247884.5392
33 | 2638476.5161 | 1247873.3681
34 | 2638524.6255 | 1247889.6746
35 | 2638473.7969 | 1247871.1268
36 | 2638467.1158 | 1247887.2651
37 | 2638539.3575 | 1247898.6385
38 | 2638462.6181 | 1247852.2943
39 | 2638462.4919 | 1247896.726
40 | 2638640.2979 | 1247803.4897
41 | 2638431.7193 | 1247806.8117
42 | 2638413.3274 | 1247826.3177
43 | 2638451.8711 | 1247886.695
44 | 2638450.3407 | 1247893.2783
45 | 2638403.942 | 1247836.1735
46 | 2638428.5996 | 1247902.4779
47 | 2638390.2033 | 1247830.6032
48 | 2638398.565 | 1247842.0093
49 | 2638401.1934 | 1247849.0608
50 | 2638410.8078 | 1247914.125
51 | 2638427.3341 | 1247903.1803
52 | 2638393.0007 | 1247925.7842
53 | 2638314.8184 | 1247895.1921
54 | 2638282.5833 | 1247932.064
55 | 2638343.7206 | 1247868.1053
56 | 2638304.5129 | 1247888.72
57 | 2638356.361 | 1247958.2465
58 | 2638374.9308 | 1247830.1455
59 | 2638252.769 | 1247936.8778
60 | 2638270.4763 | 1247945.9869
61 | 2638315.5035 | 1247858.0943
62 | 2638324.9713 | 1247849.105
63 | 2638295.8574 | 1247838.7881
64 | 2638353.7811 | 1247831.6796
65 | 2638292.56 | 1247883.3348
66 | 2638450.7501 | 1247934.9752
67 | 2638465.801 | 1247942.3149
68 | 2638442.811 | 1247962.1084
69 | 2638325.068 | 1247991.6134
70 | 2638379.6829 | 1247968.4262
71 | 2638418.9341 | 1247953.8039
72 | 2638422.2316 | 1247955.1641
73 | 2638278.2407 | 1247749.3138
74 | 2638282.1359 | 1247745.3719
75 | 2638289.5614 | 1247845.6078
76 | 2638269.7507 | 1247875.3518
77 | 2638367.5326 | 1248001.4531
78 | 2638374.7881 | 1247981.7313
79 | 2638367.1225 | 1248002.5676
80 | 2638388.2526 | 1248010.7142
81 | 2638393.6869 | 1248012.8093
82 | 2638442.4019 | 1247963.4844
83 | 2638433.4782 | 1248003.8866
84 | 2638466.2859 | 1248018.4087
85 | 2638428.6044 | 1248052.1425
86 | 2638323.446 | 1247993.4378
87 | 2638427.9158 | 1248059.8489
88 | 2638464.7643 | 1247973.0838
89 | 2638467.0824 | 1248018.7704
90 | 2638476.1517 | 1248022.8881
91 | 2638502.0019 | 1248034.6247
92 | 2638504.6467 | 1248035.8255
93 | 2638523.1255 | 1248044.6592
94 | 2638536.5313 | 1248052.1475
95 | 2638637.1016 | 1248072.9009
96 | 2638643.9899 | 1248057.6074
97 | 2638650.0398 | 1248044.1751
98 | 2638632.347 | 1248033.6649
99 | 2638666.2086 | 1248010.0873
100 | 2638577.761 | 1248082.3353
101 | 2638577.6459 | 1248082.2678
102 | 2638626.6707 | 1248030.2929
103 | 2638679.1692 | 1247981.2232
104 | 2638556.3251 | 1248066.3917
105 | 2638542.57 | 1248055.5206
106 | 2638424.7369 | 1248094.2676
107 | 2638473.7234 | 1248114.1425
108 | 2638475.9924 | 1248115.116
109 | 2638613.9982 | 1248022.765
110 | 2638662.5855 | 1247971.6047
111 | 2638607.423 | 1248018.8591
112 | 2638588.803 | 1248007.7981
113 | 2638586.8868 | 1248006.6598
114 | 2638581.558 | 1248003.4943
115 | 2638564.3406 | 1247993.8828
116 | 2638260.8685 | 1247956.4934
117 | 2638496.2661 | 1247988.833
118 | 2638513.875 | 1247997.6365
119 | 2638495.0081 | 1247988.2041
120 | 2638519.8684 | 1248000.6328
121 | 2638472.8552 | 1247977.1288
122 | 2638527.3953 | 1248004.3958
123 | 2638662.0513 | 1247971.2948
124 | 2638635.909 | 1247956.0427
125 | 2638632.2705 | 1247953.8791
126 | 2638626.6156 | 1247950.5166
127 | 2638695.827 | 1247941.168
128 | 2638618.5429 | 1247945.7163
129 | 2638714.0297 | 1247901.3506
130 | 2638581.1954 | 1247923.5125
131 | 2638587.3426 | 1247927.1639
132 | 2638571.0899 | 1247917.5194
133 | 2638597.6937 | 1247933.3189
134 | 2638564.7497 | 1247913.7594
135 | 2638598.2457 | 1247933.6472
136 | 2638547.2255 | 1247903.3666
137 | 2638600.2756 | 1247934.8542
138 | 2638546.995 | 1247903.2299
139 | 2638611.9374 | 1247941.7886
140 | 2638559.9627 | 1247991.443
141 | 2638551.8626 | 1247986.9288
142 | 2638522.3755 | 1247970.4956
143 | 2638515.4738 | 1247966.9757
144 | 2638507.4002 | 1247962.9425
145 | 2638492.0402 | 1247955.2694
146 | 2638515.3732 | 1247966.9254
147 | 2638490.444 | 1247954.4721
148 | 2638486.4773 | 1247952.4905
149 | 2638450.7501 | 1247934.9752

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97024 | -0.57446 | 0.001518 | 0.00038044
1 | 0.97028 | -0.57377 | 0.0011766 | 0.00029489
2 | 0.97028 | -0.57363 | 0.0015004 | 0.00037604
3 | 0.97036 | -0.57214 | 0.00097269 | 0.00024378
4 | 0.97043 | -0.57066 | 0.0039138 | 0.00098089
5 | 0.97176 | -0.54444 | 0.0017659 | 0.00044259
6 | 0.97181 | -0.54334 | 0.0029135 | 0.00073019
7 | 0.97066 | -0.56617 | 0.0032005 | 0.00080213
8 | 0.97088 | -0.56191 | 0.0026356 | 0.00066053
9 | 0.9715 | -0.54947 | 0.001798 | 0.00045061
10 | 0.97198 | -0.54012 | 0.0018731 | 0.00046945
11 | 0.97212 | -0.53731 | 0 | 0
12 | 0.97248 | -0.5301 | 0 | 0
13 | 0.97518 | -0.47704 | 0.0011159 | 0.00027967
14 | 0.97435 | -0.49327 | 0.0020859 | 0.00052278
15 | 0.97554 | -0.46988 | 0.0020077 | 0.00050318
16 | 0.97377 | -0.50472 | 0.0016155 | 0.00040488
17 | 0.97563 | -0.46811 | 0 | 0
18 | 0.97331 | -0.51383 | 0.0030881 | 0.00077394
19 | 0.97612 | -0.45853 | 0.0091675 | 0.0022976
20 | 0.9756 | -0.46877 | 0.0014053 | 0.0003522
21 | 0.97323 | -0.51542 | 0.0016095 | 0.00040338
22 | 0.97632 | -0.45453 | 0.0023162 | 0.00058049
23 | 0.97558 | -0.46924 | 0 | 0
24 | 0.97654 | -0.45026 | 0 | 0
25 | 0.97645 | -0.45208 | 0.0020508 | 0.00051398
26 | 0.97655 | -0.45008 | 0.0037286 | 0.00093449
27 | 0.97642 | -0.45264 | 0.0053816 | 0.0013487
28 | 0.97687 | -0.44389 | 0 | 0
29 | 0.97732 | -0.43497 | 0.009185 | 0.002302
30 | 0.97777 | -0.42618 | 0.0030414 | 0.00076225
31 | 0.97811 | -0.41961 | 0 | 0
32 | 0.97954 | -0.39158 | 0.0021846 | 0.0005475
33 | 0.97782 | -0.42516 | 0 | 0
34 | 0.97993 | -0.384 | 0.0023608 | 0.00059168
35 | 0.97776 | -0.42636 | 0 | 0
36 | 0.97753 | -0.43081 | 0.010096 | 0.0025304
37 | 0.98062 | -0.3706 | 0.0025244 | 0.00063267
38 | 0.97738 | -0.4339 | 0.0019968 | 0.00050045
39 | 0.97738 | -0.43387 | 0 | 0
40 | 0.97557 | -0.4693 | 0.0007701 | 0.000193
41 | 0.97651 | -0.45087 | 0 | 0
42 | 0.97609 | -0.45912 | 0.00078436 | 0.00019658
43 | 0.97718 | -0.4377 | 0.0014275 | 0.00035777
44 | 0.97719 | -0.43753 | 0 | 0
45 | 0.97589 | -0.46312 | 0 | 0
46 | 0.97684 | -0.44435 | 0.00085574 | 0.00021447
47 | 0.97569 | -0.46716 | 0 | 0
48 | 0.97588 | -0.46328 | 0 | 0
49 | 0.97588 | -0.46343 | 0.0011121 | 0.00027872
50 | 0.97654 | -0.4503 | 0 | 0
51 | 0.97682 | -0.44475 | 0 | 0
52 | 0.97623 | -0.45625 | 0 | 0
53 | 0.97462 | -0.48813 | 0 | 0
54 | 0.97444 | -0.4917 | 0 | 0
55 | 0.9748 | -0.48468 | 0 | 0
56 | 0.97461 | -0.48841 | 0.00043675 | 0.00010946
57 | 0.97483 | -0.48378 | 0 | 0
58 | 0.97547 | -0.47136 | 0.0038969 | 0.00097665
59 | 0.9744 | -0.49257 | 0.0015692 | 0.00039329
60 | 0.97441 | -0.49235 | 0.00090195 | 0.00022605
61 | 0.97459 | -0.48873 | 0 | 0
62 | 0.97464 | -0.48775 | 0.0022071 | 0.00055314
63 | 0.97449 | -0.49078 | 0 | 0
64 | 0.97526 | -0.47565 | 0 | 0
65 | 0.9746 | -0.48861 | 0.00050908 | 0.00012759
66 | 0.99491 | -0.097417 | 0 | 0
67 | 0.99621 | -0.072317 | 0.0017129 | 0.00042929
68 | 0.9927 | -0.13994 | 0 | 0
69 | 0.97456 | -0.48905 | 0.0010609 | 0.00026589
70 | 0.97353 | -0.50945 | 0 | 0
71 | 0.99238 | -0.14622 | 0.0074587 | 0.0018693
72 | 0.9924 | -0.14575 | 0.0033776 | 0.0008465
73 | 0.9742 | -0.4964 | 0.0014689 | 0.00036814
74 | 0.97419 | -0.49659 | 0.0018848 | 0.00047238
75 | 0.97448 | -0.4909 | 0.00071141 | 0.0001783
76 | 0.97459 | -0.48874 | 0.00029535 | 7.4021e-05
77 | 0.972 | -0.53966 | 0.014121 | 0.003539
78 | 0.9728 | -0.52381 | 0.014128 | 0.0035407
79 | 0.97197 | -0.54025 | 0 | 0
80 | 0.9714 | -0.55145 | 0.012508 | 0.0031347
81 | 0.97132 | -0.55299 | 0.014295 | 0.0035827
82 | 0.99262 | -0.14156 | 0 | 0
83 | 0.9906 | -0.18059 | 0 | 0
84 | 0.98952 | -0.20149 | 0.0067496 | 0.0016916
85 | 0.98969 | -0.19818 | 0 | 0
86 | 0.97455 | -0.48929 | 0.0052181 | 0.0013078
87 | 0.98955 | -0.20099 | 0.010177 | 0.0025505
88 | 0.99222 | -0.14916 | 0.0062334 | 0.0015622
89 | 0.9895 | -0.20189 | 0.0018527 | 0.00046433
90 | 0.98928 | -0.20617 | 0.0031853 | 0.00079831
91 | 0.98873 | -0.21678 | 0.0023955 | 0.00060037
92 | 0.98868 | -0.21774 | 0.0019162 | 0.00048024
93 | 0.98837 | -0.22383 | 0.0028132 | 0.00070506
94 | 0.98817 | -0.22762 | 0.0026932 | 0.00067499
95 | 0.99126 | -0.16542 | 0.0015814 | 0.00039633
96 | 0.99128 | -0.16495 | 0.00082383 | 0.00020647
97 | 0.99132 | -0.16432 | 0 | 0
98 | 0.99235 | -0.1447 | 0.00081889 | 0.00020523
99 | 0.98945 | -0.2 | 0.0034254 | 0.0008585
100 | 0.98785 | -0.234 | 0.0025138 | 0.00063001
101 | 0.98785 | -0.234 | 0.0025147 | 0.00063023
102 | 0.99268 | -0.13839 | 0.0033599 | 0.00084208
103 | 0.98791 | -0.22955 | 0 | 0
104 | 0.98797 | -0.23161 | 0.0032932 | 0.00082535
105 | 0.9881 | -0.229 | 0.0028225 | 0.00070739
106 | 0.98922 | -0.20728 | 0 | 0
107 | 0.98873 | -0.21689 | 0 | 0
108 | 0.9887 | -0.21734 | 0.010218 | 0.0025608
109 | 0.99343 | -0.12409 | 0.0011091 | 0.00027796
110 | 0.98698 | -0.24749 | 0.0022807 | 0.0005716
111 | 0.99382 | -0.11665 | 0.0016453 | 0.00041236
112 | 0.99494 | -0.095439 | 0.001891 | 0.00047393
113 | 0.99506 | -0.09324 | 0.0024201 | 0.00060654
114 | 0.99538 | -0.087063 | 0.0030139 | 0.00075534
115 | 0.99643 | -0.067178 | 0.0026818 | 0.00067212
116 | 0.9744 | -0.49262 | 0.0010323 | 0.00025872
117 | 0.99181 | -0.15721 | 0.0030813 | 0.00077225
118 | 0.99168 | -0.15976 | 0.0015785 | 0.0003956
119 | 0.99182 | -0.15695 | 0.0018715 | 0.00046905
120 | 0.99164 | -0.16044 | 0.0042971 | 0.001077
121 | 0.9921 | -0.15157 | 0.002738 | 0.0006862
122 | 0.99163 | -0.16066 | 0.0014405 | 0.00036102
123 | 0.98695 | -0.24806 | 0.0019764 | 0.00049532
124 | 0.9855 | -0.27588 | 0.0014617 | 0.00036634
125 | 0.9853 | -0.27975 | 0.0018299 | 0.00045861
126 | 0.98499 | -0.28572 | 0.0033308 | 0.00083478
127 | 0.97245 | -0.53082 | 0.0017292 | 0.00043339
128 | 0.98456 | -0.2941 | 0.0020866 | 0.00052295
129 | 0.97247 | -0.53037 | 0.00069724 | 0.00017474
130 | 0.98263 | -0.3315 | 0.0024666 | 0.00061819
131 | 0.98294 | -0.32554 | 0.0019886 | 0.0004984
132 | 0.98213 | -0.34118 | 0.0043892 | 0.0011
133 | 0.98346 | -0.31539 | 0.0022469 | 0.00056312
134 | 0.98182 | -0.34711 | 0.0016532 | 0.00041433
135 | 0.98349 | -0.31484 | 0.0037259 | 0.0009338
136 | 0.98099 | -0.36337 | 0.0012269 | 0.00030748
137 | 0.98359 | -0.31279 | 0.002136 | 0.00053534
138 | 0.98098 | -0.36358 | 0.0012118 | 0.00030369
139 | 0.98421 | -0.30088 | 0.0014669 | 0.00036764
140 | 0.9967 | -0.062071 | 0.0033874 | 0.00084896
141 | 0.99721 | -0.052493 | 0.0012013 | 0.00030108
142 | 0.99907 | -0.017528 | 0.0014673 | 0.00036774
143 | 0.9995 | -0.0094709 | 0.0012302 | 0.00030832
144 | 1 | 0 | -0.33962 | -0.086866
145 | 0.99856 | -0.027477 | 0.0012091 | 0.00030304
146 | 0.9995 | -0.0093534 | 0.0012063 | 0.00030233
147 | 0.99841 | -0.030299 | 0.0016088 | 0.00040321
148 | 0.99805 | -0.037191 | 0.0019134 | 0.00047954
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.001518 | -0.00038044 | 0.001518 | 0.00038017 | 4.9728e-08 | -2.7037e-07 | 0.0023281 | 0.002328 | 0.0023281 | 0.97024 | -0.57446 | 0.97028 | -0.57377 | 0.63958
1 | -0.0026946 | -0.00067506 | 0.0026947 | 0.00067503 | 1.8342e-08 | -2.3638e-08 | 0.0041324 | 0.0041324 | 0.0041324 | 0.97028 | -0.57377 | 0.97028 | -0.57363 | 1.1353
2 | -0.0041951 | -0.0010511 | 0.0041954 | 0.001051 | 2.9715e-07 | -4.6314e-08 | 0.0064334 | 0.0064333 | 0.0064334 | 0.97028 | -0.57363 | 0.97036 | -0.57214 | 1.7674
3 | -0.005168 | -0.0012948 | 0.0051684 | 0.0012948 | 3.6376e-07 | 4.1992e-08 | 0.0079249 | 0.0079248 | 0.0079249 | 0.97036 | -0.57214 | 0.97043 | -0.57066 | 2.1772
4 | -0.0090822 | -0.0022757 | 0.0090842 | 0.0022767 | 1.9429e-06 | 9.1328e-07 | 0.013926 | 0.013926 | 0.013926 | 0.97043 | -0.57066 | 0.97066 | -0.56617 | 3.8258
5 | -0.0017659 | -0.00044259 | 0.001766 | 0.00044223 | 9.1733e-08 | -3.5578e-07 | 0.0027041 | 0.002704 | 0.0027041 | 0.97176 | -0.54444 | 0.97181 | -0.54334 | 0.74289
6 | -0.0046795 | -0.0011724 | 0.0046803 | 0.0011724 | 7.1821e-07 | -2.6637e-09 | 0.0071651 | 0.0071649 | 0.0071651 | 0.97181 | -0.54334 | 0.97198 | -0.54012 | 1.9684
7 | -0.012285 | -0.0030788 | 0.012287 | 0.0030801 | 2.4966e-06 | 1.3657e-06 | 0.018832 | 0.018832 | 0.018832 | 0.97066 | -0.56617 | 0.97088 | -0.56191 | 5.1737
8 | -0.014923 | -0.0037407 | 0.014932 | 0.0037458 | 8.8503e-06 | 5.1059e-06 | 0.022872 | 0.022871 | 0.022872 | 0.97088 | -0.56191 | 0.9715 | -0.54947 | 6.2834
9 | -0.01673 | -0.0041964 | 0.016739 | 0.0042021 | 9.6986e-06 | 5.7191e-06 | 0.025625 | 0.025625 | 0.025625 | 0.9715 | -0.54947 | 0.97212 | -0.53731 | 7.0399
10 | -0.0065534 | -0.0016419 | 0.0065543 | 0.0016421 | 8.7637e-07 | 2.7305e-07 | 0.010033 | 0.010032 | 0.010033 | 0.97198 | -0.54012 | 0.97212 | -0.53731 | 2.7562
11 | -0.023294 | -0.0058443 | 0.023302 | 0.0058492 | 8.0207e-06 | 4.9246e-06 | 0.035658 | 0.035657 | 0.035658 | 0.97212 | -0.53731 | 0.97248 | -0.5301 | 9.796
12 | 0.00069725 | 0.00017449 | -0.00069724 | -0.00017474 | 8.964e-09 | -2.5485e-07 | 0.0010668 | 0.0010669 | 0.0010669 | 0.97248 | -0.5301 | 0.97247 | -0.53037 | 0.2931
13 | -0.025728 | -0.0064568 | 0.025746 | 0.006468 | 1.8018e-05 | 1.1147e-05 | 0.03937 | 0.03937 | 0.03937 | 0.97248 | -0.5301 | 0.97323 | -0.51542 | 10.816
14 | 0.0017293 | 0.00043314 | -0.0017292 | -0.00043339 | 5.9866e-08 | -2.4459e-07 | 0.0026459 | 0.002646 | 0.002646 | 0.97248 | -0.5301 | 0.97245 | -0.53082 | 0.72693
15 | 0.034204 | 0.0086101 | -0.034178 | -0.0085935 | 2.6518e-05 | 1.6648e-05 | 0.052206 | 0.052206 | 0.052206 | 0.97518 | -0.47704 | 0.97435 | -0.49327 | 14.3423
16 | -0.03532 | -0.0088898 | 0.035332 | 0.0088974 | 1.2085e-05 | 7.5962e-06 | 0.053909 | 0.053909 | 0.053909 | 0.97518 | -0.47704 | 0.97554 | -0.46988 | 14.8101
17 | 0.032092 | 0.0080707 | -0.032074 | -0.0080597 | 1.7542e-05 | 1.0985e-05 | 0.04902 | 0.049021 | 0.049021 | 0.97435 | -0.49327 | 0.97377 | -0.50472 | 13.4672
18 | -0.03734 | -0.0094006 | 0.037343 | 0.0094026 | 3.1627e-06 | 1.9917e-06 | 0.056971 | 0.056971 | 0.056971 | 0.97554 | -0.46988 | 0.97563 | -0.46811 | 15.6514
19 | 0.030459 | 0.0076548 | -0.030446 | -0.0076466 | 1.3239e-05 | 8.2702e-06 | 0.046552 | 0.046552 | 0.046552 | 0.97377 | -0.50472 | 0.97331 | -0.51383 | 12.789
20 | -0.039519 | -0.0099472 | 0.039537 | 0.0099581 | 1.8113e-05 | 1.0928e-05 | 0.060289 | 0.060289 | 0.060289 | 0.97563 | -0.46811 | 0.97612 | -0.45853 | 8.2814
21 | 0.0021755 | 0.00054458 | -0.0021754 | -0.00054475 | 6.7565e-08 | -1.6114e-07 | 0.0033178 | 0.0033179 | 0.0033179 | 0.97563 | -0.46811 | 0.9756 | -0.46877 | 0.9115
22 | 0.027358 | 0.0068726 | -0.027356 | -0.0068713 | 2.0734e-06 | 1.2877e-06 | 0.041831 | 0.041831 | 0.041831 | 0.97331 | -0.51383 | 0.97323 | -0.51542 | 11.492
23 | -0.048704 | -0.012256 | 0.048714 | 0.012261 | 9.3123e-06 | 5.0591e-06 | 0.074264 | 0.074263 | 0.074264 | 0.97612 | -0.45853 | 0.97632 | -0.45453 | 5.1005
24 | 0.00077012 | 0.00019254 | -0.0007701 | -0.00019295 | 1.7269e-08 | -4.0577e-07 | 0.0011744 | 0.0011746 | 0.0011746 | 0.9756 | -0.46877 | 0.97558 | -0.46924 | 0.32269
25 | -0.05103 | -0.012841 | 0.05104 | 0.012847 | 1.0414e-05 | 5.7467e-06 | 0.077793 | 0.077793 | 0.077793 | 0.97632 | -0.45453 | 0.97654 | -0.45026 | 5.343
26 | 0.0007701 | 0.00019295 | -0.0007701 | -0.000193 | 2.4537e-09 | -5.7645e-08 | 0.0011746 | 0.0011746 | 0.0011746 | 0.97558 | -0.46924 | 0.97557 | -0.4693 | 0.3227
27 | 0.0074332 | 0.001863 | -0.0074325 | -0.0018627 | 6.4542e-07 | 2.4524e-07 | 0.011326 | 0.011326 | 0.011326 | 0.97654 | -0.45026 | 0.97645 | -0.45208 | 3.1117
28 | -0.058473 | -0.01471 | 0.058474 | 0.01471 | 4.9168e-07 | 2.8163e-07 | 0.089119 | 0.089119 | 0.089119 | 0.97654 | -0.45026 | 0.97655 | -0.45008 | 6.1208
29 | 0.0053817 | 0.0013488 | -0.0053816 | -0.0013487 | 1.427e-07 | 2.0561e-08 | 0.0082012 | 0.0082012 | 0.0082012 | 0.97645 | -0.45208 | 0.97642 | -0.45264 | 2.2531
30 | -0.062203 | -0.015645 | 0.062221 | 0.015655 | 1.8415e-05 | 1.0691e-05 | 0.094801 | 0.0948 | 0.094801 | 0.97655 | -0.45008 | 0.97687 | -0.44389 | 6.511
31 | -0.062221 | -0.015655 | 0.062248 | 0.015671 | 2.6511e-05 | 1.5391e-05 | 0.0948 | 0.0948 | 0.0948 | 0.97687 | -0.44389 | 0.97732 | -0.43497 | 6.511
32 | -0.071433 | -0.017973 | 0.071463 | 0.017991 | 3.0035e-05 | 1.7865e-05 | 0.10878 | 0.10878 | 0.10878 | 0.97732 | -0.43497 | 0.97777 | -0.42618 | 7.4715
33 | -0.074504 | -0.018753 | 0.074527 | 0.018767 | 2.3397e-05 | 1.4001e-05 | 0.11341 | 0.11341 | 0.11341 | 0.97777 | -0.42618 | 0.97811 | -0.41961 | 7.7893
34 | -0.16745 | -0.042196 | 0.16767 | 0.042338 | 0.00022481 | 0.00014202 | 0.25483 | 0.25482 | 0.25483 | 0.97811 | -0.41961 | 0.97954 | -0.39158 | 17.5017
35 | 0.092921 | 0.023429 | -0.092896 | -0.023414 | 2.4666e-05 | 1.5126e-05 | 0.14141 | 0.14141 | 0.14141 | 0.97811 | -0.41961 | 0.97782 | -0.42516 | 9.7124
36 | -0.16986 | -0.042885 | 0.16992 | 0.042924 | 6.172e-05 | 3.9003e-05 | 0.25814 | 0.25814 | 0.25814 | 0.97954 | -0.39158 | 0.97993 | -0.384 | 17.7296
37 | 0.018855 | 0.0047365 | -0.018854 | -0.0047359 | 1.0864e-06 | 6.5118e-07 | 0.028697 | 0.028697 | 0.028697 | 0.97782 | -0.42516 | 0.97776 | -0.42636 | 7.8838
38 | 0.074041 | 0.018677 | -0.074021 | -0.018665 | 2.0047e-05 | 1.1986e-05 | 0.11272 | 0.11272 | 0.11272 | 0.97782 | -0.42516 | 0.97753 | -0.43081 | 7.7415
39 | -0.17228 | -0.043516 | 0.17239 | 0.043586 | 0.00011075 | 7.0008e-05 | 0.26173 | 0.26173 | 0.26173 | 0.97993 | -0.384 | 0.98062 | -0.3706 | 17.9758
40 | 0.018854 | 0.0047359 | -0.018847 | -0.0047318 | 6.7741e-06 | 4.0604e-06 | 0.028697 | 0.028697 | 0.028697 | 0.97776 | -0.42636 | 0.97738 | -0.4339 | 7.8838
41 | 0.063924 | 0.016135 | -0.063915 | -0.016129 | 9.3555e-06 | 5.4596e-06 | 0.097348 | 0.097348 | 0.097348 | 0.97753 | -0.43081 | 0.97738 | -0.43387 | 6.686
42 | -0.17491 | -0.044218 | 0.17497 | 0.044256 | 5.8917e-05 | 3.7257e-05 | 0.26556 | 0.26556 | 0.26556 | 0.98062 | -0.3706 | 0.98098 | -0.36358 | 18.2389
43 | 0.01685 | 0.0042314 | -0.016837 | -0.0042234 | 1.3639e-05 | 8.0369e-06 | 0.025657 | 0.025657 | 0.025657 | 0.97738 | -0.4339 | 0.97651 | -0.45087 | 7.0487
44 | 0.063915 | 0.016129 | -0.063904 | -0.016123 | 1.1195e-05 | 6.5334e-06 | 0.097348 | 0.097348 | 0.097348 | 0.97738 | -0.43387 | 0.97719 | -0.43753 | 6.686
45 | 0.016837 | 0.0042234 | -0.01683 | -0.0042195 | 6.6183e-06 | 3.9005e-06 | 0.025657 | 0.025657 | 0.025657 | 0.97651 | -0.45087 | 0.97609 | -0.45912 | 7.0487
46 | 0.016046 | 0.0040229 | -0.016043 | -0.0040211 | 3.054e-06 | 1.7844e-06 | 0.024462 | 0.024462 | 0.024462 | 0.97609 | -0.45912 | 0.97589 | -0.46312 | 6.7202
47 | -0.0014275 | -0.00035777 | 0.0014275 | 0.00035769 | 1.1976e-08 | -7.7007e-08 | 0.0021738 | 0.0021737 | 0.0021738 | 0.97718 | -0.4377 | 0.97719 | -0.43753 | 0.59719
48 | 0.062476 | 0.015765 | -0.062456 | -0.015753 | 2.0396e-05 | 1.185e-05 | 0.095174 | 0.095175 | 0.095175 | 0.97719 | -0.43753 | 0.97684 | -0.44435 | 6.5367
49 | 0.014931 | 0.0037426 | -0.014928 | -0.0037409 | 2.8777e-06 | 1.6568e-06 | 0.022766 | 0.022766 | 0.022766 | 0.97589 | -0.46312 | 0.97569 | -0.46716 | 6.2544
50 | 0.0011121 | 0.00027853 | -0.0011121 | -0.00027863 | 8.545e-09 | -9.3548e-08 | 0.0016956 | 0.0016957 | 0.0016957 | 0.97589 | -0.46312 | 0.97588 | -0.46328 | 0.46585
51 | 0.0616 | 0.015539 | -0.061599 | -0.015538 | 1.1957e-06 | 6.9275e-07 | 0.093871 | 0.093871 | 0.093871 | 0.97684 | -0.44435 | 0.97682 | -0.44475 | 6.4472
52 | 0.014928 | 0.0037409 | -0.014925 | -0.0037392 | 2.98e-06 | 1.7157e-06 | 0.022766 | 0.022766 | 0.022766 | 0.97569 | -0.46716 | 0.97547 | -0.47136 | 6.2544
53 | 0.0011121 | 0.00027863 | -0.0011121 | -0.00027872 | 8.1145e-09 | -8.883e-08 | 0.0016957 | 0.0016957 | 0.0016957 | 0.97588 | -0.46328 | 0.97588 | -0.46343 | 0.46586
54 | -0.061583 | -0.015528 | 0.061599 | 0.015538 | 1.6342e-05 | 9.4687e-06 | 0.093872 | 0.093871 | 0.093872 | 0.97654 | -0.4503 | 0.97682 | -0.44475 | 6.4472
55 | 0.061583 | 0.015528 | -0.061565 | -0.015518 | 1.7548e-05 | 1.0168e-05 | 0.093872 | 0.093872 | 0.093872 | 0.97654 | -0.4503 | 0.97623 | -0.45625 | 6.4473
56 | 0.061565 | 0.015518 | -0.061484 | -0.015468 | 8.0989e-05 | 5.0609e-05 | 0.093872 | 0.093873 | 0.093873 | 0.97623 | -0.45625 | 0.97483 | -0.48378 | 12.8946
57 | 0.0035042 | 0.00087705 | -0.0035036 | -0.00087736 | 5.9453e-07 | -3.097e-07 | 0.0053497 | 0.0053499 | 0.0053499 | 0.97462 | -0.48813 | 0.97444 | -0.4917 | 1.4698
58 | -0.0047454 | -0.0011875 | 0.0047462 | 0.0011875 | 7.7978e-07 | 5.2049e-09 | 0.0072445 | 0.0072443 | 0.0072445 | 0.97462 | -0.48813 | 0.9748 | -0.48468 | 1.9902
59 | 0.0012412 | 0.00031047 | -0.0012412 | -0.00031061 | 1.6534e-08 | -1.4245e-07 | 0.0018948 | 0.0018949 | 0.0018949 | 0.97462 | -0.48813 | 0.97461 | -0.48841 | 0.52057
60 | 0.0015693 | 0.00039295 | -0.0015692 | -0.00039329 | 6.5279e-08 | -3.3584e-07 | 0.0023962 | 0.0023964 | 0.0023964 | 0.97444 | -0.4917 | 0.9744 | -0.49257 | 0.65835
61 | 0.0019343 | 0.00048441 | -0.0019343 | -0.0004846 | 6.0371e-08 | -1.9122e-07 | 0.0029537 | 0.0029538 | 0.0029538 | 0.97444 | -0.4917 | 0.97441 | -0.49235 | 0.81147
62 | 0.0062746 | 0.0015714 | -0.0062737 | -0.0015711 | 9.1826e-07 | 2.5497e-07 | 0.0095777 | 0.0095778 | 0.0095778 | 0.9748 | -0.48468 | 0.97464 | -0.48775 | 2.6313
63 | -0.011021 | -0.0027589 | 0.011026 | 0.0027614 | 4.7406e-06 | 2.4768e-06 | 0.016822 | 0.016822 | 0.016822 | 0.9748 | -0.48468 | 0.97526 | -0.47565 | 4.6214
64 | 0.00080444 | 0.00020115 | -0.00080443 | -0.00020131 | 7.4159e-09 | -1.5866e-07 | 0.001228 | 0.0012281 | 0.0012281 | 0.97461 | -0.48841 | 0.9746 | -0.48861 | 0.33739
65 | 0.0062807 | 0.0015741 | -0.0062791 | -0.0015737 | 1.5769e-06 | 4.3898e-07 | 0.0095871 | 0.0095873 | 0.0095873 | 0.97483 | -0.48378 | 0.97456 | -0.48905 | 2.6339
66 | 0.055204 | 0.013894 | -0.055136 | -0.013851 | 6.7621e-05 | 4.2961e-05 | 0.084286 | 0.084286 | 0.084286 | 0.97483 | -0.48378 | 0.97353 | -0.50945 | 23.1554
67 | 0.011028 | 0.0027625 | -0.011026 | -0.0027614 | 2.2525e-06 | 1.1767e-06 | 0.016822 | 0.016822 | 0.016822 | 0.97547 | -0.47136 | 0.97526 | -0.47565 | 4.6214
68 | 0.0010323 | 0.00025855 | -0.0010323 | -0.00025872 | 1.3268e-08 | -1.6885e-07 | 0.0015764 | 0.0015765 | 0.0015765 | 0.97441 | -0.49235 | 0.9744 | -0.49262 | 0.43309
69 | -0.0040664 | -0.001018 | 0.0040666 | 0.001018 | 1.8869e-07 | -4.1929e-08 | 0.0062083 | 0.0062082 | 0.0062083 | 0.97459 | -0.48873 | 0.97464 | -0.48775 | 1.7056
70 | 0.0040664 | 0.001018 | -0.004066 | -0.0010181 | 3.9754e-07 | -8.827e-08 | 0.0062083 | 0.0062084 | 0.0062084 | 0.97459 | -0.48873 | 0.97449 | -0.49078 | 1.7056
71 | 0.00071141 | 0.00017818 | -0.00071141 | -0.0001783 | 4.1072e-09 | -1.1301e-07 | 0.0010863 | 0.0010863 | 0.0010863 | 0.97449 | -0.49078 | 0.97448 | -0.4909 | 0.29844
72 | 0.0033546 | 0.0008399 | -0.0033537 | -0.00084046 | 8.9727e-07 | -5.6153e-07 | 0.0051221 | 0.0051225 | 0.0051225 | 0.97449 | -0.49078 | 0.9742 | -0.4964 | 1.4073
73 | 0.00029535 | 7.3721e-05 | -0.00029535 | -7.4021e-05 | 1.8462e-09 | -3.0058e-07 | 0.00045083 | 0.00045094 | 0.00045094 | 0.9746 | -0.48861 | 0.97459 | -0.48874 | 0.12388
74 | -0.085604 | -0.021597 | 0.085707 | 0.021663 | 0.00010301 | 6.5712e-05 | 0.12808 | 0.12808 | 0.12808 | 0.99491 | -0.097417 | 0.99621 | -0.072317 | 35.1874
75 | 0.085604 | 0.021597 | -0.08543 | -0.021486 | 0.0001739 | 0.00011093 | 0.12808 | 0.12808 | 0.12808 | 0.99491 | -0.097417 | 0.9927 | -0.13994 | 35.1875
76 | -0.08742 | -0.022092 | 0.087567 | 0.022186 | 0.00014749 | 9.4093e-05 | 0.13064 | 0.13064 | 0.13064 | 0.99621 | -0.072317 | 0.99805 | -0.037191 | 35.8903
77 | 0.021256 | 0.005332 | -0.021246 | -0.0053263 | 9.3445e-06 | 5.6633e-06 | 0.031863 | 0.031863 | 0.031863 | 0.9927 | -0.13994 | 0.99222 | -0.14916 | 8.7536
78 | 0.064174 | 0.016154 | -0.064169 | -0.016151 | 4.982e-06 | 3.17e-06 | 0.096219 | 0.096219 | 0.096219 | 0.9927 | -0.13994 | 0.99262 | -0.14156 | 26.4339
79 | 0.0052182 | 0.0013078 | -0.0052181 | -0.0013078 | 5.8112e-08 | 6.774e-09 | 0.0079674 | 0.0079674 | 0.0079674 | 0.97456 | -0.48905 | 0.97455 | -0.48929 | 2.1889
80 | 0.055136 | 0.013851 | -0.055098 | -0.013827 | 3.7768e-05 | 2.3995e-05 | 0.084286 | 0.084286 | 0.084286 | 0.97353 | -0.50945 | 0.9728 | -0.52381 | 23.1554
81 | -0.0074587 | -0.0018693 | 0.0074589 | 0.0018694 | 1.6731e-07 | 6.0992e-08 | 0.011184 | 0.011184 | 0.011184 | 0.99238 | -0.14622 | 0.9924 | -0.14575 | 3.0725
82 | -0.010836 | -0.0027159 | 0.010839 | 0.002717 | 2.1601e-06 | 1.1005e-06 | 0.016248 | 0.016248 | 0.016248 | 0.9924 | -0.14575 | 0.99262 | -0.14156 | 4.4638
83 | 0.0018849 | 0.00047233 | -0.0018848 | -0.00047238 | 1.7225e-08 | -5.7978e-08 | 0.0028789 | 0.002879 | 0.002879 | 0.9742 | -0.4964 | 0.97419 | -0.49659 | 0.79092
84 | -0.04094 | -0.010266 | 0.040971 | 0.010286 | 3.0956e-05 | 1.9551e-05 | 0.062676 | 0.062676 | 0.062676 | 0.972 | -0.53966 | 0.9728 | -0.52381 | 17.2187
85 | 0.026819 | 0.0067274 | -0.026818 | -0.0067269 | 7.5076e-07 | 4.6577e-07 | 0.041059 | 0.041059 | 0.041059 | 0.972 | -0.53966 | 0.97197 | -0.54025 | 11.2799
86 | 0.026818 | 0.0067269 | -0.026804 | -0.006718 | 1.4317e-05 | 8.8821e-06 | 0.041059 | 0.041059 | 0.041059 | 0.97197 | -0.54025 | 0.9714 | -0.55145 | 11.2799
87 | 0.014296 | 0.0035833 | -0.014295 | -0.0035827 | 1.0474e-06 | 5.9826e-07 | 0.021899 | 0.021899 | 0.021899 | 0.9714 | -0.55145 | 0.97132 | -0.55299 | 6.0163
88 | 0.05333 | 0.013434 | -0.053231 | -0.013371 | 9.9339e-05 | 6.3042e-05 | 0.079971 | 0.079971 | 0.079971 | 0.99262 | -0.14156 | 0.9906 | -0.18059 | 21.9701
89 | 0.032809 | 0.0082437 | -0.032776 | -0.0082232 | 3.2691e-05 | 2.0461e-05 | 0.049291 | 0.049291 | 0.049291 | 0.9906 | -0.18059 | 0.98952 | -0.20149 | 13.5416
90 | 0.020422 | 0.0051272 | -0.020405 | -0.0051169 | 1.7126e-05 | 1.0337e-05 | 0.03068 | 0.03068 | 0.03068 | 0.9906 | -0.18059 | 0.98969 | -0.19818 | 8.4286
91 | 0.026027 | 0.0065316 | -0.026026 | -0.0065313 | 5.0257e-07 | 3.1041e-07 | 0.039142 | 0.039142 | 0.039142 | 0.98952 | -0.20149 | 0.9895 | -0.20189 | 10.7532
92 | 0.020405 | 0.0051169 | -0.020402 | -0.0051152 | 2.731e-06 | 1.6484e-06 | 0.03068 | 0.03068 | 0.03068 | 0.98969 | -0.19818 | 0.98955 | -0.20099 | 8.4286
93 | 0.010226 | 0.0025647 | -0.010223 | -0.0025632 | 3.0651e-06 | 1.5177e-06 | 0.015377 | 0.015377 | 0.015377 | 0.98955 | -0.20099 | 0.98922 | -0.20728 | 4.2246
94 | 0.015013 | 0.0037641 | -0.015011 | -0.0037631 | 1.7196e-06 | 9.8372e-07 | 0.022515 | 0.022515 | 0.022515 | 0.99222 | -0.14916 | 0.9921 | -0.15157 | 6.1855
95 | 0.024174 | 0.006067 | -0.024169 | -0.006064 | 4.9368e-06 | 3.0316e-06 | 0.036356 | 0.036356 | 0.036356 | 0.9895 | -0.20189 | 0.98928 | -0.20617 | 9.9878
96 | 0.020983 | 0.0052656 | -0.020973 | -0.0052592 | 1.0607e-05 | 6.4241e-06 | 0.031564 | 0.031565 | 0.031565 | 0.98928 | -0.20617 | 0.98873 | -0.21678 | 8.6716
97 | 0.018577 | 0.0046589 | -0.018576 | -0.0046583 | 8.5147e-07 | 5.0769e-07 | 0.027959 | 0.027959 | 0.027959 | 0.98873 | -0.21678 | 0.98868 | -0.21774 | 7.6812
98 | 0.01666 | 0.0041781 | -0.016655 | -0.0041753 | 4.8325e-06 | 2.83e-06 | 0.025075 | 0.025076 | 0.025076 | 0.98868 | -0.21774 | 0.98837 | -0.22383 | 6.8889
99 | 0.013842 | 0.0034702 | -0.01384 | -0.0034688 | 2.5009e-06 | 1.4038e-06 | 0.02084 | 0.02084 | 0.02084 | 0.98837 | -0.22383 | 0.98817 | -0.22762 | 5.7253
100 | 0.011146 | 0.0027938 | -0.011146 | -0.0027934 | 7.3075e-07 | 3.7908e-07 | 0.016785 | 0.016785 | 0.016785 | 0.98817 | -0.22762 | 0.9881 | -0.229 | 4.6112
101 | -0.0015814 | -0.00039633 | 0.0015814 | 0.00039613 | 3.5443e-08 | -1.9354e-07 | 0.0023738 | 0.0023738 | 0.0023738 | 0.99126 | -0.16542 | 0.99128 | -0.16495 | 0.65215
102 | -0.0024052 | -0.0006026 | 0.0024053 | 0.00060246 | 7.201e-08 | -1.4384e-07 | 0.0036104 | 0.0036103 | 0.0036104 | 0.99128 | -0.16495 | 0.99132 | -0.16432 | 0.99187
103 | -0.21822 | -0.05584 | 0.21843 | 0.055971 | 0.00020753 | 0.00013176 | 0.32798 | 0.32798 | 0.32798 | 0.99132 | -0.16432 | 0.99235 | -0.1447 | 22.5258
104 | 0.21582 | 0.055237 | -0.21545 | -0.055001 | 0.00037215 | 0.00023624 | 0.32437 | 0.32437 | 0.32437 | 0.99132 | -0.16432 | 0.98945 | -0.2 | 22.2779
105 | -0.21925 | -0.056177 | 0.21932 | 0.056219 | 6.708e-05 | 4.259e-05 | 0.3292 | 0.3292 | 0.3292 | 0.99235 | -0.1447 | 0.99268 | -0.13839 | 22.6101
106 | 0.21202 | 0.054142 | -0.21172 | -0.053951 | 0.00030237 | 0.00019189 | 0.31921 | 0.31922 | 0.31922 | 0.98945 | -0.2 | 0.98791 | -0.22955 | 21.9241
107 | -0.0025138 | -0.00063001 | 0.0025138 | 0.00063001 | 7.1777e-10 | -1.2496e-09 | 0.0037866 | 0.0037866 | 0.0037866 | 0.98785 | -0.234 | 0.98785 | -0.234 | 1.0403
108 | -0.0050284 | -0.0012602 | 0.005029 | 0.0012603 | 5.7259e-07 | 2.5687e-08 | 0.0075744 | 0.0075743 | 0.0075744 | 0.98785 | -0.234 | 0.98797 | -0.23161 | 2.0809
109 | -0.22268 | -0.057061 | 0.22283 | 0.057159 | 0.00015438 | 9.8038e-05 | 0.33424 | 0.33424 | 0.33424 | 0.99268 | -0.13839 | 0.99343 | -0.12409 | 22.956
110 | 0.21172 | 0.053951 | -0.21154 | -0.053834 | 0.00018314 | 0.00011623 | 0.31922 | 0.31922 | 0.31922 | 0.98791 | -0.22955 | 0.98698 | -0.24749 | 21.9242
111 | -0.0083222 | -0.0020856 | 0.0083232 | 0.0020861 | 1.0337e-06 | 4.3685e-07 | 0.012534 | 0.012534 | 0.012534 | 0.98797 | -0.23161 | 0.9881 | -0.229 | 3.4435
112 | 0.010223 | 0.0025632 | -0.010218 | -0.0025609 | 4.6785e-06 | 2.3172e-06 | 0.015377 | 0.015378 | 0.015378 | 0.98922 | -0.20728 | 0.98873 | -0.21689 | 4.2247
113 | 0.010218 | 0.0025609 | -0.010218 | -0.0025608 | 2.1895e-07 | 1.0846e-07 | 0.015378 | 0.015378 | 0.015378 | 0.98873 | -0.21689 | 0.9887 | -0.21734 | 4.2247
114 | -0.22394 | -0.057437 | 0.22402 | 0.057489 | 8.0896e-05 | 5.1377e-05 | 0.3359 | 0.3359 | 0.3359 | 0.99343 | -0.12409 | 0.99382 | -0.11665 | 23.0701
115 | 0.20926 | 0.053263 | -0.20925 | -0.053259 | 5.7729e-06 | 3.6631e-06 | 0.31578 | 0.31578 | 0.31578 | 0.98698 | -0.24749 | 0.98695 | -0.24806 | 21.688
116 | -0.22567 | -0.057901 | 0.2259 | 0.058049 | 0.00023246 | 0.00014765 | 0.33836 | 0.33836 | 0.33836 | 0.99382 | -0.11665 | 0.99494 | -0.095439 | 23.2393
117 | -0.22779 | -0.058523 | 0.22782 | 0.058538 | 2.4325e-05 | 1.5452e-05 | 0.34119 | 0.34119 | 0.34119 | 0.99494 | -0.095439 | 0.99506 | -0.09324 | 23.4335
118 | -0.23024 | -0.059145 | 0.2303 | 0.059189 | 6.9086e-05 | 4.3893e-05 | 0.34481 | 0.34481 | 0.34481 | 0.99506 | -0.09324 | 0.99538 | -0.087063 | 23.6821
119 | -0.23332 | -0.059944 | 0.23354 | 0.060087 | 0.00022557 | 0.00014334 | 0.34932 | 0.34932 | 0.34932 | 0.99538 | -0.087063 | 0.99643 | -0.067178 | 23.9915
120 | -0.23623 | -0.060759 | 0.23628 | 0.060797 | 5.8656e-05 | 3.7279e-05 | 0.35332 | 0.35332 | 0.35332 | 0.99643 | -0.067178 | 0.9967 | -0.062071 | 24.2665
121 | 0.0073171 | 0.0018338 | -0.0073162 | -0.0018335 | 8.8972e-07 | 3.1539e-07 | 0.010978 | 0.010978 | 0.010978 | 0.99181 | -0.15721 | 0.99168 | -0.15976 | 3.0159
122 | -0.010398 | -0.0026061 | 0.010399 | 0.0026061 | 1.2837e-07 | 6.4004e-08 | 0.015601 | 0.015601 | 0.015601 | 0.99181 | -0.15721 | 0.99182 | -0.15695 | 4.2859
123 | 0.0057378 | 0.0014379 | -0.0057376 | -0.0014379 | 1.8626e-07 | 3.2756e-08 | 0.0086095 | 0.0086096 | 0.0086096 | 0.99168 | -0.15976 | 0.99164 | -0.16044 | 2.3653
124 | -0.01227 | -0.0030752 | 0.012273 | 0.0030769 | 3.1474e-06 | 1.6946e-06 | 0.018409 | 0.018409 | 0.018409 | 0.99182 | -0.15695 | 0.9921 | -0.15157 | 5.0573
125 | 0.0014405 | 0.00036092 | -0.0014405 | -0.00036102 | 1.4744e-08 | -9.9126e-08 | 0.0021615 | 0.0021615 | 0.0021615 | 0.99164 | -0.16044 | 0.99163 | -0.16066 | 0.59383
126 | 0.20727 | 0.052764 | -0.207 | -0.052588 | 0.00027763 | 0.00017614 | 0.3128 | 0.3128 | 0.3128 | 0.98695 | -0.24806 | 0.9855 | -0.27588 | 21.4834
127 | 0.20553 | 0.052221 | -0.2055 | -0.052197 | 3.8284e-05 | 2.4286e-05 | 0.31059 | 0.31059 | 0.31059 | 0.9855 | -0.27588 | 0.9853 | -0.27975 | 21.3318
128 | 0.20367 | 0.051738 | -0.20361 | -0.051701 | 5.8446e-05 | 3.707e-05 | 0.30783 | 0.30783 | 0.30783 | 0.9853 | -0.27975 | 0.98499 | -0.28572 | 21.142
129 | 0.20028 | 0.050867 | -0.2002 | -0.050815 | 8.073e-05 | 5.1189e-05 | 0.3028 | 0.3028 | 0.3028 | 0.98499 | -0.28572 | 0.98456 | -0.2941 | 20.7964
130 | 0.19811 | 0.050292 | -0.19804 | -0.050251 | 6.4688e-05 | 4.1009e-05 | 0.29964 | 0.29964 | 0.29964 | 0.98456 | -0.2941 | 0.98421 | -0.30088 | 20.5799
131 | -0.1862 | -0.047175 | 0.18625 | 0.047208 | 5.336e-05 | 3.3788e-05 | 0.28215 | 0.28215 | 0.28215 | 0.98263 | -0.3315 | 0.98294 | -0.32554 | 19.3782
132 | 0.18373 | 0.046556 | -0.18365 | -0.046502 | 8.5378e-05 | 5.4047e-05 | 0.27841 | 0.27841 | 0.27841 | 0.98263 | -0.3315 | 0.98213 | -0.34118 | 19.1217
133 | -0.18824 | -0.047707 | 0.18833 | 0.047765 | 9.1805e-05 | 5.8144e-05 | 0.28516 | 0.28516 | 0.28516 | 0.98294 | -0.32554 | 0.98346 | -0.31539 | 19.585
134 | 0.17926 | 0.045402 | -0.17921 | -0.04537 | 5.1038e-05 | 3.2291e-05 | 0.27176 | 0.27176 | 0.27176 | 0.98213 | -0.34118 | 0.98182 | -0.34711 | 18.665
135 | -0.19058 | -0.048328 | 0.19058 | 0.048331 | 5.0137e-06 | 3.1762e-06 | 0.28856 | 0.28856 | 0.28856 | 0.98346 | -0.31539 | 0.98349 | -0.31484 | 19.8184
136 | 0.17755 | 0.044956 | -0.17741 | -0.044868 | 0.00013848 | 8.7597e-05 | 0.26926 | 0.26926 | 0.26926 | 0.98182 | -0.34711 | 0.98099 | -0.36337 | 18.4929
137 | -0.19431 | -0.049265 | 0.19433 | 0.049277 | 1.9163e-05 | 1.2144e-05 | 0.29419 | 0.29419 | 0.29419 | 0.98349 | -0.31484 | 0.98359 | -0.31279 | 20.2056
138 | 0.17619 | 0.044561 | -0.17619 | -0.044559 | 1.7963e-06 | 1.1361e-06 | 0.2674 | 0.2674 | 0.2674 | 0.98099 | -0.36337 | 0.98098 | -0.36358 | 18.3651
139 | -0.19646 | -0.049812 | 0.19658 | 0.049884 | 0.00011252 | 7.1324e-05 | 0.29743 | 0.29743 | 0.29743 | 0.98359 | -0.31279 | 0.98421 | -0.30088 | 20.4276
140 | -0.23967 | -0.061646 | 0.23978 | 0.061717 | 0.00011165 | 7.0975e-05 | 0.35838 | 0.35838 | 0.35838 | 0.9967 | -0.062071 | 0.99721 | -0.052493 | 24.6138
141 | -0.24098 | -0.062018 | 0.2414 | 0.062279 | 0.00041053 | 0.00026098 | 0.36017 | 0.36017 | 0.36017 | 0.99721 | -0.052493 | 0.99907 | -0.017528 | 24.7369
142 | -0.24286 | -0.062646 | 0.24296 | 0.062707 | 9.5382e-05 | 6.0638e-05 | 0.36235 | 0.36235 | 0.36235 | 0.99907 | -0.017528 | 0.9995 | -0.0094709 | 24.887
143 | -0.24419 | -0.063015 | 0.24419 | 0.063016 | 1.3983e-06 | 8.8903e-07 | 0.36419 | 0.36419 | 0.36419 | 0.9995 | -0.0094709 | 0.9995 | -0.0093534 | 25.0128
144 | 0.092462 | 0.023477 | -0.09234 | -0.023399 | 0.00012207 | 7.7902e-05 | 0.13769 | 0.13769 | 0.13769 | 1 | 0 | 0.99856 | -0.027477 | 37.8277
145 | 0.24551 | 0.06339 | -0.2454 | -0.063319 | 0.00011192 | 7.1158e-05 | 0.36598 | 0.36598 | 0.36598 | 1 | 0 | 0.9995 | -0.0093534 | 25.1361
146 | 0.091131 | 0.023096 | -0.091119 | -0.023088 | 1.2356e-05 | 7.8843e-06 | 0.13589 | 0.13589 | 0.13589 | 0.99856 | -0.027477 | 0.99841 | -0.030299 | 37.3327
147 | 0.08951 | 0.022685 | -0.08948 | -0.022666 | 2.9632e-05 | 1.8906e-05 | 0.13349 | 0.13349 | 0.13349 | 0.99841 | -0.030299 | 0.99805 | -0.037191 | 36.674

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3415 | 0.087337

## res_load
| p_mw | q_mvar
0 | 0.001518 | 0.00038044
1 | 0.0011766 | 0.00029489
2 | 0.0015004 | 0.00037604
3 | 0.00097269 | 0.00024378
4 | 0.0039138 | 0.00098089
5 | 0.0017659 | 0.00044259
6 | 0.0029135 | 0.00073019
7 | 0.0032005 | 0.00080213
8 | 0.0026356 | 0.00066053
9 | 0.001798 | 0.00045061
10 | 0.0018731 | 0.00046945
11 | 0.0011159 | 0.00027967
12 | 0.0020859 | 0.00052278
13 | 0.0020077 | 0.00050318
14 | 0.0016155 | 0.00040488
15 | 0.0030881 | 0.00077394
16 | 0.0091675 | 0.0022976
17 | 0.0014053 | 0.0003522
18 | 0.0016095 | 0.00040338
19 | 0.0023162 | 0.00058049
20 | 0.0020508 | 0.00051398
21 | 0.0037286 | 0.00093449
22 | 0.0053816 | 0.0013487
23 | 0.009185 | 0.002302
24 | 0.0030414 | 0.00076225
25 | 0.0021846 | 0.0005475
26 | 0.0023608 | 0.00059168
27 | 0.010096 | 0.0025304
28 | 0.0025244 | 0.00063267
29 | 0.0019968 | 0.00050045
30 | 0.0007701 | 0.000193
31 | 0.00078436 | 0.00019658
32 | 0.0014275 | 0.00035777
33 | 0.00085574 | 0.00021447
34 | 0.0011121 | 0.00027872
35 | 0.00043675 | 0.00010946
36 | 0.0038969 | 0.00097665
37 | 0.0015692 | 0.00039329
38 | 0.00090195 | 0.00022605
39 | 0.0022071 | 0.00055314
40 | 0.00050908 | 0.00012759
41 | 0.0017129 | 0.00042929
42 | 0.0010609 | 0.00026589
43 | 0.0074587 | 0.0018693
44 | 0.0033776 | 0.0008465
45 | 0.0014689 | 0.00036814
46 | 0.0018848 | 0.00047238
47 | 0.00071141 | 0.0001783
48 | 0.00029535 | 7.4021e-05
49 | 0.014121 | 0.003539
50 | 0.014128 | 0.0035407
51 | 0.012508 | 0.0031347
52 | 0.014295 | 0.0035827
53 | 0.0067496 | 0.0016916
54 | 0.0052181 | 0.0013078
55 | 0.010177 | 0.0025505
56 | 0.0062334 | 0.0015622
57 | 0.0018527 | 0.00046433
58 | 0.0031853 | 0.00079831
59 | 0.0023955 | 0.00060037
60 | 0.0019162 | 0.00048024
61 | 0.0028132 | 0.00070506
62 | 0.0026932 | 0.00067499
63 | 0.0015814 | 0.00039633
64 | 0.00082383 | 0.00020647
65 | 0.00081889 | 0.00020523
66 | 0.0034254 | 0.0008585
67 | 0.0025138 | 0.00063001
68 | 0.0025147 | 0.00063023
69 | 0.0033599 | 0.00084208
70 | 0.0032932 | 0.00082535
71 | 0.0028225 | 0.00070739
72 | 0.010218 | 0.0025608
73 | 0.0011091 | 0.00027796
74 | 0.0022807 | 0.0005716
75 | 0.0016453 | 0.00041236
76 | 0.001891 | 0.00047393
77 | 0.0024201 | 0.00060654
78 | 0.0030139 | 0.00075534
79 | 0.0026818 | 0.00067212
80 | 0.0010323 | 0.00025872
81 | 0.0030813 | 0.00077225
82 | 0.0015785 | 0.0003956
83 | 0.0018715 | 0.00046905
84 | 0.0042971 | 0.001077
85 | 0.002738 | 0.0006862
86 | 0.0014405 | 0.00036102
87 | 0.0019764 | 0.00049532
88 | 0.0014617 | 0.00036634
89 | 0.0018299 | 0.00045861
90 | 0.0033308 | 0.00083478
91 | 0.0017292 | 0.00043339
92 | 0.0020866 | 0.00052295
93 | 0.00069724 | 0.00017474
94 | 0.0024666 | 0.00061819
95 | 0.0019886 | 0.0004984
96 | 0.0043892 | 0.0011
97 | 0.0022469 | 0.00056312
98 | 0.0016532 | 0.00041433
99 | 0.0037259 | 0.0009338
100 | 0.0012269 | 0.00030748
101 | 0.002136 | 0.00053534
102 | 0.0012118 | 0.00030369
103 | 0.0014669 | 0.00036764
104 | 0.0033874 | 0.00084896
105 | 0.0012013 | 0.00030108
106 | 0.0014673 | 0.00036774
107 | 0.0012302 | 0.00030832
108 | 0.0018781 | 0.0004707
109 | 0.0012091 | 0.00030304
110 | 0.0012063 | 0.00030233
111 | 0.0016088 | 0.00040321
112 | 0.0019134 | 0.00047954

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1