## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2493-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2493-7_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2493-7_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2493-7_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2493-7_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_2493-7_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_2493-7_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2493-7_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2493-7_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_2493-7_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_2493-7_0_4_node_77 | 0.4 | n |  | TRUE
11 | bus_LV_2493-7_0_4_node_75 | 0.4 | n |  | TRUE
12 | bus_LV_2493-7_0_4_node_124 | 0.4 | n |  | TRUE
13 | bus_LV_2493-7_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2493-7_0_4_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_2493-7_0_4_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_2493-7_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2493-7_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2493-7_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_2493-7_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2493-7_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2493-7_0_4_node_60 | 0.4 | n |  | TRUE
22 | bus_LV_2493-7_0_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_2493-7_0_4_node_127 | 0.4 | n |  | TRUE
24 | bus_LV_2493-7_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_2493-7_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_2493-7_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2493-7_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2493-7_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_2493-7_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_2493-7_0_4_node_98 | 0.4 | n |  | TRUE
31 | bus_LV_2493-7_0_4_node_106 | 0.4 | n |  | TRUE
32 | bus_LV_2493-7_0_4_node_111 | 0.4 | n |  | TRUE
33 | bus_LV_2493-7_0_4_node_99 | 0.4 | n |  | TRUE
34 | bus_LV_2493-7_0_4_node_105 | 0.4 | n |  | TRUE
35 | bus_LV_2493-7_0_4_node_110 | 0.4 | n |  | TRUE
36 | bus_LV_2493-7_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_2493-7_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_2493-7_0_4_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_2493-7_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_2493-7_0_4_node_93 | 0.4 | n |  | TRUE
41 | bus_LV_2493-7_0_4_node_115 | 0.4 | n |  | TRUE
42 | bus_LV_2493-7_0_4_node_119 | 0.4 | n |  | TRUE
43 | bus_LV_2493-7_0_4_node_122 | 0.4 | n |  | TRUE
44 | bus_LV_2493-7_0_4_node_123 | 0.4 | n |  | TRUE
45 | bus_LV_2493-7_0_4_node_92 | 0.4 | n |  | TRUE
46 | bus_LV_2493-7_0_4_node_116 | 0.4 | n |  | TRUE
47 | bus_LV_2493-7_0_4_node_120 | 0.4 | n |  | TRUE
48 | bus_LV_2493-7_0_4_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_2493-7_0_4_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_2493-7_0_4_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_2493-7_0_4_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_2493-7_0_4_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_2493-7_0_4_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_2493-7_0_4_node_139 | 0.4 | n |  | TRUE
55 | bus_LV_2493-7_0_4_node_112 | 0.4 | n |  | TRUE
56 | bus_LV_2493-7_0_4_node_141 | 0.4 | n |  | TRUE
57 | bus_LV_2493-7_0_4_node_113 | 0.4 | n |  | TRUE
58 | bus_LV_2493-7_0_4_node_114 | 0.4 | n |  | TRUE
59 | bus_LV_2493-7_0_4_node_140 | 0.4 | n |  | TRUE
60 | bus_LV_2493-7_0_4_node_35 | 0.4 | n |  | TRUE
61 | bus_LV_2493-7_0_4_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_2493-7_0_4_node_37 | 0.4 | n |  | TRUE
63 | bus_LV_2493-7_0_4_node_38 | 0.4 | n |  | TRUE
64 | bus_LV_2493-7_0_4_node_39 | 0.4 | n |  | TRUE
65 | bus_LV_2493-7_0_4_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_2493-7_0_4_node_80 | 0.4 | n |  | TRUE
67 | bus_LV_2493-7_0_4_node_84 | 0.4 | n |  | TRUE
68 | bus_LV_2493-7_0_4_node_83 | 0.4 | n |  | TRUE
69 | bus_LV_2493-7_0_4_node_47 | 0.4 | n |  | TRUE
70 | bus_LV_2493-7_0_4_node_81 | 0.4 | n |  | TRUE
71 | bus_LV_2493-7_0_4_node_82 | 0.4 | n |  | TRUE
72 | bus_LV_2493-7_0_4_node_45 | 0.4 | n |  | TRUE
73 | bus_LV_2493-7_0_4_node_41 | 0.4 | n |  | TRUE
74 | bus_LV_2493-7_0_4_node_42 | 0.4 | n |  | TRUE
75 | bus_LV_2493-7_0_4_node_43 | 0.4 | n |  | TRUE
76 | bus_LV_2493-7_0_4_node_44 | 0.4 | n |  | TRUE
77 | bus_LV_2493-7_0_4_node_46 | 0.4 | n |  | TRUE
78 | bus_LV_2493-7_0_4_node_57 | 0.4 | n |  | TRUE
79 | bus_LV_2493-7_0_4_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_2493-7_0_4_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_2493-7_0_4_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_2493-7_0_4_node_48 | 0.4 | n |  | TRUE
83 | bus_LV_2493-7_0_4_node_49 | 0.4 | n |  | TRUE
84 | bus_LV_2493-7_0_4_node_51 | 0.4 | n |  | TRUE
85 | bus_LV_2493-7_0_4_node_50 | 0.4 | n |  | TRUE
86 | bus_LV_2493-7_0_4_node_52 | 0.4 | n |  | TRUE
87 | bus_LV_2493-7_0_4_node_73 | 0.4 | n |  | TRUE
88 | bus_LV_2493-7_0_4_node_100 | 0.4 | n |  | TRUE
89 | bus_LV_2493-7_0_4_node_137 | 0.4 | n |  | TRUE
90 | bus_LV_2493-7_0_4_node_103 | 0.4 | n |  | TRUE
91 | bus_LV_2493-7_0_4_node_71 | 0.4 | n |  | TRUE
92 | bus_LV_2493-7_0_4_node_88 | 0.4 | n |  | TRUE
93 | bus_LV_2493-7_0_4_node_138 | 0.4 | n |  | TRUE
94 | bus_LV_2493-7_0_4_node_53 | 0.4 | n |  | TRUE
95 | bus_LV_2493-7_0_4_node_54 | 0.4 | n |  | TRUE
96 | bus_LV_2493-7_0_4_node_55 | 0.4 | n |  | TRUE
97 | bus_LV_2493-7_0_4_node_56 | 0.4 | n |  | TRUE
98 | bus_LV_2493-7_0_4_node_121 | 0.4 | n |  | TRUE
99 | bus_LV_2493-7_0_4_node_59 | 0.4 | n |  | TRUE
100 | bus_LV_2493-7_0_4_node_129 | 0.4 | n |  | TRUE
101 | bus_LV_2493-7_0_4_node_126 | 0.4 | n |  | TRUE
102 | bus_LV_2493-7_0_4_node_132 | 0.4 | n |  | TRUE
103 | bus_LV_2493-7_0_4_node_61 | 0.4 | n |  | TRUE
104 | bus_LV_2493-7_0_4_node_62 | 0.4 | n |  | TRUE
105 | bus_LV_2493-7_0_4_node_65 | 0.4 | n |  | TRUE
106 | bus_LV_2493-7_0_4_node_66 | 0.4 | n |  | TRUE
107 | bus_LV_2493-7_0_4_node_67 | 0.4 | n |  | TRUE
108 | bus_LV_2493-7_0_4_node_68 | 0.4 | n |  | TRUE
109 | bus_LV_2493-7_0_4_node_69 | 0.4 | n |  | TRUE
110 | bus_LV_2493-7_0_4_node_95 | 0.4 | n |  | TRUE
111 | bus_LV_2493-7_0_4_node_96 | 0.4 | n |  | TRUE
112 | bus_LV_2493-7_0_4_node_70 | 0.4 | n |  | TRUE
113 | bus_LV_2493-7_0_4_node_72 | 0.4 | n |  | TRUE
114 | bus_LV_2493-7_0_4_node_74 | 0.4 | n |  | TRUE
115 | bus_LV_2493-7_0_4_node_131 | 0.4 | n |  | TRUE
116 | bus_LV_2493-7_0_4_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_2493-7_0_4_node_130 | 0.4 | n |  | TRUE
118 | bus_LV_2493-7_0_4_node_79 | 0.4 | n |  | TRUE
119 | bus_LV_2493-7_0_4_node_142 | 0.4 | n |  | TRUE
120 | bus_LV_2493-7_0_4_node_109 | 0.4 | n |  | TRUE
121 | bus_LV_2493-7_0_4_node_85 | 0.4 | n |  | TRUE
122 | bus_LV_2493-7_0_4_node_86 | 0.4 | n |  | TRUE
123 | bus_LV_2493-7_0_4_node_87 | 0.4 | n |  | TRUE
124 | bus_LV_2493-7_0_4_node_89 | 0.4 | n |  | TRUE
125 | bus_LV_2493-7_0_4_node_136 | 0.4 | n |  | TRUE
126 | bus_LV_2493-7_0_4_node_91 | 0.4 | n |  | TRUE
127 | bus_LV_2493-7_0_4_node_135 | 0.4 | n |  | TRUE
128 | bus_LV_2493-7_0_4_node_90 | 0.4 | n |  | TRUE
129 | bus_LV_2493-7_0_4_node_94 | 0.4 | n |  | TRUE
130 | bus_LV_2493-7_0_4_node_125 | 0.4 | n |  | TRUE
131 | bus_LV_2493-7_0_4_node_118 | 0.4 | n |  | TRUE
132 | bus_LV_2493-7_0_4_node_97 | 0.4 | n |  | TRUE
133 | bus_LV_2493-7_0_4_node_107 | 0.4 | n |  | TRUE
134 | bus_LV_2493-7_0_4_node_102 | 0.4 | n |  | TRUE
135 | bus_LV_2493-7_0_4_node_104 | 0.4 | n |  | TRUE
136 | bus_LV_2493-7_0_4_node_108 | 0.4 | n |  | TRUE
137 | bus_LV_2493-7_0_4_node_117 | 0.4 | n |  | TRUE
138 | bus_LV_2493-7_0_4_node_128 | 0.4 | n |  | TRUE
139 | bus_LV_2493-7_0_4_node_134 | 0.4 | n |  | TRUE
140 | bus_MV_291_1_node_71 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2493-7_0_4_load_0 | 0 | 0.009492 | 0.0023789 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2493-7_0_4_load_2 | 2 | 0.029053 | 0.0072813 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2493-7_0_4_load_3 | 3 | 0.0038404 | 0.0009625 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2493-7_0_4_load_8 | 5 | 0.00041185 | 0.00010322 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2493-7_0_4_load_9 | 8 | 0.00093325 | 0.00023389 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2493-7_0_4_load_4 | 9 | 0.0032028 | 0.0008027 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2493-7_0_4_load_77 | 10 | 0.0016829 | 0.00042178 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2493-7_0_4_load_75 | 11 | 0.0021162 | 0.00053036 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2493-7_0_4_load_124 | 12 | 0.0028012 | 0.00070205 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2493-7_0_4_load_10 | 13 | 0.0020655 | 0.00051766 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2493-7_0_4_load_26 | 15 | 0.0015274 | 0.00038279 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2493-7_0_4_load_11 | 16 | 0.0034431 | 0.00086292 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2493-7_0_4_load_12 | 17 | 0.0021839 | 0.00054734 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2493-7_0_4_load_13 | 18 | 0.0020822 | 0.00052185 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2493-7_0_4_load_14 | 19 | 0.0012591 | 0.00031556 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2493-7_0_4_load_15 | 20 | 0.0020045 | 0.00050237 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2493-7_0_4_load_19 | 22 | 0.0019838 | 0.00049719 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2493-7_0_4_load_127 | 23 | 0.0020316 | 0.00050917 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2493-7_0_4_load_17 | 24 | 0.0023016 | 0.00057684 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2493-7_0_4_load_16 | 25 | 0.0033444 | 0.00083819 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2493-7_0_4_load_20 | 27 | 0.0055972 | 0.0014028 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2493-7_0_4_load_21 | 28 | 0.0055787 | 0.0013982 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2493-7_0_4_load_22 | 29 | 0.0021599 | 0.00054133 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2493-7_0_4_load_98 | 30 | 0.0021824 | 0.00054697 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2493-7_0_4_load_106 | 31 | 0.0035925 | 0.00090036 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2493-7_0_4_load_111 | 32 | 0.0035808 | 0.00089744 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2493-7_0_4_load_99 | 33 | 0.0029519 | 0.00073982 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2493-7_0_4_load_105 | 34 | 0.0033746 | 0.00084577 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2493-7_0_4_load_110 | 35 | 0.0031556 | 0.00079087 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2493-7_0_4_load_23 | 36 | 0.0042628 | 0.0010684 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2493-7_0_4_load_28 | 39 | 0.0010072 | 0.00025242 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2493-7_0_4_load_93 | 40 | 0.00077764 | 0.0001949 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2493-7_0_4_load_115 | 41 | 0.025812 | 0.0064692 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2493-7_0_4_load_119 | 42 | 0.00078874 | 0.00019768 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2493-7_0_4_load_122 | 43 | 0.0032431 | 0.00081279 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2493-7_0_4_load_123 | 44 | 0.0018192 | 0.00045594 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2493-7_0_4_load_116 | 46 | 0.015671 | 0.0039275 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2493-7_0_4_load_120 | 47 | 0.0019746 | 0.00049489 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2493-7_0_4_load_29 | 48 | 0.0016321 | 0.00040904 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2493-7_0_4_load_32 | 51 | 0.0010168 | 0.00025483 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2493-7_0_4_load_33 | 52 | 0.0021569 | 0.00054058 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2493-7_0_4_load_34 | 53 | 0.0039733 | 0.0009958 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2493-7_0_4_load_139 | 54 | 0.0049049 | 0.0012293 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2493-7_0_4_load_113 | 57 | 0.00070333 | 0.00017627 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2493-7_0_4_load_114 | 58 | 0.00694 | 0.0017393 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2493-7_0_4_load_140 | 59 | 0.0068222 | 0.0017098 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2493-7_0_4_load_35 | 60 | 0.0013646 | 0.00034201 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2493-7_0_4_load_36 | 61 | 0.0024572 | 0.00061583 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2493-7_0_4_load_38 | 63 | 0.0029675 | 0.00074373 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2493-7_0_4_load_40 | 65 | 0.00089113 | 0.00022334 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2493-7_0_4_load_84 | 67 | 0.0051362 | 0.0012873 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2493-7_0_4_load_83 | 68 | 0.0020699 | 0.00051878 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2493-7_0_4_load_47 | 69 | 0.0017548 | 0.0004398 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2493-7_0_4_load_81 | 70 | 0.0028376 | 0.00071118 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2493-7_0_4_load_82 | 71 | 0.0050084 | 0.0012552 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2493-7_0_4_load_45 | 72 | 0.0032275 | 0.00080888 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2493-7_0_4_load_41 | 73 | 0.0014943 | 0.00037452 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2493-7_0_4_load_42 | 74 | 0.0025808 | 0.00064681 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2493-7_0_4_load_44 | 76 | 0.0025687 | 0.00064378 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2493-7_0_4_load_57 | 78 | 0.0033471 | 0.00083886 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2493-7_0_4_load_64 | 79 | 0.0019009 | 0.00047641 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2493-7_0_4_load_58 | 80 | 0.0074788 | 0.0018744 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2493-7_0_4_load_63 | 81 | 0.0017152 | 0.00042987 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2493-7_0_4_load_48 | 82 | 0.00069562 | 0.00017434 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2493-7_0_4_load_49 | 83 | 0.00045972 | 0.00011522 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2493-7_0_4_load_50 | 85 | 0.0026145 | 0.00065525 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2493-7_0_4_load_52 | 86 | 0.00078317 | 0.00019628 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2493-7_0_4_load_100 | 88 | 0.01127 | 0.0028246 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2493-7_0_4_load_103 | 90 | 0.0019091 | 0.00047847 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2493-7_0_4_load_71 | 91 | 0.0012994 | 0.00032567 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2493-7_0_4_load_138 | 93 | 0.0014013 | 0.0003512 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2493-7_0_4_load_53 | 94 | 0.0020282 | 0.00050831 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2493-7_0_4_load_54 | 95 | 0.0024563 | 0.00061562 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2493-7_0_4_load_55 | 96 | 0.0021276 | 0.00053323 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2493-7_0_4_load_56 | 97 | 0.0016351 | 0.00040979 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2493-7_0_4_load_59 | 99 | 0.0024176 | 0.0006059 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2493-7_0_4_load_129 | 100 | 0.0023388 | 0.00058617 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2493-7_0_4_load_132 | 102 | 0.0010874 | 0.00027252 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2493-7_0_4_load_61 | 103 | 0.0018683 | 0.00046825 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2493-7_0_4_load_62 | 104 | 0.0018679 | 0.00046814 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2493-7_0_4_load_65 | 105 | 0.0011468 | 0.00028741 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2493-7_0_4_load_66 | 106 | 0.0009223 | 0.00023115 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2493-7_0_4_load_67 | 107 | 0.0013311 | 0.00033359 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2493-7_0_4_load_68 | 108 | 0.0024581 | 0.00061607 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2493-7_0_4_load_69 | 109 | 0.00068912 | 0.00017271 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2493-7_0_4_load_95 | 110 | 0.0010656 | 0.00026706 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2493-7_0_4_load_96 | 111 | 0.0019111 | 0.00047897 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2493-7_0_4_load_70 | 112 | 0.002727 | 0.00068345 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2493-7_0_4_load_72 | 113 | 0.0019077 | 0.00047811 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2493-7_0_4_load_74 | 114 | 0.0035996 | 0.00090215 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2493-7_0_4_load_131 | 115 | 0.002144 | 0.00053734 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2493-7_0_4_load_101 | 116 | 0.0058894 | 0.001476 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2493-7_0_4_load_130 | 117 | 0.0025024 | 0.00062717 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2493-7_0_4_load_79 | 118 | 0.0069369 | 0.0017385 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2493-7_0_4_load_109 | 120 | 0.0097669 | 0.0024478 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2493-7_0_4_load_85 | 121 | 0.0028718 | 0.00071975 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2493-7_0_4_load_86 | 122 | 0.0028937 | 0.00072522 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2493-7_0_4_load_87 | 123 | 0.0053417 | 0.0013388 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2493-7_0_4_load_136 | 125 | 0.0041204 | 0.0010327 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2493-7_0_4_load_91 | 126 | 0.0013883 | 0.00034793 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2493-7_0_4_load_90 | 128 | 0.0064594 | 0.0016189 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2493-7_0_4_load_94 | 129 | 0.0012896 | 0.00032321 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2493-7_0_4_load_125 | 130 | 0.00099813 | 0.00025016 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2493-7_0_4_load_118 | 131 | 0.0010798 | 0.00027061 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2493-7_0_4_load_97 | 132 | 0.0033518 | 0.00084004 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2493-7_0_4_load_107 | 133 | 0.0017199 | 0.00043106 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2493-7_0_4_load_102 | 134 | 0.0035556 | 0.00089111 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2493-7_0_4_load_104 | 135 | 0.0058618 | 0.0014691 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2493-7_0_4_load_108 | 136 | 0.0028419 | 0.00071225 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2493-7_0_4_load_117 | 137 | 0.00070525 | 0.00017675 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2493-7_0_4_load_128 | 138 | 0.0017089 | 0.0004283 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2493-7_0_4_load_134 | 139 | 0.0033764 | 0.00084621 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 121 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2493-7_0_4_line_0 |  | 0 | 1 | 0.080041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2493-7_0_4_line_1 |  | 1 | 2 | 0.035192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2493-7_0_4_line_2 |  | 1 | 3 | 0.052842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2493-7_0_4_line_3 |  | 2 | 4 | 0.068025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2493-7_0_4_line_4 |  | 3 | 5 | 0.056721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2493-7_0_4_line_5 |  | 4 | 6 | 0.01455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2493-7_0_4_line_6 |  | 4 | 7 | 0.075086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2493-7_0_4_line_7 |  | 5 | 8 | 0.027229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2493-7_0_4_line_8 |  | 6 | 10 | 0.019409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2493-7_0_4_line_9 |  | 6 | 11 | 0.036329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2493-7_0_4_line_10 |  | 7 | 9 | 0.022488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2493-7_0_4_line_11 |  | 8 | 13 | 0.033054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2493-7_0_4_line_12 |  | 10 | 12 | 0.006708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2493-7_0_4_line_13 |  | 12 | 98 | 0.029751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2493-7_0_4_line_14 |  | 13 | 14 | 0.038116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2493-7_0_4_line_15 |  | 14 | 15 | 0.027522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2493-7_0_4_line_16 |  | 15 | 43 | 0.0070072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2493-7_0_4_line_17 |  | 16 | 17 | 0.0058043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2493-7_0_4_line_18 |  | 16 | 18 | 0.015662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2493-7_0_4_line_19 |  | 17 | 19 | 0.0095675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2493-7_0_4_line_20 |  | 18 | 20 | 0.012259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2493-7_0_4_line_21 |  | 19 | 21 | 0.023245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2493-7_0_4_line_22 |  | 20 | 22 | 0.0007047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2493-7_0_4_line_23 |  | 21 | 23 | 0.013132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2493-7_0_4_line_24 |  | 22 | 24 | 0.01238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2493-7_0_4_line_25 |  | 23 | 102 | 0.038925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2493-7_0_4_line_26 |  | 24 | 25 | 0.012633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2493-7_0_4_line_27 |  | 25 | 26 | 0.027722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2493-7_0_4_line_28 |  | 26 | 27 | 0.036497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2493-7_0_4_line_29 |  | 26 | 28 | 0.018056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2493-7_0_4_line_30 |  | 26 | 29 | 0.020213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2493-7_0_4_line_31 |  | 27 | 30 | 0.0020796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2493-7_0_4_line_32 |  | 28 | 31 | 0.0022859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2493-7_0_4_line_33 |  | 29 | 32 | 0.0022979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2493-7_0_4_line_34 |  | 30 | 33 | 0.023272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2493-7_0_4_line_35 |  | 31 | 34 | 0.022391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2493-7_0_4_line_36 |  | 32 | 35 | 0.020871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2493-7_0_4_line_37 |  | 33 | 133 | 0.0021937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2493-7_0_4_line_38 |  | 34 | 135 | 0.0093769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2493-7_0_4_line_39 |  | 35 | 77 | 0.019615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2493-7_0_4_line_40 |  | 36 | 37 | 0.021521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2493-7_0_4_line_41 |  | 37 | 38 | 0.015127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_2493-7_0_4_line_42 |  | 37 | 39 | 0.035893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_2493-7_0_4_line_43 |  | 38 | 40 | 0.0099429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_2493-7_0_4_line_44 |  | 38 | 41 | 0.065368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2493-7_0_4_line_45 |  | 39 | 42 | 0.01809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_2493-7_0_4_line_46 |  | 40 | 45 | 0.032475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_2493-7_0_4_line_47 |  | 41 | 46 | 0.024222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2493-7_0_4_line_48 |  | 42 | 47 | 0.026506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_2493-7_0_4_line_49 |  | 43 | 44 | 0.016724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2493-7_0_4_line_50 |  | 45 | 129 | 0.02526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2493-7_0_4_line_51 |  | 45 | 128 | 0.0099095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_2493-7_0_4_line_52 |  | 47 | 98 | 0.042017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_2493-7_0_4_line_53 |  | 48 | 49 | 0.031588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2493-7_0_4_line_54 |  | 48 | 50 | 0.012992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2493-7_0_4_line_55 |  | 49 | 51 | 0.011282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2493-7_0_4_line_56 |  | 50 | 52 | 0.013743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2493-7_0_4_line_57 |  | 50 | 53 | 0.027239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2493-7_0_4_line_58 |  | 51 | 54 | 0.036865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2493-7_0_4_line_59 |  | 52 | 55 | 0.019121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2493-7_0_4_line_60 |  | 53 | 56 | 0.024341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2493-7_0_4_line_61 |  | 55 | 57 | 0.011298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2493-7_0_4_line_62 |  | 55 | 58 | 0.026487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2493-7_0_4_line_63 |  | 56 | 59 | 0.027746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2493-7_0_4_line_64 |  | 57 | 137 | 0.0053124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2493-7_0_4_line_65 |  | 58 | 119 | 0.02932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2493-7_0_4_line_66 |  | 60 | 61 | 0.00072395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2493-7_0_4_line_67 |  | 60 | 62 | 0.016169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2493-7_0_4_line_68 |  | 61 | 63 | 0.022419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2493-7_0_4_line_69 |  | 62 | 64 | 0.001502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2493-7_0_4_line_70 |  | 62 | 65 | 0.025548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2493-7_0_4_line_71 |  | 63 | 66 | 0.034639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2493-7_0_4_line_72 |  | 64 | 67 | 0.048215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2493-7_0_4_line_73 |  | 64 | 68 | 0.017859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2493-7_0_4_line_74 |  | 65 | 69 | 0.010269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2493-7_0_4_line_75 |  | 66 | 70 | 0.015683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2493-7_0_4_line_76 |  | 66 | 71 | 0.014894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2493-7_0_4_line_77 |  | 69 | 72 | 0.0093391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2493-7_0_4_line_78 |  | 70 | 120 | 0.01918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2493-7_0_4_line_79 |  | 72 | 75 | 0.0060122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2493-7_0_4_line_80 |  | 73 | 74 | 0.01582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2493-7_0_4_line_81 |  | 73 | 75 | 0.015459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2493-7_0_4_line_82 |  | 74 | 76 | 0.013169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2493-7_0_4_line_83 |  | 75 | 77 | 0.01533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2493-7_0_4_line_84 |  | 76 | 78 | 0.016658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2493-7_0_4_line_85 |  | 77 | 79 | 0.017531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2493-7_0_4_line_86 |  | 78 | 80 | 0.0087362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2493-7_0_4_line_87 |  | 79 | 81 | 0.02115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2493-7_0_4_line_88 |  | 80 | 99 | 0.0072816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2493-7_0_4_line_89 |  | 81 | 103 | 0.021157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2493-7_0_4_line_90 |  | 82 | 83 | 0.0063648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2493-7_0_4_line_91 |  | 83 | 84 | 0.029286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2493-7_0_4_line_92 |  | 84 | 87 | 0.024078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
93 | LV_2493-7_0_4_line_93 |  | 84 | 88 | 0.0074459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_2493-7_0_4_line_94 |  | 85 | 86 | 0.032998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2493-7_0_4_line_95 |  | 86 | 89 | 0.01088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2493-7_0_4_line_96 |  | 87 | 90 | 0.012284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_2493-7_0_4_line_97 |  | 87 | 91 | 0.016201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2493-7_0_4_line_98 |  | 88 | 92 | 0.04623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_2493-7_0_4_line_99 |  | 89 | 93 | 0.021924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2493-7_0_4_line_100 |  | 90 | 116 | 0.0024039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_2493-7_0_4_line_101 |  | 91 | 112 | 0.010196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2493-7_0_4_line_102 |  | 92 | 122 | 0.020434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_2493-7_0_4_line_103 |  | 93 | 108 | 0.022511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2493-7_0_4_line_104 |  | 94 | 95 | 0.013951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2493-7_0_4_line_105 |  | 94 | 96 | 0.00043432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2493-7_0_4_line_106 |  | 95 | 97 | 0.012591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2493-7_0_4_line_107 |  | 97 | 98 | 0.015512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2493-7_0_4_line_108 |  | 99 | 100 | 0.028395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2493-7_0_4_line_109 |  | 100 | 101 | 0.027062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2493-7_0_4_line_110 |  | 101 | 136 | 0.0015237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2493-7_0_4_line_111 |  | 103 | 104 | 0.023057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2493-7_0_4_line_112 |  | 105 | 106 | 0.018747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2493-7_0_4_line_113 |  | 105 | 107 | 0.011331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2493-7_0_4_line_114 |  | 106 | 108 | 0.0062363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2493-7_0_4_line_115 |  | 107 | 109 | 0.010114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2493-7_0_4_line_116 |  | 109 | 110 | 0.0059997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2493-7_0_4_line_117 |  | 110 | 111 | 0.010654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2493-7_0_4_line_118 |  | 111 | 132 | 0.015027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2493-7_0_4_line_119 |  | 112 | 113 | 0.0048633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2493-7_0_4_line_120 |  | 113 | 114 | 0.0119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2493-7_0_4_line_121 |  | 114 | 115 | 0.0059163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2493-7_0_4_line_122 |  | 115 | 117 | 0.004988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2493-7_0_4_line_123 |  | 116 | 134 | 0.016448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2493-7_0_4_line_124 |  | 117 | 132 | 0.0011902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2493-7_0_4_line_125 |  | 118 | 119 | 0.028369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2493-7_0_4_line_126 |  | 121 | 122 | 0.038138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
127 | LV_2493-7_0_4_line_127 |  | 121 | 123 | 0.051469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
128 | LV_2493-7_0_4_line_128 |  | 123 | 124 | 0.022621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
129 | LV_2493-7_0_4_line_129 |  | 124 | 125 | 0.034103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2493-7_0_4_line_130 |  | 124 | 126 | 0.034806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
131 | LV_2493-7_0_4_line_131 |  | 125 | 127 | 0.0023074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2493-7_0_4_line_132 |  | 126 | 128 | 0.022942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
133 | LV_2493-7_0_4_line_133 |  | 127 | 139 | 0.02307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2493-7_0_4_line_134 |  | 129 | 130 | 0.007143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2493-7_0_4_line_135 |  | 130 | 131 | 0.015265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2493-7_0_4_line_136 |  | 131 | 137 | 0.02883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2493-7_0_4_line_137 |  | 134 | 135 | 0.0027604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2493-7_0_4_line_138 |  | 138 | 139 | 0.0025982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2493-7_0_4_trafo_85 | 0.63 MVA 20/0.4 kV | 140 | 121 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2638861.5763 | 1247607.312 | 2638897.9898 | 1247536.033
1 | 2638861.5763 | 1247607.312 | 2638845.561 | 1247638.6486
2 | 2638861.5763 | 1247607.312 | 2638815.2194 | 1247581.949
3 | 2638813.4304 | 1247698.6017 | 2638822.8148 | 1247681.7186 | 2638838.9623 | 1247651.5599 | 2638845.561 | 1247638.6486
4 | 2638764.992 | 1247555.5969 | 2638812.3988 | 1247580.4058 | 2638815.2194 | 1247581.949
5 | 2638807.227 | 1247711.7699 | 2638813.4304 | 1247698.6017
6 | 2638813.4304 | 1247698.6017 | 2638880.1768 | 1247732.9946
7 | 2638740.8671 | 1247542.9718 | 2638764.992 | 1247555.5969
8 | 2638807.227 | 1247711.7699 | 2638790.0594 | 1247702.7156
9 | 2638807.227 | 1247711.7699 | 2638791.5486 | 1247744.5418
10 | 2638880.1768 | 1247732.9946 | 2638891.0762 | 1247739.6371 | 2638899.6193 | 1247744.2825
11 | 2638740.8671 | 1247542.9718 | 2638720.101 | 1247532.1045 | 2638711.5506 | 1247527.7042
12 | 2638784.126 | 1247699.5864 | 2638790.0594 | 1247702.7156
13 | 2638757.8104 | 1247685.7075 | 2638784.126 | 1247699.5864
14 | 2638677.2411 | 1247511.3558 | 2638682.3981 | 1247512.7014 | 2638711.5506 | 1247527.7042
15 | 2638677.2411 | 1247511.3558 | 2638680.3597 | 1247494.0536 | 2638682.9253 | 1247484.4494
16 | 2638682.9253 | 1247484.4494 | 2638684.3001 | 1247479.3029 | 2638684.7067 | 1247477.6726
17 | 2638371.4681 | 1247548.0521 | 2638372.3 | 1247548.9015 | 2638375.555 | 1247552.1736
18 | 2638386.6009 | 1247563.2776 | 2638375.555 | 1247552.1736
19 | 2638371.4681 | 1247548.0521 | 2638364.7736 | 1247541.2167
20 | 2638386.6009 | 1247563.2776 | 2638390.6009 | 1247567.2986 | 2638395.2208 | 1247571.9939
21 | 2638348.5088 | 1247524.6095 | 2638364.7736 | 1247541.2167
22 | 2638395.2208 | 1247571.9939 | 2638395.7151 | 1247572.4963
23 | 2638348.5088 | 1247524.6095 | 2638357.3521 | 1247514.9016
24 | 2638395.7151 | 1247572.4963 | 2638404.3977 | 1247581.3206
25 | 2638357.3521 | 1247514.9016 | 2638368.848 | 1247502.2818 | 2638375.9258 | 1247498.5917 | 2638387.4302 | 1247506.3436
26 | 2638413.1943 | 1247590.386 | 2638411.2338 | 1247588.2682 | 2638404.3977 | 1247581.3206
27 | 2638431.8938 | 1247610.8501 | 2638424.5908 | 1247602.6975 | 2638413.1943 | 1247590.386
28 | 2638431.8938 | 1247610.8501 | 2638440.9016 | 1247622.8052 | 2638454.0406 | 1247639.859
29 | 2638431.8938 | 1247610.8501 | 2638444.9095 | 1247598.3356
30 | 2638431.8938 | 1247610.8501 | 2638416.956 | 1247624.4676
31 | 2638454.0406 | 1247639.859 | 2638455.3098 | 1247641.5064
32 | 2638444.9095 | 1247598.3356 | 2638446.5572 | 1247596.7513
33 | 2638415.2579 | 1247626.0157 | 2638416.956 | 1247624.4676
34 | 2638468.8696 | 1247660.4155 | 2638457.9994 | 1247644.9973 | 2638455.3098 | 1247641.5064
35 | 2638462.7849 | 1247581.3235 | 2638452.9826 | 1247590.5733 | 2638446.5572 | 1247596.7513
36 | 2638415.2579 | 1247626.0157 | 2638412.2023 | 1247628.8012 | 2638399.6078 | 1247639.8227
37 | 2638468.8696 | 1247660.4155 | 2638470.1337 | 1247662.2084
38 | 2638469.6048 | 1247574.888 | 2638462.7849 | 1247581.3235
39 | 2638384.897 | 1247652.7959 | 2638388.2016 | 1247649.8042 | 2638399.6078 | 1247639.8227
40 | 2638649.4477 | 1247628.5632 | 2638654.5908 | 1247607.6658
41 | 2638644.604 | 1247642.8967 | 2638649.4477 | 1247628.5632
42 | 2638649.4477 | 1247628.5632 | 2638681.1965 | 1247645.3057
43 | 2638644.604 | 1247642.8967 | 2638640.6025 | 1247651.9989
44 | 2638644.604 | 1247642.8967 | 2638613.9238 | 1247645.7323 | 2638604.4899 | 1247612.4876
45 | 2638697.1983 | 1247653.7442 | 2638681.1965 | 1247645.3057
46 | 2638623.9203 | 1247679.7531 | 2638628.7037 | 1247673.5023 | 2638634.9012 | 1247663.5027 | 2638640.6025 | 1247651.9989
47 | 2638604.4899 | 1247612.4876 | 2638597.8774 | 1247589.1854
48 | 2638697.1983 | 1247653.7442 | 2638720.6442 | 1247666.1082
49 | 2638688.7538 | 1247461.446 | 2638684.7067 | 1247477.6726
50 | 2638623.9203 | 1247679.7531 | 2638639.7531 | 1247688.4841 | 2638646.1376 | 1247691.768
51 | 2638623.9203 | 1247679.7531 | 2638620.2033 | 1247684.5988 | 2638617.8007 | 1247687.5459
52 | 2638757.8104 | 1247685.7075 | 2638720.6442 | 1247666.1082
53 | 2638638.4167 | 1247807.8432 | 2638648.2235 | 1247785.1476 | 2638651.0786 | 1247778.9048
54 | 2638656.4822 | 1247767.0894 | 2638651.0786 | 1247778.9048
55 | 2638638.4167 | 1247807.8432 | 2638628.3475 | 1247802.7537
56 | 2638656.4822 | 1247767.0894 | 2638661.7883 | 1247754.4124
57 | 2638656.4822 | 1247767.0894 | 2638680.2726 | 1247780.3557
58 | 2638615.9234 | 1247779.4002 | 2638609.0457 | 1247792.9978 | 2638628.3475 | 1247802.7537
59 | 2638669.1709 | 1247736.7743 | 2638661.7883 | 1247754.4124
60 | 2638701.5321 | 1247792.2107 | 2638680.2726 | 1247780.3557
61 | 2638669.1709 | 1247736.7743 | 2638673.5294 | 1247726.351
62 | 2638669.1709 | 1247736.7743 | 2638692.1972 | 1247749.8638
63 | 2638701.5321 | 1247792.2107 | 2638725.7649 | 1247805.7248
64 | 2638673.5294 | 1247726.351 | 2638673.6127 | 1247726.1518 | 2638675.608 | 1247721.4621
65 | 2638717.6864 | 1247764.3532 | 2638692.1972 | 1247749.8638
66 | 2638344.2746 | 1247707.7323 | 2638344.7581 | 1247708.2711
67 | 2638333.8261 | 1247695.394 | 2638342.4819 | 1247705.7345 | 2638344.2746 | 1247707.7323
68 | 2638359.7273 | 1247724.9606 | 2638358.9401 | 1247724.0752 | 2638344.7581 | 1247708.2711
69 | 2638333.8261 | 1247695.394 | 2638332.8593 | 1247694.2426
70 | 2638333.8261 | 1247695.394 | 2638337.4476 | 1247692.4266 | 2638340.5672 | 1247690.0007 | 2638345.0984 | 1247686.5054 | 2638353.7683 | 1247679.4286
71 | 2638382.7446 | 1247750.8467 | 2638359.7273 | 1247724.9606
72 | 2638332.8593 | 1247694.2426 | 2638328.8396 | 1247698.0525 | 2638321.7389 | 1247705.3448 | 2638298.8738 | 1247728.4389
73 | 2638332.8593 | 1247694.2426 | 2638321.6579 | 1247680.3328
74 | 2638361.7239 | 1247672.9348 | 2638353.7683 | 1247679.4286
75 | 2638382.7446 | 1247750.8467 | 2638394.4951 | 1247740.4594
76 | 2638382.7446 | 1247750.8467 | 2638392.4985 | 1247762.1031
77 | 2638368.8915 | 1247666.949 | 2638365.8022 | 1247669.6058 | 2638361.7239 | 1247672.9348
78 | 2638408.8655 | 1247727.756 | 2638394.4951 | 1247740.4594
79 | 2638373.4498 | 1247663.0287 | 2638368.8915 | 1247666.949
80 | 2638395.0313 | 1247685.572 | 2638395.0313 | 1247685.572 | 2638390.3278 | 1247681.8502 | 2638383.7705 | 1247674.5379
81 | 2638373.4498 | 1247663.0287 | 2638383.7705 | 1247674.5379
82 | 2638407.7267 | 1247688.7756 | 2638402.9385 | 1247687.8802 | 2638398.5481 | 1247687.118 | 2638395.0313 | 1247685.572
83 | 2638384.897 | 1247652.7959 | 2638378.5018 | 1247658.4027 | 2638373.4498 | 1247663.0287
84 | 2638407.7267 | 1247688.7756 | 2638411.8694 | 1247689.5502 | 2638419.5985 | 1247690.2007 | 2638424.2716 | 1247690.5574
85 | 2638384.897 | 1247652.7959 | 2638373.6988 | 1247639.7038 | 2638373.501 | 1247639.4745
86 | 2638424.2716 | 1247690.5574 | 2638432.9824 | 1247691.2224
87 | 2638359.6868 | 1247623.4596 | 2638373.501 | 1247639.4745
88 | 2638432.9824 | 1247691.2224 | 2638434.7178 | 1247691.3549 | 2638440.2419 | 1247691.79
89 | 2638345.8317 | 1247607.4703 | 2638349.202 | 1247611.3045 | 2638359.6868 | 1247623.4596
90 | 2638508.756 | 1247505.5906 | 2638509.6407 | 1247511.8935
91 | 2638514.7134 | 1247540.7184 | 2638512.8195 | 1247532.3006 | 2638511.5207 | 1247525.2875 | 2638509.6407 | 1247511.8935
92 | 2638514.7134 | 1247540.7184 | 2638504.3852 | 1247542.5304 | 2638498.0464 | 1247547.5593 | 2638493.9739 | 1247551.3353
93 | 2638514.7134 | 1247540.7184 | 2638517.1256 | 1247547.7627
94 | 2638501.8264 | 1247428.5639 | 2638504.7109 | 1247461.4354
95 | 2638500.8753 | 1247417.7253 | 2638501.8264 | 1247428.5639
96 | 2638493.9739 | 1247551.3353 | 2638484.9645 | 1247559.686
97 | 2638493.9739 | 1247551.3353 | 2638485.0555 | 1247537.8097
98 | 2638534.683 | 1247590.492 | 2638524.9592 | 1247569.0258 | 2638519.8571 | 1247555.7395 | 2638517.1256 | 1247547.7627
99 | 2638500.8753 | 1247417.7253 | 2638492.8952 | 1247419.6192 | 2638482.9217 | 1247429.0435
100 | 2638483.2528 | 1247561.3734 | 2638484.5752 | 1247560.0468 | 2638484.9645 | 1247559.686
101 | 2638479.503 | 1247529.2582 | 2638482.5838 | 1247534.0612 | 2638485.0555 | 1247537.8097
102 | 2638534.683 | 1247590.492 | 2638542.6727 | 1247609.2988
103 | 2638466.5596 | 1247444.5045 | 2638482.9217 | 1247429.0435
104 | 2638757.3085 | 1247717.0078 | 2638744.8844 | 1247710.6619 | 2638744.8844 | 1247710.6619
105 | 2638757.6953 | 1247717.2054 | 2638757.3085 | 1247717.0078
106 | 2638750.6757 | 1247699.4815 | 2638744.8844 | 1247710.6619
107 | 2638757.8104 | 1247685.7075 | 2638750.6757 | 1247699.4815
108 | 2638468.5491 | 1247694.0178 | 2638467.9376 | 1247693.9718 | 2638440.2419 | 1247691.79
109 | 2638495.0335 | 1247691.8016 | 2638489.99 | 1247692.7584 | 2638485.9521 | 1247694.7113 | 2638480.8831 | 1247694.9452 | 2638468.5491 | 1247694.0178
110 | 2638495.0335 | 1247691.8016 | 2638494.0324 | 1247690.6528
111 | 2638345.8317 | 1247607.4703 | 2638330.6097 | 1247590.1525
112 | 2638448.4008 | 1247461.6634 | 2638462.0269 | 1247448.7877
113 | 2638448.4008 | 1247461.6634 | 2638446.1387 | 1247463.8009 | 2638442.3039 | 1247468.1901 | 2638440.8716 | 1247470.1043 | 2638440.8716 | 1247470.1043
114 | 2638466.5596 | 1247444.5045 | 2638462.0269 | 1247448.7877
115 | 2638446.4464 | 1247478.5431 | 2638440.8716 | 1247470.1043
116 | 2638449.7534 | 1247483.5492 | 2638446.4464 | 1247478.5431
117 | 2638455.626 | 1247492.4389 | 2638449.7534 | 1247483.5492
118 | 2638455.626 | 1247492.4389 | 2638463.9089 | 1247504.9772
119 | 2638479.503 | 1247529.2582 | 2638476.8772 | 1247525.1647
120 | 2638470.4524 | 1247515.1486 | 2638476.8772 | 1247525.1647
121 | 2638470.4524 | 1247515.1486 | 2638467.2581 | 1247510.1688
122 | 2638464.565 | 1247505.9703 | 2638467.2581 | 1247510.1688
123 | 2638483.2528 | 1247561.3734 | 2638472.5721 | 1247572.0881 | 2638471.6125 | 1247572.9935
124 | 2638464.565 | 1247505.9703 | 2638464.565 | 1247505.9703 | 2638463.9089 | 1247504.9772
125 | 2638717.6864 | 1247764.3532 | 2638742.3465 | 1247778.3766
126 | 2638557.5832 | 1247644.401 | 2638556.0684 | 1247640.8307 | 2638542.6727 | 1247609.2988
127 | 2638572.6275 | 1247693.3544 | 2638572.0038 | 1247688.399 | 2638570.3077 | 1247678.626 | 2638567.6043 | 1247669.3023 | 2638563.2016 | 1247657.6437 | 2638557.5832 | 1247644.401
128 | 2638572.0741 | 1247715.9176 | 2638573.0473 | 1247704.4497 | 2638572.8512 | 1247695.1312 | 2638572.6275 | 1247693.3544
129 | 2638572.0741 | 1247715.9176 | 2638569.6607 | 1247727.0204 | 2638566.4404 | 1247737.9623 | 2638563.0445 | 1247748.7762
130 | 2638572.0741 | 1247715.9176 | 2638582.7565 | 1247716.4874 | 2638589.727 | 1247715.332 | 2638600.061 | 1247709.1062 | 2638603.2375 | 1247705.2733
131 | 2638562.3532 | 1247750.9776 | 2638563.0445 | 1247748.7762
132 | 2638617.8007 | 1247687.5459 | 2638610.0325 | 1247697.0742 | 2638603.2375 | 1247705.2733
133 | 2638562.3532 | 1247750.9776 | 2638553.3202 | 1247746.4493 | 2638544.8632 | 1247738.1222 | 2638544.0546 | 1247737.3814
134 | 2638652.4897 | 1247695.0352 | 2638646.1376 | 1247691.768
135 | 2638652.4897 | 1247695.0352 | 2638659.195 | 1247698.484 | 2638665.9719 | 1247702.1921
136 | 2638675.608 | 1247721.4621 | 2638680.4387 | 1247710.1079 | 2638665.9719 | 1247702.1921
137 | 2638469.6048 | 1247574.888 | 2638471.6125 | 1247572.9935
138 | 2638544.0546 | 1247737.3814 | 2638542.1387 | 1247735.6264

## bus_geodata
| x | y | coords
0 | 2638897.9898 | 1247536.033
1 | 2638861.5763 | 1247607.312
2 | 2638845.561 | 1247638.6486
3 | 2638815.2194 | 1247581.949
4 | 2638813.4304 | 1247698.6017
5 | 2638764.992 | 1247555.5969
6 | 2638807.227 | 1247711.7699
7 | 2638880.1768 | 1247732.9946
8 | 2638740.8671 | 1247542.9718
9 | 2638899.6193 | 1247744.2825
10 | 2638790.0594 | 1247702.7156
11 | 2638791.5486 | 1247744.5418
12 | 2638784.126 | 1247699.5864
13 | 2638711.5506 | 1247527.7042
14 | 2638677.2411 | 1247511.3558
15 | 2638682.9253 | 1247484.4494
16 | 2638375.555 | 1247552.1736
17 | 2638371.4681 | 1247548.0521
18 | 2638386.6009 | 1247563.2776
19 | 2638364.7736 | 1247541.2167
20 | 2638395.2208 | 1247571.9939
21 | 2638348.5088 | 1247524.6095
22 | 2638395.7151 | 1247572.4963
23 | 2638357.3521 | 1247514.9016
24 | 2638404.3977 | 1247581.3206
25 | 2638413.1943 | 1247590.386
26 | 2638431.8938 | 1247610.8501
27 | 2638454.0406 | 1247639.859
28 | 2638444.9095 | 1247598.3356
29 | 2638416.956 | 1247624.4676
30 | 2638455.3098 | 1247641.5064
31 | 2638446.5572 | 1247596.7513
32 | 2638415.2579 | 1247626.0157
33 | 2638468.8696 | 1247660.4155
34 | 2638462.7849 | 1247581.3235
35 | 2638399.6078 | 1247639.8227
36 | 2638654.5908 | 1247607.6658
37 | 2638649.4477 | 1247628.5632
38 | 2638644.604 | 1247642.8967
39 | 2638681.1965 | 1247645.3057
40 | 2638640.6025 | 1247651.9989
41 | 2638604.4899 | 1247612.4876
42 | 2638697.1983 | 1247653.7442
43 | 2638684.7067 | 1247477.6726
44 | 2638688.7538 | 1247461.446
45 | 2638623.9203 | 1247679.7531
46 | 2638597.8774 | 1247589.1854
47 | 2638720.6442 | 1247666.1082
48 | 2638651.0786 | 1247778.9048
49 | 2638638.4167 | 1247807.8432
50 | 2638656.4822 | 1247767.0894
51 | 2638628.3475 | 1247802.7537
52 | 2638661.7883 | 1247754.4124
53 | 2638680.2726 | 1247780.3557
54 | 2638615.9234 | 1247779.4002
55 | 2638669.1709 | 1247736.7743
56 | 2638701.5321 | 1247792.2107
57 | 2638673.5294 | 1247726.351
58 | 2638692.1972 | 1247749.8638
59 | 2638725.7649 | 1247805.7248
60 | 2638344.2746 | 1247707.7323
61 | 2638344.7581 | 1247708.2711
62 | 2638333.8261 | 1247695.394
63 | 2638359.7273 | 1247724.9606
64 | 2638332.8593 | 1247694.2426
65 | 2638353.7683 | 1247679.4286
66 | 2638382.7446 | 1247750.8467
67 | 2638298.8738 | 1247728.4389
68 | 2638321.6579 | 1247680.3328
69 | 2638361.7239 | 1247672.9348
70 | 2638394.4951 | 1247740.4594
71 | 2638392.4985 | 1247762.1031
72 | 2638368.8915 | 1247666.949
73 | 2638383.7705 | 1247674.5379
74 | 2638395.0313 | 1247685.572
75 | 2638373.4498 | 1247663.0287
76 | 2638407.7267 | 1247688.7756
77 | 2638384.897 | 1247652.7959
78 | 2638424.2716 | 1247690.5574
79 | 2638373.501 | 1247639.4745
80 | 2638432.9824 | 1247691.2224
81 | 2638359.6868 | 1247623.4596
82 | 2638508.756 | 1247505.5906
83 | 2638509.6407 | 1247511.8935
84 | 2638514.7134 | 1247540.7184
85 | 2638504.7109 | 1247461.4354
86 | 2638501.8264 | 1247428.5639
87 | 2638493.9739 | 1247551.3353
88 | 2638517.1256 | 1247547.7627
89 | 2638500.8753 | 1247417.7253
90 | 2638484.9645 | 1247559.686
91 | 2638485.0555 | 1247537.8097
92 | 2638534.683 | 1247590.492
93 | 2638482.9217 | 1247429.0435
94 | 2638757.3085 | 1247717.0078
95 | 2638744.8844 | 1247710.6619
96 | 2638757.6953 | 1247717.2054
97 | 2638750.6757 | 1247699.4815
98 | 2638757.8104 | 1247685.7075
99 | 2638440.2419 | 1247691.79
100 | 2638468.5491 | 1247694.0178
101 | 2638495.0335 | 1247691.8016
102 | 2638387.4302 | 1247506.3436
103 | 2638345.8317 | 1247607.4703
104 | 2638330.6097 | 1247590.1525
105 | 2638448.4008 | 1247461.6634
106 | 2638462.0269 | 1247448.7877
107 | 2638440.8716 | 1247470.1043
108 | 2638466.5596 | 1247444.5045
109 | 2638446.4464 | 1247478.5431
110 | 2638449.7534 | 1247483.5492
111 | 2638455.626 | 1247492.4389
112 | 2638479.503 | 1247529.2582
113 | 2638476.8772 | 1247525.1647
114 | 2638470.4524 | 1247515.1486
115 | 2638467.2581 | 1247510.1688
116 | 2638483.2528 | 1247561.3734
117 | 2638464.565 | 1247505.9703
118 | 2638742.3465 | 1247778.3766
119 | 2638717.6864 | 1247764.3532
120 | 2638408.8655 | 1247727.756
121 | 2638557.5832 | 1247644.401
122 | 2638542.6727 | 1247609.2988
123 | 2638572.6275 | 1247693.3544
124 | 2638572.0741 | 1247715.9176
125 | 2638563.0445 | 1247748.7762
126 | 2638603.2375 | 1247705.2733
127 | 2638562.3532 | 1247750.9776
128 | 2638617.8007 | 1247687.5459
129 | 2638646.1376 | 1247691.768
130 | 2638652.4897 | 1247695.0352
131 | 2638665.9719 | 1247702.1921
132 | 2638463.9089 | 1247504.9772
133 | 2638470.1337 | 1247662.2084
134 | 2638471.6125 | 1247572.9935
135 | 2638469.6048 | 1247574.888
136 | 2638494.0324 | 1247690.6528
137 | 2638675.608 | 1247721.4621
138 | 2638542.1387 | 1247735.6264
139 | 2638544.0546 | 1247737.3814
140 | 2638534.683 | 1247590.492

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97288 | -0.52357 | 0.009492 | 0.0023789
1 | 0.97359 | -0.50959 | 0 | 0
2 | 0.97435 | -0.4945 | 0.029053 | 0.0072813
3 | 0.9729 | -0.52306 | 0.0038404 | 0.0009625
4 | 0.97767 | -0.42928 | 0 | 0
5 | 0.97237 | -0.53351 | 0.00041185 | 0.00010322
6 | 0.97842 | -0.41454 | 0 | 0
7 | 0.97745 | -0.43367 | 0 | 0
8 | 0.97213 | -0.53833 | 0.00093325 | 0.00023389
9 | 0.97738 | -0.43498 | 0.0032028 | 0.0008027
10 | 0.97947 | -0.39416 | 0.0016829 | 0.00042178
11 | 0.97835 | -0.41594 | 0.0021162 | 0.00053036
12 | 0.97984 | -0.38692 | 0.0028012 | 0.00070205
13 | 0.97186 | -0.54361 | 0.0020655 | 0.00051766
14 | 0.97163 | -0.54824 | 0 | 0
15 | 0.97146 | -0.55159 | 0.0015274 | 0.00038279
16 | 0.97789 | -0.42446 | 0.0034431 | 0.00086292
17 | 0.97785 | -0.42516 | 0.0021839 | 0.00054734
18 | 0.97803 | -0.4216 | 0.0020822 | 0.00052185
19 | 0.97781 | -0.42592 | 0.0012591 | 0.00031556
20 | 0.97817 | -0.4189 | 0.0020045 | 0.00050237
21 | 0.97775 | -0.42724 | 0 | 0
22 | 0.97818 | -0.41872 | 0.0019838 | 0.00049719
23 | 0.97771 | -0.42799 | 0.0020316 | 0.00050917
24 | 0.97837 | -0.4151 | 0.0023016 | 0.00057684
25 | 0.97858 | -0.41087 | 0.0033444 | 0.00083819
26 | 0.97914 | -0.39991 | 0 | 0
27 | 0.97872 | -0.40818 | 0.0055972 | 0.0014028
28 | 0.98104 | -0.36289 | 0.0055787 | 0.0013982
29 | 0.97765 | -0.42892 | 0.0021599 | 0.00054133
30 | 0.9787 | -0.40844 | 0.0021824 | 0.00054697
31 | 0.98129 | -0.35799 | 0.0035925 | 0.00090036
32 | 0.97749 | -0.43213 | 0.0035808 | 0.00089744
33 | 0.9786 | -0.41042 | 0.0029519 | 0.00073982
34 | 0.98383 | -0.3086 | 0.0033746 | 0.00084577
35 | 0.97607 | -0.45999 | 0.0031556 | 0.00079087
36 | 0.9856 | -0.27514 | 0.0042628 | 0.0010684
37 | 0.98569 | -0.27349 | 0 | 0
38 | 0.98624 | -0.26285 | 0 | 0
39 | 0.98445 | -0.29742 | 0.0010072 | 0.00025242
40 | 0.98679 | -0.25216 | 0.00077764 | 0.0001949
41 | 0.98374 | -0.31156 | 0.025812 | 0.0064692
42 | 0.98383 | -0.30934 | 0.00078874 | 0.00019768
43 | 0.97143 | -0.55225 | 0.0032431 | 0.00081279
44 | 0.9714 | -0.55281 | 0.0018192 | 0.00045594
45 | 0.98861 | -0.21713 | 0 | 0
46 | 0.98339 | -0.3184 | 0.015671 | 0.0039275
47 | 0.98294 | -0.32664 | 0.0019746 | 0.00049489
48 | 0.98477 | -0.29184 | 0.0016321 | 0.00040904
49 | 0.98459 | -0.2952 | 0 | 0
50 | 0.98486 | -0.29007 | 0 | 0
51 | 0.98453 | -0.2964 | 0.0010168 | 0.00025483
52 | 0.98509 | -0.28554 | 0.0021569 | 0.00054058
53 | 0.98459 | -0.29536 | 0.0039733 | 0.0009958
54 | 0.98437 | -0.29965 | 0.0049049 | 0.0012293
55 | 0.98545 | -0.2785 | 0 | 0
56 | 0.98443 | -0.29835 | 0 | 0
57 | 0.98581 | -0.27153 | 0.00070333 | 0.00017627
58 | 0.98511 | -0.2851 | 0.00694 | 0.0017393
59 | 0.98426 | -0.30175 | 0.0068222 | 0.0017098
60 | 0.97195 | -0.54105 | 0.0013646 | 0.00034201
61 | 0.97194 | -0.54136 | 0.0024572 | 0.00061583
62 | 0.97232 | -0.53377 | 0 | 0
63 | 0.9715 | -0.54988 | 0.0029675 | 0.00074373
64 | 0.97231 | -0.53397 | 0 | 0
65 | 0.97307 | -0.51889 | 0.00089113 | 0.00022334
66 | 0.97093 | -0.56115 | 0 | 0
67 | 0.97208 | -0.53854 | 0.0051362 | 0.0012873
68 | 0.97228 | -0.53465 | 0.0020699 | 0.00051878
69 | 0.97339 | -0.51275 | 0.0017548 | 0.0004398
70 | 0.97075 | -0.56481 | 0.0028376 | 0.00071118
71 | 0.97087 | -0.56253 | 0.0050084 | 0.0012552
72 | 0.97368 | -0.50687 | 0.0032275 | 0.00080888
73 | 0.97353 | -0.50985 | 0.0014943 | 0.00037452
74 | 0.97319 | -0.51671 | 0.0025808 | 0.00064681
75 | 0.97389 | -0.50272 | 0 | 0
76 | 0.97293 | -0.5218 | 0.0025687 | 0.00064378
77 | 0.97479 | -0.48512 | 0 | 0
78 | 0.97264 | -0.52745 | 0.0033471 | 0.00083886
79 | 0.97467 | -0.48748 | 0.0019009 | 0.00047641
80 | 0.97252 | -0.52988 | 0.0074788 | 0.0018744
81 | 0.97456 | -0.4896 | 0.0017152 | 0.00042987
82 | 0.99022 | -0.18569 | 0.00069562 | 0.00017434
83 | 0.99022 | -0.18561 | 0.00045972 | 0.00011522
84 | 0.99025 | -0.18501 | 0 | 0
85 | 0.98586 | -0.27002 | 0.0026145 | 0.00065525
86 | 0.98594 | -0.26848 | 0.00078317 | 0.00019628
87 | 0.9883 | -0.22245 | 0 | 0
88 | 0.99086 | -0.17339 | 0.01127 | 0.0028246
89 | 0.98597 | -0.26781 | 0 | 0
90 | 0.98749 | -0.23811 | 0.0019091 | 0.00047847
91 | 0.98783 | -0.23167 | 0.0012994 | 0.00032567
92 | 0.99487 | -0.096939 | 0 | 0
93 | 0.98604 | -0.26648 | 0.0014013 | 0.0003512
94 | 0.98131 | -0.35826 | 0.0020282 | 0.00050831
95 | 0.98137 | -0.35721 | 0.0024563 | 0.00061562
96 | 0.98131 | -0.35827 | 0.0021276 | 0.00053323
97 | 0.98144 | -0.3557 | 0.0016351 | 0.00040979
98 | 0.98156 | -0.35338 | 0 | 0
99 | 0.97247 | -0.5309 | 0.0024176 | 0.0006059
100 | 0.97233 | -0.53361 | 0.0023388 | 0.00058617
101 | 0.97226 | -0.53503 | 0 | 0
102 | 0.97767 | -0.42876 | 0.0010874 | 0.00027252
103 | 0.97449 | -0.49105 | 0.0018683 | 0.00046825
104 | 0.97445 | -0.49184 | 0.0018679 | 0.00046814
105 | 0.98632 | -0.26098 | 0.0011468 | 0.00028741
106 | 0.98618 | -0.26373 | 0.0009223 | 0.00023115
107 | 0.98642 | -0.25909 | 0.0013311 | 0.00033359
108 | 0.98614 | -0.26454 | 0.0024581 | 0.00061607
109 | 0.98652 | -0.25715 | 0.00068912 | 0.00017271
110 | 0.98658 | -0.25593 | 0.0010656 | 0.00026706
111 | 0.9867 | -0.25357 | 0.0019111 | 0.00047897
112 | 0.98754 | -0.23723 | 0.002727 | 0.00068345
113 | 0.98742 | -0.23965 | 0.0019077 | 0.00047811
114 | 0.98714 | -0.24517 | 0.0035996 | 0.00090215
115 | 0.98701 | -0.24753 | 0.002144 | 0.00053734
116 | 0.98733 | -0.24114 | 0.0058894 | 0.001476
117 | 0.98692 | -0.24934 | 0.0025024 | 0.00062717
118 | 0.98474 | -0.29229 | 0.0069369 | 0.0017385
119 | 0.98493 | -0.28875 | 0 | 0
120 | 0.97058 | -0.56827 | 0.0097669 | 0.0024478
121 | 1 | 0 | -0.38059 | -0.097558
122 | 0.99664 | -0.063345 | 0.0028937 | 0.00072522
123 | 0.99566 | -0.082144 | 0.0053417 | 0.0013388
124 | 0.99381 | -0.11741 | 0 | 0
125 | 0.99352 | -0.12295 | 0.0041204 | 0.0010327
126 | 0.99111 | -0.16908 | 0.0013883 | 0.00034793
127 | 0.99351 | -0.12316 | 0 | 0
128 | 0.98934 | -0.20301 | 0.0064594 | 0.0016189
129 | 0.9877 | -0.23479 | 0.0012896 | 0.00032321
130 | 0.98745 | -0.23963 | 0.00099813 | 0.00025016
131 | 0.98693 | -0.2497 | 0.0010798 | 0.00027061
132 | 0.9869 | -0.24971 | 0.0033518 | 0.00084004
133 | 0.9786 | -0.41049 | 0.0017199 | 0.00043106
134 | 0.98527 | -0.28091 | 0.0035556 | 0.00089111
135 | 0.98493 | -0.28743 | 0.0058618 | 0.0014691
136 | 0.97225 | -0.53511 | 0.0028419 | 0.00071225
137 | 0.98598 | -0.26818 | 0.00070525 | 0.00017675
138 | 0.9934 | -0.12531 | 0.0017089 | 0.0004283
139 | 0.99341 | -0.12523 | 0.0033764 | 0.00084621
140 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.009492 | -0.0023789 | 0.0094984 | 0.002382 | 6.3264e-06 | 3.0542e-06 | 0.014518 | 0.014518 | 0.014518 | 0.97288 | -0.52357 | 0.97359 | -0.50959 | 3.9885
1 | -0.02336 | -0.005861 | 0.023377 | 0.0058713 | 1.6824e-05 | 1.033e-05 | 0.035705 | 0.035705 | 0.035705 | 0.97359 | -0.50959 | 0.97435 | -0.4945 | 9.8092
2 | 0.013862 | 0.003479 | -0.013853 | -0.003474 | 8.8957e-06 | 5.0366e-06 | 0.021188 | 0.021188 | 0.021188 | 0.97359 | -0.50959 | 0.9729 | -0.52306 | 5.8209
3 | -0.052429 | -0.013153 | 0.052593 | 0.013256 | 0.00016356 | 0.00010383 | 0.080074 | 0.080074 | 0.080074 | 0.97435 | -0.4945 | 0.97767 | -0.42928 | 21.9984
4 | 0.010012 | 0.0025115 | -0.010007 | -0.002509 | 4.9885e-06 | 2.4887e-06 | 0.015314 | 0.015314 | 0.015314 | 0.9729 | -0.52306 | 0.97237 | -0.53351 | 4.2073
5 | -0.055797 | -0.014058 | 0.055836 | 0.014083 | 3.9374e-05 | 2.5017e-05 | 0.084949 | 0.084949 | 0.084949 | 0.97767 | -0.42928 | 0.97842 | -0.41454 | 23.3377
6 | 0.0032037 | 0.00080203 | -0.003203 | -0.00080254 | 6.6941e-07 | -5.1294e-07 | 0.0048757 | 0.004876 | 0.004876 | 0.97767 | -0.42928 | 0.97745 | -0.43367 | 1.3396
7 | 0.0095955 | 0.0024058 | -0.0095933 | -0.0024047 | 2.2017e-06 | 1.0714e-06 | 0.014684 | 0.014684 | 0.014684 | 0.97237 | -0.53351 | 0.97213 | -0.53833 | 4.0341
8 | -0.057952 | -0.014613 | 0.058009 | 0.014649 | 5.6578e-05 | 3.5966e-05 | 0.088168 | 0.088168 | 0.088168 | 0.97842 | -0.41454 | 0.97947 | -0.39416 | 24.2219
9 | 0.0021163 | 0.00052999 | -0.0021162 | -0.00053036 | 1.4112e-07 | -3.6592e-07 | 0.0032184 | 0.0032185 | 0.0032185 | 0.97842 | -0.41454 | 0.97835 | -0.41594 | 0.88421
10 | 0.003203 | 0.00080254 | -0.0032028 | -0.0008027 | 2.0051e-07 | -1.5353e-07 | 0.004876 | 0.0048761 | 0.0048761 | 0.97745 | -0.43367 | 0.97738 | -0.43498 | 1.3396
11 | 0.00866 | 0.0021708 | -0.0086578 | -0.0021698 | 2.1781e-06 | 9.8427e-07 | 0.013256 | 0.013256 | 0.013256 | 0.97213 | -0.53833 | 0.97186 | -0.54361 | 3.6417
12 | -0.059692 | -0.015071 | 0.059713 | 0.015084 | 2.0705e-05 | 1.3167e-05 | 0.090724 | 0.090724 | 0.090724 | 0.97947 | -0.39416 | 0.97984 | -0.38692 | 24.9243
13 | -0.062514 | -0.015786 | 0.062614 | 0.01585 | 0.00010064 | 6.4036e-05 | 0.094978 | 0.094978 | 0.094978 | 0.97984 | -0.38692 | 0.98156 | -0.35338 | 26.0929
14 | 0.0065923 | 0.0016521 | -0.0065909 | -0.0016517 | 1.4562e-06 | 4.5979e-07 | 0.010093 | 0.010094 | 0.010094 | 0.97186 | -0.54361 | 0.97163 | -0.54824 | 2.773
15 | 0.0065909 | 0.0016517 | -0.0065898 | -0.0016514 | 1.0515e-06 | 3.3215e-07 | 0.010094 | 0.010094 | 0.010094 | 0.97163 | -0.54824 | 0.97146 | -0.55159 | 2.773
16 | 0.0050625 | 0.0012686 | -0.0050623 | -0.0012685 | 1.58e-07 | 1.4367e-08 | 0.0077543 | 0.0077543 | 0.0077543 | 0.97146 | -0.55159 | 0.97143 | -0.55225 | 2.1303
17 | 0.0065627 | 0.0016439 | -0.0065625 | -0.0016438 | 2.1705e-07 | 6.6095e-08 | 0.0099859 | 0.0099859 | 0.0099859 | 0.97789 | -0.42446 | 0.97785 | -0.42516 | 2.7434
18 | -0.010006 | -0.0025068 | 0.010007 | 0.0025075 | 1.3615e-06 | 6.7483e-07 | 0.015225 | 0.015225 | 0.015225 | 0.97789 | -0.42446 | 0.97803 | -0.4216 | 4.1827
19 | 0.0043786 | 0.0010965 | -0.0043784 | -0.0010965 | 1.5927e-07 | -1.8085e-08 | 0.0066626 | 0.0066627 | 0.0066627 | 0.97785 | -0.42516 | 0.97781 | -0.42592 | 1.8304
20 | -0.012089 | -0.0030294 | 0.012091 | 0.0030302 | 1.5552e-06 | 8.4146e-07 | 0.018393 | 0.018393 | 0.018393 | 0.97803 | -0.4216 | 0.97817 | -0.4189 | 5.053
21 | 0.0031193 | 0.00078096 | -0.0031191 | -0.00078113 | 1.964e-07 | -1.6587e-07 | 0.0047466 | 0.0047467 | 0.0047467 | 0.97781 | -0.42592 | 0.97775 | -0.42724 | 1.304
22 | -0.014095 | -0.0035326 | 0.014096 | 0.0035326 | 1.215e-07 | 6.8913e-08 | 0.021442 | 0.021442 | 0.021442 | 0.97817 | -0.4189 | 0.97818 | -0.41872 | 5.8907
23 | 0.0031191 | 0.00078113 | -0.003119 | -0.00078122 | 1.1096e-07 | -9.3682e-08 | 0.0047467 | 0.0047468 | 0.0047468 | 0.97775 | -0.42724 | 0.97771 | -0.42799 | 1.3041
24 | -0.016079 | -0.0040298 | 0.016082 | 0.0040315 | 2.7775e-06 | 1.6222e-06 | 0.02446 | 0.02446 | 0.02446 | 0.97818 | -0.41872 | 0.97837 | -0.4151 | 6.7198
25 | 0.0010874 | 0.00027205 | -0.0010874 | -0.00027252 | 3.9975e-08 | -4.6255e-07 | 0.0016548 | 0.001655 | 0.001655 | 0.97771 | -0.42799 | 0.97767 | -0.42876 | 0.45466
26 | -0.018384 | -0.0046083 | 0.018387 | 0.0046105 | 3.7036e-06 | 2.2116e-06 | 0.027961 | 0.02796 | 0.027961 | 0.97837 | -0.4151 | 0.97858 | -0.41087 | 7.6815
27 | -0.021732 | -0.0054487 | 0.021743 | 0.0054556 | 1.1352e-05 | 6.9171e-06 | 0.033046 | 0.033046 | 0.033046 | 0.97858 | -0.41087 | 0.97914 | -0.39991 | 9.0786
28 | 0.012457 | 0.0031233 | -0.012452 | -0.0031206 | 4.9053e-06 | 2.6805e-06 | 0.018931 | 0.018932 | 0.018932 | 0.97914 | -0.39991 | 0.97872 | -0.40818 | 5.201
29 | -0.11347 | -0.028621 | 0.11367 | 0.02875 | 0.00020149 | 0.00012873 | 0.1725 | 0.1725 | 0.1725 | 0.97914 | -0.39991 | 0.98104 | -0.36289 | 47.3914
30 | 0.079267 | 0.020042 | -0.079157 | -0.019972 | 0.00011011 | 7.0218e-05 | 0.12053 | 0.12053 | 0.12053 | 0.97914 | -0.39991 | 0.97765 | -0.42892 | 33.1119
31 | 0.0068548 | 0.0017178 | -0.0068547 | -0.0017178 | 8.4702e-08 | 2.8076e-08 | 0.010422 | 0.010422 | 0.010422 | 0.97872 | -0.40818 | 0.9787 | -0.40844 | 2.8631
32 | -0.11925 | -0.030148 | 0.11928 | 0.030166 | 2.8072e-05 | 1.7937e-05 | 0.18097 | 0.18097 | 0.18097 | 0.98104 | -0.36289 | 0.98129 | -0.35799 | 49.716
33 | 0.076997 | 0.019431 | -0.076985 | -0.019423 | 1.1844e-05 | 7.5515e-06 | 0.11724 | 0.11724 | 0.11724 | 0.97765 | -0.42892 | 0.97749 | -0.43213 | 32.2088
34 | 0.0046723 | 0.0011708 | -0.0046719 | -0.0011709 | 4.4038e-07 | -1.0568e-08 | 0.0071037 | 0.0071038 | 0.0071038 | 0.9787 | -0.40844 | 0.9786 | -0.41042 | 1.9516
35 | -0.12287 | -0.031066 | 0.12316 | 0.031253 | 0.00029179 | 0.00018646 | 0.18641 | 0.18641 | 0.18641 | 0.98129 | -0.35799 | 0.98383 | -0.3086 | 51.2125
36 | 0.073405 | 0.018526 | -0.073307 | -0.018463 | 9.7806e-05 | 6.2335e-05 | 0.11179 | 0.11179 | 0.11179 | 0.97749 | -0.43213 | 0.97607 | -0.45999 | 30.7113
37 | 0.0017199 | 0.00043103 | -0.0017199 | -0.00043106 | 5.6266e-09 | -2.3961e-08 | 0.0026153 | 0.0026153 | 0.0026153 | 0.9786 | -0.41042 | 0.9786 | -0.41049 | 0.71848
38 | -0.12653 | -0.032098 | 0.12666 | 0.032181 | 0.00012898 | 8.2425e-05 | 0.19152 | 0.19152 | 0.19152 | 0.98383 | -0.3086 | 0.98493 | -0.28743 | 52.6147
39 | 0.070151 | 0.017672 | -0.070067 | -0.017619 | 8.4178e-05 | 5.3629e-05 | 0.10698 | 0.10698 | 0.10698 | 0.97607 | -0.45999 | 0.97479 | -0.48512 | 29.3897
40 | -0.0042628 | -0.0010684 | 0.0042632 | 0.0010683 | 3.3427e-07 | -6.0361e-08 | 0.0064358 | 0.0064357 | 0.0064358 | 0.9856 | -0.27514 | 0.98569 | -0.27349 | 1.7681
41 | -0.079177 | -0.020107 | 0.079218 | 0.020133 | 4.0586e-05 | 2.5589e-05 | 0.11962 | 0.11962 | 0.11962 | 0.98569 | -0.27349 | 0.98624 | -0.26285 | 16.4316
42 | 0.074914 | 0.019039 | -0.074828 | -0.018985 | 8.6218e-05 | 5.4266e-05 | 0.11319 | 0.11319 | 0.11319 | 0.98569 | -0.27349 | 0.98445 | -0.29742 | 15.5476
43 | -0.1208 | -0.030594 | 0.12086 | 0.030633 | 6.201e-05 | 3.9433e-05 | 0.18238 | 0.18238 | 0.18238 | 0.98624 | -0.26285 | 0.98679 | -0.25216 | 25.052
44 | 0.041585 | 0.010461 | -0.041489 | -0.0104 | 9.6542e-05 | 6.0955e-05 | 0.062757 | 0.062757 | 0.062757 | 0.98624 | -0.26285 | 0.98374 | -0.31156 | 17.2409
45 | 0.073821 | 0.018732 | -0.073778 | -0.018706 | 4.2294e-05 | 2.6609e-05 | 0.11166 | 0.11166 | 0.11166 | 0.98445 | -0.29742 | 0.98383 | -0.30934 | 15.3385
46 | -0.12164 | -0.030828 | 0.12185 | 0.030958 | 0.00020514 | 0.00013046 | 0.18355 | 0.18355 | 0.18355 | 0.98679 | -0.25216 | 0.98861 | -0.21713 | 25.213
47 | 0.015676 | 0.0039305 | -0.015671 | -0.0039275 | 5.1074e-06 | 2.9613e-06 | 0.023712 | 0.023713 | 0.023713 | 0.98374 | -0.31156 | 0.98339 | -0.3184 | 6.5145
48 | 0.07299 | 0.018508 | -0.072929 | -0.01847 | 6.0653e-05 | 3.8145e-05 | 0.11047 | 0.11047 | 0.11047 | 0.98383 | -0.30934 | 0.98294 | -0.32664 | 15.1747
49 | 0.0018193 | 0.00045576 | -0.0018192 | -0.00045594 | 4.8701e-08 | -1.7587e-07 | 0.0027866 | 0.0027867 | 0.0027867 | 0.97143 | -0.55225 | 0.9714 | -0.55281 | 0.76558
50 | 0.039293 | 0.0098947 | -0.039259 | -0.0098738 | 3.3151e-05 | 2.0893e-05 | 0.059158 | 0.059159 | 0.059159 | 0.98861 | -0.21713 | 0.9877 | -0.23479 | 16.2524
51 | -0.16114 | -0.040853 | 0.16125 | 0.040923 | 0.00010945 | 6.9795e-05 | 0.24271 | 0.24271 | 0.24271 | 0.98861 | -0.21713 | 0.98934 | -0.20301 | 33.3392
52 | 0.070954 | 0.017975 | -0.070863 | -0.017918 | 9.1014e-05 | 5.7185e-05 | 0.10748 | 0.10748 | 0.10748 | 0.98294 | -0.32664 | 0.98156 | -0.35338 | 14.7642
53 | 0.0059238 | 0.0014844 | -0.0059228 | -0.0014842 | 9.4908e-07 | 2.0559e-07 | 0.0089509 | 0.0089511 | 0.0089511 | 0.98477 | -0.29184 | 0.98459 | -0.2952 | 2.4591
54 | -0.0075558 | -0.0018935 | 0.0075565 | 0.0018937 | 6.3508e-07 | 2.4114e-07 | 0.011417 | 0.011417 | 0.011417 | 0.98477 | -0.29184 | 0.98486 | -0.29007 | 3.1366
55 | 0.0059228 | 0.0014842 | -0.0059225 | -0.0014841 | 3.3899e-07 | 7.3469e-08 | 0.0089511 | 0.0089511 | 0.0089511 | 0.98459 | -0.2952 | 0.98453 | -0.2964 | 2.4591
56 | -0.018357 | -0.0046014 | 0.018361 | 0.0046037 | 3.9643e-06 | 2.3623e-06 | 0.027735 | 0.027735 | 0.027735 | 0.98486 | -0.29007 | 0.98509 | -0.28554 | 7.6196
57 | 0.0108 | 0.0027077 | -0.010798 | -0.0027063 | 2.7201e-06 | 1.3943e-06 | 0.016318 | 0.016319 | 0.016319 | 0.98486 | -0.29007 | 0.98459 | -0.29536 | 4.4831
58 | 0.0049057 | 0.0012293 | -0.0049049 | -0.0012293 | 7.5998e-07 | 1.7667e-08 | 0.0074143 | 0.0074145 | 0.0074145 | 0.98453 | -0.2964 | 0.98437 | -0.29965 | 2.037
59 | -0.020518 | -0.0051443 | 0.020525 | 0.0051485 | 6.8877e-06 | 4.1646e-06 | 0.030993 | 0.030993 | 0.030993 | 0.98509 | -0.28554 | 0.98545 | -0.2785 | 8.5147
60 | 0.0068243 | 0.0017105 | -0.0068233 | -0.0017102 | 9.7097e-07 | 3.119e-07 | 0.010314 | 0.010314 | 0.010314 | 0.98459 | -0.29536 | 0.98443 | -0.29835 | 2.8334
61 | -0.034408 | -0.0086296 | 0.03442 | 0.0086368 | 1.1437e-05 | 7.176e-06 | 0.051958 | 0.051958 | 0.051958 | 0.98545 | -0.2785 | 0.98581 | -0.27153 | 14.2742
62 | 0.013884 | 0.0034811 | -0.013879 | -0.0034787 | 4.3655e-06 | 2.4566e-06 | 0.020965 | 0.020965 | 0.020965 | 0.98545 | -0.2785 | 0.98511 | -0.2851 | 5.7595
63 | 0.0068233 | 0.0017102 | -0.0068222 | -0.0017098 | 1.1068e-06 | 3.5566e-07 | 0.010314 | 0.010314 | 0.010314 | 0.98443 | -0.29835 | 0.98426 | -0.30175 | 2.8335
64 | -0.035123 | -0.008813 | 0.035129 | 0.0088165 | 5.6001e-06 | 3.5163e-06 | 0.05302 | 0.05302 | 0.05302 | 0.98581 | -0.27153 | 0.98598 | -0.26818 | 14.5658
65 | 0.0069392 | 0.0017393 | -0.006938 | -0.0017389 | 1.208e-06 | 3.9991e-07 | 0.010482 | 0.010482 | 0.010482 | 0.98511 | -0.2851 | 0.98493 | -0.28875 | 2.8797
66 | 0.02306 | 0.0057867 | -0.02306 | -0.0057865 | 3.3842e-07 | 2.0761e-07 | 0.035307 | 0.035307 | 0.035307 | 0.97195 | -0.54105 | 0.97194 | -0.54136 | 9.6996
67 | -0.024425 | -0.0061287 | 0.024433 | 0.006134 | 8.4794e-06 | 5.2264e-06 | 0.037396 | 0.037396 | 0.037396 | 0.97195 | -0.54105 | 0.97232 | -0.53377 | 10.2736
68 | 0.020602 | 0.0051707 | -0.020594 | -0.0051656 | 8.3657e-06 | 5.0763e-06 | 0.031545 | 0.031545 | 0.031545 | 0.97194 | -0.54136 | 0.9715 | -0.54988 | 8.6661
69 | 0.0072074 | 0.001806 | -0.0072073 | -0.001806 | 6.8524e-08 | 2.5226e-08 | 0.01103 | 0.01103 | 0.01103 | 0.97232 | -0.53377 | 0.97231 | -0.53397 | 3.0302
70 | -0.03164 | -0.00794 | 0.031663 | 0.007954 | 2.2466e-05 | 1.4061e-05 | 0.048426 | 0.048425 | 0.048426 | 0.97232 | -0.53377 | 0.97307 | -0.51889 | 13.3037
71 | 0.017627 | 0.0044219 | -0.017617 | -0.0044163 | 9.4692e-06 | 5.6316e-06 | 0.026999 | 0.027 | 0.027 | 0.9715 | -0.54988 | 0.97093 | -0.56115 | 7.4175
72 | 0.0051373 | 0.0012874 | -0.0051362 | -0.0012873 | 1.1176e-06 | 1.1742e-07 | 0.007862 | 0.0078623 | 0.0078623 | 0.97231 | -0.53397 | 0.97208 | -0.53854 | 2.16
73 | 0.00207 | 0.0005186 | -0.0020699 | -0.00051878 | 6.721e-08 | -1.7848e-07 | 0.0031679 | 0.0031679 | 0.0031679 | 0.97231 | -0.53397 | 0.97228 | -0.53465 | 0.87031
74 | -0.032554 | -0.0081774 | 0.032564 | 0.0081833 | 9.5461e-06 | 5.9819e-06 | 0.049788 | 0.049788 | 0.049788 | 0.97307 | -0.51889 | 0.97339 | -0.51275 | 13.6781
75 | 0.012608 | 0.003161 | -0.012606 | -0.0031598 | 2.1961e-06 | 1.2115e-06 | 0.019323 | 0.019323 | 0.019323 | 0.97093 | -0.56115 | 0.97075 | -0.56481 | 5.3086
76 | 0.0050088 | 0.0012553 | -0.0050084 | -0.0012552 | 3.2912e-07 | 2.6439e-08 | 0.0076762 | 0.0076763 | 0.0076763 | 0.97093 | -0.56115 | 0.97087 | -0.56253 | 2.1089
77 | -0.034318 | -0.0086231 | 0.034328 | 0.0086292 | 9.642e-06 | 6.0548e-06 | 0.052471 | 0.052471 | 0.052471 | 0.97339 | -0.51275 | 0.97368 | -0.50687 | 14.415
78 | 0.0097685 | 0.0024486 | -0.0097669 | -0.0024478 | 1.6127e-06 | 7.9504e-07 | 0.014974 | 0.014974 | 0.014974 | 0.97075 | -0.56481 | 0.97058 | -0.56827 | 4.1137
79 | -0.037556 | -0.0094381 | 0.037563 | 0.0094428 | 7.4291e-06 | 4.6798e-06 | 0.057403 | 0.057403 | 0.057403 | 0.97368 | -0.50687 | 0.97389 | -0.50272 | 15.77
80 | 0.023594 | 0.0059199 | -0.023587 | -0.0059152 | 7.7165e-06 | 4.7419e-06 | 0.036066 | 0.036066 | 0.036066 | 0.97353 | -0.50985 | 0.97319 | -0.51671 | 9.9082
81 | -0.025089 | -0.0062944 | 0.025097 | 0.0062997 | 8.5259e-06 | 5.2643e-06 | 0.03835 | 0.03835 | 0.03835 | 0.97353 | -0.50985 | 0.97389 | -0.50272 | 10.5357
82 | 0.021006 | 0.0052684 | -0.021001 | -0.0052653 | 5.0948e-06 | 3.0971e-06 | 0.03212 | 0.03212 | 0.03212 | 0.97319 | -0.51671 | 0.97293 | -0.5218 | 8.8241
83 | -0.06266 | -0.015742 | 0.062713 | 0.015776 | 5.2708e-05 | 3.3542e-05 | 0.095753 | 0.095753 | 0.095753 | 0.97389 | -0.50272 | 0.97479 | -0.48512 | 26.3057
84 | 0.018432 | 0.0046215 | -0.018427 | -0.0046185 | 4.9644e-06 | 2.9704e-06 | 0.028191 | 0.028191 | 0.028191 | 0.97293 | -0.5218 | 0.97264 | -0.52745 | 7.7449
85 | 0.007354 | 0.0018427 | -0.0073532 | -0.0018424 | 8.2846e-07 | 3.117e-07 | 0.011226 | 0.011226 | 0.011226 | 0.97479 | -0.48512 | 0.97467 | -0.48748 | 3.084
86 | 0.01508 | 0.0037797 | -0.015078 | -0.0037787 | 1.7437e-06 | 1.0076e-06 | 0.023071 | 0.023071 | 0.023071 | 0.97264 | -0.52745 | 0.97252 | -0.52988 | 6.3381
87 | 0.0054523 | 0.001366 | -0.0054517 | -0.0013659 | 5.4952e-07 | 8.813e-08 | 0.0083238 | 0.0083239 | 0.0083239 | 0.97467 | -0.48748 | 0.97456 | -0.4896 | 2.2868
88 | 0.0075996 | 0.0019043 | -0.0075992 | -0.0019042 | 3.6919e-07 | 1.4593e-07 | 0.011628 | 0.011628 | 0.011628 | 0.97252 | -0.52988 | 0.97247 | -0.5309 | 3.1944
89 | 0.0037366 | 0.00093605 | -0.0037363 | -0.00093614 | 2.5823e-07 | -9.8336e-08 | 0.005705 | 0.0057051 | 0.0057051 | 0.97456 | -0.4896 | 0.97449 | -0.49105 | 1.5673
90 | -0.00069562 | -0.00017434 | 0.00069563 | 0.00017426 | 2.608e-09 | -8.0207e-08 | 0.0010453 | 0.0010453 | 0.0010453 | 0.99022 | -0.18569 | 0.99022 | -0.18561 | 0.28718
91 | -0.0011553 | -0.00028948 | 0.0011554 | 0.00028912 | 3.3099e-08 | -3.5556e-07 | 0.0017361 | 0.001736 | 0.0017361 | 0.99022 | -0.18561 | 0.99025 | -0.18501 | 0.47696
92 | 0.17653 | 0.044985 | -0.17621 | -0.044782 | 0.00031831 | 0.0002031 | 0.26553 | 0.26553 | 0.26553 | 0.99025 | -0.18501 | 0.9883 | -0.22245 | 36.474
93 | -0.17769 | -0.045274 | 0.17779 | 0.045337 | 9.9726e-05 | 6.3633e-05 | 0.26727 | 0.26727 | 0.26727 | 0.99025 | -0.18501 | 0.99086 | -0.17339 | 36.7125
94 | -0.0026145 | -0.00065525 | 0.0026147 | 0.00065495 | 1.9269e-07 | -2.9747e-07 | 0.0039462 | 0.003946 | 0.0039462 | 0.98586 | -0.27002 | 0.98594 | -0.26848 | 1.0841
95 | -0.0033978 | -0.00085124 | 0.003398 | 0.00085117 | 1.0729e-07 | -7.0094e-08 | 0.005128 | 0.005128 | 0.005128 | 0.98594 | -0.26848 | 0.98597 | -0.26781 | 1.4088
96 | 0.14431 | 0.036772 | -0.1442 | -0.036702 | 0.00010896 | 6.9417e-05 | 0.2175 | 0.2175 | 0.2175 | 0.9883 | -0.22245 | 0.98749 | -0.23811 | 29.8758
97 | 0.031901 | 0.0080099 | -0.031887 | -0.0080012 | 1.4019e-05 | 8.7644e-06 | 0.048036 | 0.048036 | 0.048036 | 0.9883 | -0.22245 | 0.98783 | -0.23167 | 13.1966
98 | -0.18906 | -0.048162 | 0.18976 | 0.048609 | 0.00070007 | 0.00044685 | 0.28419 | 0.28419 | 0.28419 | 0.99086 | -0.17339 | 0.99487 | -0.096939 | 39.0374
99 | -0.003398 | -0.00085117 | 0.0033982 | 0.00085102 | 2.1619e-07 | -1.4127e-07 | 0.005128 | 0.0051279 | 0.005128 | 0.98597 | -0.26781 | 0.98604 | -0.26648 | 1.4088
100 | 0.14229 | 0.036224 | -0.14227 | -0.036211 | 2.0761e-05 | 1.3226e-05 | 0.21462 | 0.21462 | 0.21462 | 0.98749 | -0.23811 | 0.98733 | -0.24114 | 29.4806
101 | 0.030587 | 0.0076755 | -0.030579 | -0.0076704 | 8.1183e-06 | 5.0652e-06 | 0.046078 | 0.046078 | 0.046078 | 0.98783 | -0.23167 | 0.98754 | -0.23723 | 12.6589
102 | -0.18976 | -0.048609 | 0.19007 | 0.048806 | 0.00030943 | 0.00019751 | 0.28419 | 0.28419 | 0.28419 | 0.99487 | -0.096939 | 0.99664 | -0.063345 | 39.0373
103 | -0.0047995 | -0.0012022 | 0.0047999 | 0.0012022 | 4.4281e-07 | -3.7789e-09 | 0.0072426 | 0.0072425 | 0.0072426 | 0.98604 | -0.26648 | 0.98614 | -0.26454 | 1.9897
104 | -0.0041558 | -0.0010415 | 0.004156 | 0.0010415 | 2.0775e-07 | -4.3302e-08 | 0.0063016 | 0.0063015 | 0.0063016 | 0.98131 | -0.35826 | 0.98137 | -0.35721 | 1.7312
105 | 0.0021276 | 0.00053322 | -0.0021276 | -0.00053323 | 1.695e-09 | -4.4023e-09 | 0.0032262 | 0.0032262 | 0.0032262 | 0.98131 | -0.35826 | 0.98131 | -0.35827 | 0.88631
106 | -0.0066123 | -0.0016571 | 0.0066128 | 0.0016572 | 4.7463e-07 | 1.4466e-07 | 0.010026 | 0.010026 | 0.010026 | 0.98137 | -0.35721 | 0.98144 | -0.3557 | 2.7544
107 | -0.0082479 | -0.002067 | 0.0082488 | 0.0020674 | 9.0964e-07 | 3.8612e-07 | 0.012505 | 0.012505 | 0.012505 | 0.98144 | -0.3557 | 0.98156 | -0.35338 | 3.4354
108 | 0.0051816 | 0.0012983 | -0.005181 | -0.0012982 | 6.6936e-07 | 7.6153e-08 | 0.0079285 | 0.0079287 | 0.0079287 | 0.97247 | -0.5309 | 0.97233 | -0.53361 | 2.1782
109 | 0.0028421 | 0.00071203 | -0.0028419 | -0.00071224 | 1.9198e-07 | -2.1277e-07 | 0.0043494 | 0.0043495 | 0.0043495 | 0.97233 | -0.53361 | 0.97226 | -0.53503 | 1.1949
110 | 0.0028419 | 0.00071224 | -0.0028419 | -0.00071225 | 1.081e-08 | -1.1978e-08 | 0.0043495 | 0.0043495 | 0.0043495 | 0.97226 | -0.53503 | 0.97225 | -0.53511 | 1.1949
111 | 0.001868 | 0.0004679 | -0.0018679 | -0.00046814 | 7.0343e-08 | -2.4222e-07 | 0.0028523 | 0.0028524 | 0.0028524 | 0.97449 | -0.49105 | 0.97445 | -0.49184 | 0.78361
112 | 0.0081817 | 0.00205 | -0.0081807 | -0.0020495 | 1.0711e-06 | 4.4626e-07 | 0.012343 | 0.012343 | 0.012343 | 0.98632 | -0.26098 | 0.98618 | -0.26373 | 3.391
113 | -0.0093285 | -0.0023374 | 0.0093293 | 0.0023378 | 8.4159e-07 | 3.9398e-07 | 0.014073 | 0.014073 | 0.014073 | 0.98632 | -0.26098 | 0.98642 | -0.25909 | 3.8663
114 | 0.0072584 | 0.0018184 | -0.0072581 | -0.0018183 | 2.8049e-07 | 9.9945e-08 | 0.010952 | 0.010952 | 0.010952 | 0.98618 | -0.26373 | 0.98614 | -0.26454 | 3.0087
115 | -0.01066 | -0.0026714 | 0.010661 | 0.0026719 | 9.808e-07 | 4.9859e-07 | 0.016081 | 0.016081 | 0.016081 | 0.98642 | -0.25909 | 0.98652 | -0.25715 | 4.4179
116 | -0.01135 | -0.0028446 | 0.011351 | 0.0028449 | 6.5947e-07 | 3.4545e-07 | 0.01712 | 0.01712 | 0.01712 | 0.98652 | -0.25715 | 0.98658 | -0.25593 | 4.7034
117 | -0.012417 | -0.003112 | 0.012418 | 0.0031128 | 1.4013e-06 | 7.6074e-07 | 0.018728 | 0.018728 | 0.018728 | 0.98658 | -0.25593 | 0.9867 | -0.25357 | 5.1449
118 | -0.014329 | -0.0035917 | 0.014332 | 0.0035932 | 2.6315e-06 | 1.4922e-06 | 0.02161 | 0.02161 | 0.02161 | 0.9867 | -0.25357 | 0.9869 | -0.24971 | 5.9367
119 | 0.027852 | 0.006987 | -0.027849 | -0.006985 | 3.2124e-06 | 1.9937e-06 | 0.041969 | 0.041969 | 0.041969 | 0.98754 | -0.23723 | 0.98742 | -0.23965 | 11.5301
120 | 0.025941 | 0.0065069 | -0.025934 | -0.0065027 | 6.8202e-06 | 4.2128e-06 | 0.039095 | 0.039095 | 0.039095 | 0.98742 | -0.23965 | 0.98714 | -0.24517 | 10.7403
121 | 0.022335 | 0.0056005 | -0.022332 | -0.005599 | 2.5149e-06 | 1.5339e-06 | 0.033669 | 0.033669 | 0.033669 | 0.98714 | -0.24517 | 0.98701 | -0.24753 | 9.2496
122 | 0.020188 | 0.0050617 | -0.020186 | -0.0050606 | 1.7328e-06 | 1.0452e-06 | 0.030436 | 0.030436 | 0.030436 | 0.98701 | -0.24753 | 0.98692 | -0.24934 | 8.3616
123 | 0.13638 | 0.034735 | -0.13612 | -0.034568 | 0.0002611 | 0.00016689 | 0.20574 | 0.20574 | 0.20574 | 0.98733 | -0.24114 | 0.98527 | -0.28091 | 56.5229
124 | 0.017684 | 0.0044334 | -0.017684 | -0.0044333 | 3.1731e-07 | 1.8787e-07 | 0.026663 | 0.026663 | 0.026663 | 0.98692 | -0.24934 | 0.9869 | -0.24971 | 7.3251
125 | -0.0069369 | -0.0017385 | 0.006938 | 0.0017389 | 1.1689e-06 | 3.8709e-07 | 0.010482 | 0.010482 | 0.010482 | 0.98474 | -0.29229 | 0.98493 | -0.28875 | 2.8797
126 | 0.19355 | 0.049912 | -0.19296 | -0.049532 | 0.00059523 | 0.00037995 | 0.28851 | 0.28851 | 0.28851 | 1 | 0 | 0.99664 | -0.063345 | 39.6307
127 | 0.18539 | 0.047646 | -0.18465 | -0.047176 | 0.00073661 | 0.00047009 | 0.27628 | 0.27628 | 0.27628 | 1 | 0 | 0.99566 | -0.082144 | 37.9504
128 | 0.17931 | 0.045837 | -0.179 | -0.045643 | 0.0003053 | 0.00019481 | 0.2683 | 0.2683 | 0.2683 | 0.99566 | -0.082144 | 0.99381 | -0.11741 | 36.8538
129 | 0.0092087 | 0.0023083 | -0.0092063 | -0.0023072 | 2.4313e-06 | 1.1143e-06 | 0.013788 | 0.013788 | 0.013788 | 0.99381 | -0.11741 | 0.99352 | -0.12295 | 3.788
130 | 0.16979 | 0.043334 | -0.16937 | -0.043065 | 0.00042272 | 0.00026964 | 0.25451 | 0.25451 | 0.25451 | 0.99381 | -0.11741 | 0.99111 | -0.16908 | 34.9599
131 | 0.0050859 | 0.0012745 | -0.0050859 | -0.0012745 | 5.0206e-08 | 2.251e-09 | 0.0076172 | 0.0076172 | 0.0076172 | 0.99352 | -0.12295 | 0.99351 | -0.12316 | 2.0926
132 | 0.16798 | 0.042717 | -0.16771 | -0.042542 | 0.0002741 | 0.00017483 | 0.25242 | 0.25242 | 0.25242 | 0.99111 | -0.16908 | 0.98934 | -0.20301 | 34.6736
133 | 0.0050859 | 0.0012745 | -0.0050854 | -0.0012745 | 5.0196e-07 | 2.2546e-08 | 0.0076172 | 0.0076173 | 0.0076173 | 0.99351 | -0.12316 | 0.99341 | -0.12523 | 2.0927
134 | 0.03797 | 0.0095506 | -0.037961 | -0.0095451 | 8.7689e-06 | 5.5207e-06 | 0.057216 | 0.057216 | 0.057216 | 0.9877 | -0.23479 | 0.98745 | -0.23963 | 15.7186
135 | 0.036963 | 0.009295 | -0.036945 | -0.0092838 | 1.7768e-05 | 1.1176e-05 | 0.055712 | 0.055712 | 0.055712 | 0.98745 | -0.23963 | 0.98693 | -0.2497 | 15.3054
136 | 0.035865 | 0.0090132 | -0.035834 | -0.0089933 | 3.1624e-05 | 1.9871e-05 | 0.054084 | 0.054084 | 0.054084 | 0.98693 | -0.2497 | 0.98598 | -0.26818 | 14.8582
137 | 0.13257 | 0.033677 | -0.13253 | -0.03365 | 4.1561e-05 | 2.6564e-05 | 0.20037 | 0.20037 | 0.20037 | 0.98527 | -0.28091 | 0.98493 | -0.28743 | 55.0476
138 | -0.0017089 | -0.0004283 | 0.0017089 | 0.00042827 | 6.3842e-09 | -2.9552e-08 | 0.0025598 | 0.0025598 | 0.0025598 | 0.9934 | -0.12531 | 0.99341 | -0.12523 | 0.70324

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38346 | 0.098278

## res_load
| p_mw | q_mvar
0 | 0.009492 | 0.0023789
1 | 0.029053 | 0.0072813
2 | 0.0038404 | 0.0009625
3 | 0.00041185 | 0.00010322
4 | 0.00093325 | 0.00023389
5 | 0.0032028 | 0.0008027
6 | 0.0016829 | 0.00042178
7 | 0.0021162 | 0.00053036
8 | 0.0028012 | 0.00070205
9 | 0.0020655 | 0.00051766
10 | 0.0015274 | 0.00038279
11 | 0.0034431 | 0.00086292
12 | 0.0021839 | 0.00054734
13 | 0.0020822 | 0.00052185
14 | 0.0012591 | 0.00031556
15 | 0.0020045 | 0.00050237
16 | 0.0019838 | 0.00049719
17 | 0.0020316 | 0.00050917
18 | 0.0023016 | 0.00057684
19 | 0.0033444 | 0.00083819
20 | 0.0055972 | 0.0014028
21 | 0.0055787 | 0.0013982
22 | 0.0021599 | 0.00054133
23 | 0.0021824 | 0.00054697
24 | 0.0035925 | 0.00090036
25 | 0.0035808 | 0.00089744
26 | 0.0029519 | 0.00073982
27 | 0.0033746 | 0.00084577
28 | 0.0031556 | 0.00079087
29 | 0.0042628 | 0.0010684
30 | 0.0010072 | 0.00025242
31 | 0.00077764 | 0.0001949
32 | 0.025812 | 0.0064692
33 | 0.00078874 | 0.00019768
34 | 0.0032431 | 0.00081279
35 | 0.0018192 | 0.00045594
36 | 0.015671 | 0.0039275
37 | 0.0019746 | 0.00049489
38 | 0.0016321 | 0.00040904
39 | 0.0010168 | 0.00025483
40 | 0.0021569 | 0.00054058
41 | 0.0039733 | 0.0009958
42 | 0.0049049 | 0.0012293
43 | 0.00070333 | 0.00017627
44 | 0.00694 | 0.0017393
45 | 0.0068222 | 0.0017098
46 | 0.0013646 | 0.00034201
47 | 0.0024572 | 0.00061583
48 | 0.0029675 | 0.00074373
49 | 0.00089113 | 0.00022334
50 | 0.0051362 | 0.0012873
51 | 0.0020699 | 0.00051878
52 | 0.0017548 | 0.0004398
53 | 0.0028376 | 0.00071118
54 | 0.0050084 | 0.0012552
55 | 0.0032275 | 0.00080888
56 | 0.0014943 | 0.00037452
57 | 0.0025808 | 0.00064681
58 | 0.0025687 | 0.00064378
59 | 0.0033471 | 0.00083886
60 | 0.0019009 | 0.00047641
61 | 0.0074788 | 0.0018744
62 | 0.0017152 | 0.00042987
63 | 0.00069562 | 0.00017434
64 | 0.00045972 | 0.00011522
65 | 0.0026145 | 0.00065525
66 | 0.00078317 | 0.00019628
67 | 0.01127 | 0.0028246
68 | 0.0019091 | 0.00047847
69 | 0.0012994 | 0.00032567
70 | 0.0014013 | 0.0003512
71 | 0.0020282 | 0.00050831
72 | 0.0024563 | 0.00061562
73 | 0.0021276 | 0.00053323
74 | 0.0016351 | 0.00040979
75 | 0.0024176 | 0.0006059
76 | 0.0023388 | 0.00058617
77 | 0.0010874 | 0.00027252
78 | 0.0018683 | 0.00046825
79 | 0.0018679 | 0.00046814
80 | 0.0011468 | 0.00028741
81 | 0.0009223 | 0.00023115
82 | 0.0013311 | 0.00033359
83 | 0.0024581 | 0.00061607
84 | 0.00068912 | 0.00017271
85 | 0.0010656 | 0.00026706
86 | 0.0019111 | 0.00047897
87 | 0.002727 | 0.00068345
88 | 0.0019077 | 0.00047811
89 | 0.0035996 | 0.00090215
90 | 0.002144 | 0.00053734
91 | 0.0058894 | 0.001476
92 | 0.0025024 | 0.00062717
93 | 0.0069369 | 0.0017385
94 | 0.0097669 | 0.0024478
95 | 0.0028718 | 0.00071975
96 | 0.0028937 | 0.00072522
97 | 0.0053417 | 0.0013388
98 | 0.0041204 | 0.0010327
99 | 0.0013883 | 0.00034793
100 | 0.0064594 | 0.0016189
101 | 0.0012896 | 0.00032321
102 | 0.00099813 | 0.00025016
103 | 0.0010798 | 0.00027061
104 | 0.0033518 | 0.00084004
105 | 0.0017199 | 0.00043106
106 | 0.0035556 | 0.00089111
107 | 0.0058618 | 0.0014691
108 | 0.0028419 | 0.00071225
109 | 0.00070525 | 0.00017675
110 | 0.0017089 | 0.0004283
111 | 0.0033764 | 0.00084621

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1