## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2499-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2499-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2499-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2499-1_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2499-1_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2499-1_0_3_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_2499-1_0_3_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_2499-1_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2499-1_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2499-1_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2499-1_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2499-1_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2499-1_0_3_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_2499-1_0_3_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_2499-1_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2499-1_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2499-1_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2499-1_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2499-1_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2499-1_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2499-1_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2499-1_0_3_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_2499-1_0_3_node_55 | 0.4 | n |  | TRUE
23 | bus_LV_2499-1_0_3_node_47 | 0.4 | n |  | TRUE
24 | bus_LV_2499-1_0_3_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_2499-1_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_2499-1_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2499-1_0_3_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_2499-1_0_3_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_2499-1_0_3_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_2499-1_0_3_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_2499-1_0_3_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_2499-1_0_3_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_2499-1_0_3_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_2499-1_0_3_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_2499-1_0_3_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_2499-1_0_3_node_54 | 0.4 | n |  | TRUE
37 | bus_LV_2499-1_0_3_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_2499-1_0_3_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_2499-1_0_3_node_53 | 0.4 | n |  | TRUE
40 | bus_LV_2499-1_0_3_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_2499-1_0_3_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_2499-1_0_3_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_2499-1_0_3_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_2499-1_0_3_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_2499-1_0_3_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_2499-1_0_3_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_2499-1_0_3_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_2499-1_0_3_node_238 | 0.4 | n |  | TRUE
49 | bus_LV_2499-1_0_3_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_2499-1_0_3_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_2499-1_0_3_node_44 | 0.4 | n |  | TRUE
52 | bus_LV_2499-1_0_3_node_419 | 0.4 | n |  | TRUE
53 | bus_LV_2499-1_0_3_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_2499-1_0_3_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_2499-1_0_3_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_2499-1_0_3_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_2499-1_0_3_node_56 | 0.4 | n |  | TRUE
58 | bus_LV_2499-1_0_3_node_314 | 0.4 | n |  | TRUE
59 | bus_LV_2499-1_0_3_node_389 | 0.4 | n |  | TRUE
60 | bus_LV_2499-1_0_3_node_159 | 0.4 | n |  | TRUE
61 | bus_LV_2499-1_0_3_node_157 | 0.4 | n |  | TRUE
62 | bus_LV_2499-1_0_3_node_160 | 0.4 | n |  | TRUE
63 | bus_LV_2499-1_0_3_node_158 | 0.4 | n |  | TRUE
64 | bus_LV_2499-1_0_3_node_300 | 0.4 | n |  | TRUE
65 | bus_LV_2499-1_0_3_node_388 | 0.4 | n |  | TRUE
66 | bus_LV_2499-1_0_3_node_199 | 0.4 | n |  | TRUE
67 | bus_LV_2499-1_0_3_node_239 | 0.4 | n |  | TRUE
68 | bus_LV_2499-1_0_3_node_301 | 0.4 | n |  | TRUE
69 | bus_LV_2499-1_0_3_node_240 | 0.4 | n |  | TRUE
70 | bus_LV_2499-1_0_3_node_426 | 0.4 | n |  | TRUE
71 | bus_LV_2499-1_0_3_node_427 | 0.4 | n |  | TRUE
72 | bus_LV_2499-1_0_3_node_236 | 0.4 | n |  | TRUE
73 | bus_LV_2499-1_0_3_node_237 | 0.4 | n |  | TRUE
74 | bus_MV_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2499-1_0_3_load_0 | 0 | 0.0015813 | 0.00039631 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2499-1_0_3_load_1 | 1 | 0.0049758 | 0.0012471 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2499-1_0_3_load_26 | 5 | 0.0023787 | 0.00059617 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2499-1_0_3_load_22 | 6 | 0.0014559 | 0.00036489 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2499-1_0_3_load_5 | 7 | 0.00031998 | 8.0195e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2499-1_0_3_load_6 | 8 | 0.00049967 | 0.00012523 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2499-1_0_3_load_8 | 10 | 0.00051452 | 0.00012895 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2499-1_0_3_load_9 | 11 | 0.00054922 | 0.00013765 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2499-1_0_3_load_31 | 12 | 0.00047841 | 0.0001199 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2499-1_0_3_load_10 | 14 | 0.00060057 | 0.00015052 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2499-1_0_3_load_13 | 17 | 0.0015827 | 0.00039667 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2499-1_0_3_load_15 | 18 | 0.00134 | 0.00033583 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2499-1_0_3_load_16 | 19 | 0.00048361 | 0.00012121 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2499-1_0_3_load_20 | 21 | 0.0019317 | 0.00048414 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2499-1_0_3_load_55 | 22 | 0.0003865 | 9.6866e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2499-1_0_3_load_47 | 23 | 0.00066748 | 0.00016729 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2499-1_0_3_load_42 | 24 | 0.0009639 | 0.00024158 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2499-1_0_3_load_17 | 25 | 0.00037033 | 9.2814e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2499-1_0_3_load_19 | 27 | 0.00028719 | 7.1977e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2499-1_0_3_load_33 | 28 | 0.0021798 | 0.00054631 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2499-1_0_3_load_21 | 29 | 0.00025275 | 6.3346e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2499-1_0_3_load_25 | 33 | 0.0018529 | 0.00046437 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2499-1_0_3_load_30 | 34 | 0.0023428 | 0.00058716 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2499-1_0_3_load_27 | 35 | 0.0012365 | 0.00030989 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2499-1_0_3_load_54 | 36 | 0.002359 | 0.00059121 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2499-1_0_3_load_28 | 37 | 0.0075003 | 0.0018798 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2499-1_0_3_load_29 | 38 | 0.0006148 | 0.00015408 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2499-1_0_3_load_32 | 41 | 0.00042782 | 0.00010722 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2499-1_0_3_load_40 | 42 | 0.0011964 | 0.00029984 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2499-1_0_3_load_41 | 43 | 0.0012234 | 0.00030663 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2499-1_0_3_load_36 | 44 | 0.0010362 | 0.00025969 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2499-1_0_3_load_37 | 45 | 0.00020112 | 5.0405e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2499-1_0_3_load_52 | 50 | 0.00068387 | 0.00017139 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2499-1_0_3_load_44 | 51 | 0.00019275 | 4.8307e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2499-1_0_3_load_419 | 52 | 0.00040394 | 0.00010124 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2499-1_0_3_load_46 | 53 | 0.00025451 | 6.3786e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2499-1_0_3_load_49 | 54 | 0.0006965 | 0.00017456 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2499-1_0_3_load_50 | 55 | 0.0025262 | 0.00063314 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2499-1_0_3_load_51 | 56 | 0.00073505 | 0.00018422 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2499-1_0_3_load_56 | 57 | 0.0011851 | 0.00029702 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2499-1_0_3_load_314 | 58 | 0.00056355 | 0.00014124 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2499-1_0_3_load_159 | 60 | 0.00064461 | 0.00016155 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2499-1_0_3_load_157 | 61 | 0.00079846 | 0.00020011 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2499-1_0_3_load_160 | 62 | 0.00019468 | 4.8792e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2499-1_0_3_load_158 | 63 | 0.00072622 | 0.00018201 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2499-1_0_3_load_239 | 67 | 0.0017683 | 0.00044317 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2499-1_0_3_load_301 | 68 | 0.00026236 | 6.5753e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2499-1_0_3_load_426 | 70 | 0.00018934 | 4.7453e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2499-1_0_3_load_427 | 71 | 0.00012846 | 3.2195e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2499-1_0_3_load_236 | 72 | 0.00035371 | 8.8649e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2499-1_0_3_line_0 |  | 0 | 1 | 0.01047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2499-1_0_3_line_1 |  | 0 | 2 | 0.05167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2499-1_0_3_line_2 |  | 2 | 3 | 0.01398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2499-1_0_3_line_3 |  | 3 | 5 | 0.0079937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2499-1_0_3_line_4 |  | 4 | 5 | 0.0050333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2499-1_0_3_line_5 |  | 4 | 6 | 0.022018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2499-1_0_3_line_6 |  | 6 | 31 | 0.052714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2499-1_0_3_line_7 |  | 7 | 8 | 0.018898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2499-1_0_3_line_8 |  | 7 | 9 | 0.015743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2499-1_0_3_line_9 |  | 8 | 10 | 0.031416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2499-1_0_3_line_10 |  | 9 | 11 | 0.013254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2499-1_0_3_line_11 |  | 10 | 12 | 0.0021963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2499-1_0_3_line_12 |  | 11 | 13 | 0.057885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2499-1_0_3_line_13 |  | 12 | 40 | 0.2296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2499-1_0_3_line_14 |  | 13 | 53 | 0.033911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2499-1_0_3_line_15 |  | 13 | 23 | 0.007545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2499-1_0_3_line_16 |  | 14 | 15 | 0.019243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2499-1_0_3_line_17 |  | 14 | 16 | 0.0016872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2499-1_0_3_line_18 |  | 15 | 17 | 0.021379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2499-1_0_3_line_19 |  | 15 | 18 | 0.034769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2499-1_0_3_line_20 |  | 16 | 19 | 0.051674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2499-1_0_3_line_21 |  | 16 | 20 | 0.026189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2499-1_0_3_line_22 |  | 17 | 21 | 0.018779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2499-1_0_3_line_23 |  | 18 | 23 | 0.071431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2499-1_0_3_line_24 |  | 19 | 24 | 0.018035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2499-1_0_3_line_25 |  | 20 | 22 | 0.017899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2499-1_0_3_line_26 |  | 21 | 29 | 0.0049627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2499-1_0_3_line_27 |  | 22 | 41 | 0.047114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2499-1_0_3_line_28 |  | 24 | 49 | 0.11015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2499-1_0_3_line_29 |  | 25 | 26 | 0.014943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2499-1_0_3_line_30 |  | 26 | 27 | 0.032783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2499-1_0_3_line_31 |  | 27 | 28 | 0.0090687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2499-1_0_3_line_32 |  | 28 | 40 | 0.048699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2499-1_0_3_line_33 |  | 29 | 30 | 0.020807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2499-1_0_3_line_34 |  | 30 | 42 | 0.043702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2499-1_0_3_line_35 |  | 30 | 43 | 0.025028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2499-1_0_3_line_36 |  | 31 | 32 | 0.006383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2499-1_0_3_line_37 |  | 31 | 33 | 0.014353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2499-1_0_3_line_38 |  | 32 | 34 | 0.031895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2499-1_0_3_line_39 |  | 32 | 35 | 0.074939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2499-1_0_3_line_40 |  | 33 | 36 | 0.027371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2499-1_0_3_line_41 |  | 34 | 39 | 0.010909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2499-1_0_3_line_42 |  | 35 | 37 | 0.0020993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2499-1_0_3_line_43 |  | 37 | 38 | 0.0065544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2499-1_0_3_line_44 |  | 39 | 57 | 0.012407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2499-1_0_3_line_45 |  | 39 | 56 | 0.022628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2499-1_0_3_line_46 |  | 42 | 50 | 3.0158e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2499-1_0_3_line_47 |  | 44 | 45 | 0.024587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2499-1_0_3_line_48 |  | 44 | 46 | 0.16158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2499-1_0_3_line_49 |  | 45 | 47 | 0.0035865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2499-1_0_3_line_50 |  | 46 | 48 | 0.41028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2499-1_0_3_line_51 |  | 47 | 49 | 0.034423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2499-1_0_3_line_52 |  | 48 | 72 | 0.0026195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2499-1_0_3_line_53 |  | 49 | 51 | 0.04508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2499-1_0_3_line_54 |  | 50 | 55 | 0.015744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2499-1_0_3_line_55 |  | 51 | 52 | 0.0098766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2499-1_0_3_line_56 |  | 54 | 55 | 0.014317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2499-1_0_3_line_57 |  | 54 | 56 | 0.010035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2499-1_0_3_line_58 |  | 58 | 59 | 0.041579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2499-1_0_3_line_59 |  | 59 | 66 | 0.10237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2499-1_0_3_line_60 |  | 59 | 69 | 0.18915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2499-1_0_3_line_61 |  | 60 | 61 | 0.0099102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2499-1_0_3_line_62 |  | 61 | 63 | 0.014786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2499-1_0_3_line_63 |  | 62 | 63 | 0.018298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2499-1_0_3_line_64 |  | 62 | 64 | 0.029754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2499-1_0_3_line_65 |  | 64 | 68 | 0.053081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2499-1_0_3_line_66 |  | 65 | 66 | 0.10358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2499-1_0_3_line_67 |  | 65 | 67 | 0.18257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2499-1_0_3_line_68 |  | 65 | 68 | 0.15449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2499-1_0_3_line_69 |  | 67 | 73 | 0.036933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2499-1_0_3_line_70 |  | 69 | 70 | 0.017731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2499-1_0_3_line_71 |  | 70 | 71 | 0.30834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2499-1_0_3_line_72 |  | 72 | 73 | 0.03857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2499-1_0_3_trafo_12 | 0.63 MVA 20/0.4 kV | 74 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34
0 | 2638742.8662 | 1251291.6562 | 2638752.4571 | 1251293.518 | 2638753.1491 | 1251293.6222
1 | 2638705.1121 | 1251264.5562 | 2638705.227 | 1251267.7702 | 2638706.159 | 1251272.9798 | 2638709.0381 | 1251278.2354 | 2638715.6052 | 1251283.8932 | 2638720.2536 | 1251286.3362 | 2638730.8233 | 1251289.3184 | 2638742.8662 | 1251291.6562
2 | 2638700.7989 | 1251252.3865 | 2638701.0535 | 1251255.0122 | 2638705.6247 | 1251260.0343 | 2638705.1121 | 1251264.5562
3 | 2638700.7989 | 1251252.3865 | 2638704.026 | 1251249.4056 | 2638707.5261 | 1251248.5612
4 | 2638711.8644 | 1251251.1134 | 2638707.5261 | 1251248.5612
5 | 2638711.8644 | 1251251.1134 | 2638714.2787 | 1251248.9277 | 2638718.7637 | 1251246.3553 | 2638723.6982 | 1251244.2972 | 2638729.2949 | 1251242.5214 | 2638731.5655 | 1251241.8344
6 | 2638782.323 | 1251227.6913 | 2638775.1824 | 1251230.0907 | 2638767.3398 | 1251232.5077 | 2638752.8928 | 1251236.1046 | 2638736.381 | 1251240.3774 | 2638731.5655 | 1251241.8344
7 | 2639124.9232 | 1251177.0294 | 2639125.6231 | 1251175.3549 | 2639132.331 | 1251159.6442
8 | 2639118.8517 | 1251191.5544 | 2639124.9232 | 1251177.0294
9 | 2639132.331 | 1251159.6442 | 2639132.331 | 1251159.6442 | 2639132.4927 | 1251154.5863 | 2639125.2004 | 1251150.2019 | 2639109.3777 | 1251141.9479
10 | 2639118.8517 | 1251191.5544 | 2639111.9025 | 1251185.5046 | 2639108.6114 | 1251183.161
11 | 2639107.4304 | 1251140.932 | 2639109.3777 | 1251141.9479
12 | 2639056.7011 | 1251157.7 | 2639079.8973 | 1251168.8047 | 2639097.198 | 1251176.6017 | 2639105.2991 | 1251180.8023 | 2639108.6114 | 1251183.161
13 | 2639107.4304 | 1251140.932 | 2639204.5975 | 1250932.9027
14 | 2639056.7011 | 1251157.7 | 2639048.5964 | 1251159.7591 | 2639044.1064 | 1251159.6184 | 2639027.3425 | 1251158.5518 | 2639023.1783 | 1251159.4453
15 | 2639056.7011 | 1251157.7 | 2639049.9021 | 1251154.4287
16 | 2638955.6043 | 1251106.501 | 2638952.7972 | 1251099.5 | 2638950.4988 | 1251093.203 | 2638949.3119 | 1251088.3493
17 | 2638948.9112 | 1251086.7104 | 2638949.3119 | 1251088.3493
18 | 2638955.6043 | 1251106.501 | 2638947.7041 | 1251114.1987 | 2638939.2659 | 1251120.1904
19 | 2638955.6043 | 1251106.501 | 2638960.275 | 1251111.3015 | 2638977.0656 | 1251118.6612 | 2638985.9633 | 1251122.6186
20 | 2638948.9112 | 1251086.7104 | 2638946.7072 | 1251076.3779 | 2638943.4009 | 1251059.2002 | 2638938.524 | 1251036.093
21 | 2638974.8975 | 1251084.5018 | 2638968.2369 | 1251083.8799 | 2638956.7727 | 1251084.9053 | 2638948.9112 | 1251086.7104
22 | 2638923.9127 | 1251130.9905 | 2638926.804 | 1251129.2049 | 2638933.1976 | 1251124.4993 | 2638939.2659 | 1251120.1904
23 | 2639049.9021 | 1251154.4287 | 2639038.0043 | 1251148.7042 | 2639013.6989 | 1251136.3694 | 2638995.639 | 1251126.9221 | 2638985.9633 | 1251122.6186
24 | 2638934.4488 | 1251018.5392 | 2638935.5979 | 1251022.202 | 2638938.5038 | 1251035.997 | 2638938.524 | 1251036.093
25 | 2638974.8975 | 1251084.5018 | 2638990.3864 | 1251093.4726
26 | 2638923.9127 | 1251130.9905 | 2638921.3172 | 1251132.5934 | 2638919.6286 | 1251133.4906
27 | 2638990.3864 | 1251093.4726 | 2639000.1016 | 1251099.0995 | 2639005.1986 | 1251102.2017 | 2639009.5996 | 1251104.3988 | 2639013.8013 | 1251105.9052 | 2639019.6032 | 1251107.3999 | 2639033.8588 | 1251110.292
28 | 2638911.7975 | 1250912.1054 | 2638912.0043 | 1250917.3992 | 2638913.002 | 1250924.0991 | 2638915.099 | 1250933.497 | 2638916.4041 | 1250942.8007 | 2638917.1035 | 1250950.099 | 2638917.197 | 1250955.4032 | 2638916.8993 | 1250960.5047 | 2638916.9023 | 1250968.0986 | 2638917.5973 | 1250974.8967 | 2638918.9041 | 1250980.4979 | 2638922.1979 | 1250988.1023 | 2638929.5016 | 1251004.6058 | 2638932.8994 | 1251013.6008 | 2638934.4488 | 1251018.5392
29 | 2639289.1008 | 1250964.2049 | 2639294.4642 | 1250974.9365 | 2639296.3395 | 1250977.2082
30 | 2639289.1008 | 1250964.2049 | 2639274.2002 | 1250959.8033 | 2639265.2039 | 1250957.3977 | 2639258.8014 | 1250955.3984 | 2639257.6606 | 1250954.9488
31 | 2639249.2536 | 1250951.5512 | 2639251.1978 | 1250952.4017 | 2639257.6606 | 1250954.9488
32 | 2639204.5975 | 1250932.9027 | 2639208.2041 | 1250933.1044 | 2639211.0979 | 1250933.8018 | 2639214.8028 | 1250935.1049 | 2639223.3969 | 1250938.9977 | 2639244.1007 | 1250949.2971 | 2639249.2536 | 1250951.5512
33 | 2638900.7471 | 1251142.1871 | 2638907.2097 | 1251139.6167 | 2638914.455 | 1251136.2397 | 2638919.6286 | 1251133.4906
34 | 2638900.7471 | 1251142.1871 | 2638891.3838 | 1251145.1277 | 2638877.2042 | 1251148.2035 | 2638862.5994 | 1251150.4982 | 2638858.1024 | 1251151.4417
35 | 2638900.7471 | 1251142.1871 | 2638901.3997 | 1251145.1045 | 2638901.4001 | 1251146.2052 | 2638901.0968 | 1251148.7049 | 2638899.7974 | 1251151.198 | 2638895.103 | 1251159.206 | 2638894.2 | 1251163.4029 | 2638894.602 | 1251165.3957
36 | 2638782.323 | 1251227.6913 | 2638788.0775 | 1251224.8937
37 | 2638782.323 | 1251227.6913 | 2638776.7984 | 1251224.1973 | 2638770.5981 | 1251221.2992 | 2638769.6769 | 1251220.9887
38 | 2638788.0775 | 1251224.8937 | 2638790.842 | 1251221.1092 | 2638794.5985 | 1251215.6857 | 2638797.0766 | 1251211.8438 | 2638801.3184 | 1251204.9224 | 2638804.5933 | 1251197.7097
39 | 2638788.0775 | 1251224.8937 | 2638794.403 | 1251229.4047 | 2638804.9005 | 1251231.8973 | 2638814.6024 | 1251233.7064 | 2638816.7988 | 1251233.6986 | 2638821.1626 | 1251232.3484 | 2638839.7225 | 1251225.3764 | 2638844.6351 | 1251222.0507 | 2638850.4057 | 1251211.0367 | 2638850.9267 | 1251209.5723
40 | 2638743.904 | 1251211.7962 | 2638752.8024 | 1251215.3012 | 2638769.6769 | 1251220.9887
41 | 2638809.5579 | 1251188.0095 | 2638806.8551 | 1251192.7283 | 2638804.5933 | 1251197.7097
42 | 2638851.6304 | 1251207.5945 | 2638850.9267 | 1251209.5723
43 | 2638853.8274 | 1251201.4193 | 2638851.6304 | 1251207.5945
44 | 2638809.5579 | 1251188.0095 | 2638805.7962 | 1251184.9939 | 2638800.0781 | 1251180.0094
45 | 2638809.5579 | 1251188.0095 | 2638817.3305 | 1251176.6972 | 2638823.354 | 1251170.1414
46 | 2638858.1024 | 1251151.4417 | 2638858.0729 | 1251151.4479
47 | 2638938.0353 | 1250855.9712 | 2638930.2004 | 1250868.2968 | 2638925.0024 | 1250876.8186
48 | 2638987.5707 | 1250704.5195 | 2638983.6618 | 1250710.0864 | 2638982.7513 | 1250711.9595 | 2638982.1295 | 1250714.6794 | 2638978.6817 | 1250737.3831 | 2638974.7661 | 1250762.3519 | 2638973.1847 | 1250772.1258 | 2638970.7539 | 1250783.6398 | 2638968.08 | 1250794.2626 | 2638965.7686 | 1250802.5641 | 2638963.1805 | 1250810.4524 | 2638960.7534 | 1250816.8296 | 2638958.1211 | 1250822.2715 | 2638954.8418 | 1250828.532 | 2638950.8997 | 1250835.7331 | 2638938.0353 | 1250855.9712
49 | 2638923.1349 | 1250879.8805 | 2638925.0024 | 1250876.8186
50 | 2639280.3394 | 1250417.0917 | 2638987.5707 | 1250704.5195
51 | 2638911.7975 | 1250912.1054 | 2638912.5031 | 1250905.8058 | 2638913.6025 | 1250901.5991 | 2638915.204 | 1250896.8064 | 2638923.1349 | 1250879.8805
52 | 2639280.3394 | 1250417.0917 | 2639282.8258 | 1250416.2674
53 | 2638911.7975 | 1250912.1054 | 2638906.7382 | 1250920.489 | 2638903.2453 | 1250932.8633 | 2638903.3386 | 1250945.1054 | 2638902.8388 | 1250955.281
54 | 2638843.1549 | 1251156.2763 | 2638851.6025 | 1251152.8055 | 2638858.0729 | 1251151.4479
55 | 2638902.3542 | 1250965.1457 | 2638902.8388 | 1250955.281
56 | 2638830.8422 | 1251163.4963 | 2638832.5439 | 1251162.1203 | 2638841.4007 | 1251156.9971 | 2638843.1549 | 1251156.2763
57 | 2638830.8422 | 1251163.4963 | 2638825.4645 | 1251167.8445 | 2638823.354 | 1251170.1414
58 | 2639539.2565 | 1250119.5016 | 2639533.131 | 1250110.9328 | 2639527.0124 | 1250101.319 | 2639525.6134 | 1250096.0283 | 2639524.7684 | 1250090.2966 | 2639524.3788 | 1250081.9218
59 | 2639467.3726 | 1250177.6729 | 2639469.7375 | 1250179.6344 | 2639471.8718 | 1250181.0718 | 2639474.1903 | 1250182.0657 | 2639476.0455 | 1250182.3449 | 2639478.288 | 1250182.2709 | 2639481.3588 | 1250181.3796 | 2639484.6327 | 1250179.4668 | 2639487.0449 | 1250177.715 | 2639490.2225 | 1250174.3895 | 2639498.7485 | 1250163.7057 | 2639504.659 | 1250155.8176 | 2639521.9032 | 1250132.806 | 2639527.3242 | 1250124.7589 | 2639529.8992 | 1250122.3745 | 2639532.4537 | 1250120.8016 | 2639535.927 | 1250119.5572 | 2639539.2565 | 1250119.5016
60 | 2639539.2565 | 1250119.5016 | 2639541.8254 | 1250120.297 | 2639543.9925 | 1250121.3566 | 2639546.1229 | 1250123.3721 | 2639547.9781 | 1250125.9195 | 2639549.2015 | 1250129.2521 | 2639549.6762 | 1250132.7688 | 2639550.0062 | 1250136.4846 | 2639549.8476 | 1250142.1651 | 2639549.2249 | 1250148.3651 | 2639548.2973 | 1250160.6893 | 2639548.2562 | 1250165.7147 | 2639548.7749 | 1250171.6999 | 2639549.5886 | 1250177.587 | 2639551.1637 | 1250185.9142 | 2639552.743 | 1250195.8536 | 2639554.3285 | 1250204.8702 | 2639555.0029 | 1250211.2901 | 2639554.874 | 1250217.0264 | 2639554.2126 | 1250221.1136 | 2639552.9158 | 1250225.3967 | 2639551.4428 | 1250228.9448 | 2639548.9461 | 1250233.1755 | 2639545.3056 | 1250237.9989 | 2639539.6325 | 1250244.2319 | 2639535.0715 | 1250250.1276 | 2639533.271 | 1250254.1072 | 2639532.6653 | 1250257.7612 | 2639533.0356 | 1250261.0992 | 2639534.3326 | 1250264.7103 | 2639536.3737 | 1250267.6703 | 2639539.9976 | 1250270.9855 | 2639548.4748 | 1250275.534 | 2639550.9792 | 1250276.9405 | 2639556.1803 | 1250267.8913
61 | 2639221.6336 | 1250143.2445 | 2639219.7654 | 1250150.6352 | 2639219.2483 | 1250152.8631
62 | 2639215.9052 | 1250167.2663 | 2639219.2483 | 1250152.8631
63 | 2639213.445 | 1250185.1609 | 2639212.7954 | 1250180.6647 | 2639215.9052 | 1250167.2663
64 | 2639235.7313 | 1250175.7575 | 2639229.5551 | 1250185.0673 | 2639225.865 | 1250188.2895 | 2639220.5543 | 1250188.8659 | 2639216.0771 | 1250187.8245 | 2639213.445 | 1250185.1609
65 | 2639235.7313 | 1250175.7575 | 2639238.28 | 1250178.4651 | 2639236.7325 | 1250194.4322 | 2639236.0465 | 1250205.6907 | 2639236.9931 | 1250217.7939 | 2639246.8329 | 1250218.8922
66 | 2639391.829 | 1250208.5804 | 2639391.998 | 1250207.0027 | 2639393.2033 | 1250205.0984 | 2639395.4979 | 1250204.0017 | 2639403.8091 | 1250202.8895 | 2639422.6374 | 1250202.6922 | 2639436.1 | 1250202.2592 | 2639443.1477 | 1250201.5723 | 2639448.6042 | 1250200.6412 | 2639453.8996 | 1250198.9531 | 2639460.7514 | 1250195.9522 | 2639466.048 | 1250192.9521 | 2639470.6159 | 1250189.4357 | 2639473.8404 | 1250185.8659 | 2639476.0455 | 1250182.3449 | 2639474.1903 | 1250182.0657 | 2639471.8718 | 1250181.0718 | 2639469.7375 | 1250179.6344 | 2639467.3726 | 1250177.6729
67 | 2639391.829 | 1250208.5804 | 2639391.2015 | 1250214.4024 | 2639386.8072 | 1250232.7077 | 2639384.3687 | 1250240.6968 | 2639380.3036 | 1250248.0859 | 2639376.5523 | 1250253.6981 | 2639371.8881 | 1250261.5168 | 2639365.8004 | 1250271.105 | 2639361.4987 | 1250278.9039 | 2639353.954 | 1250294.2085 | 2639336.0992 | 1250340.0096 | 2639330.0216 | 1250354.9349 | 2639324.3971 | 1250363.003 | 2639316.0992 | 1250370.1194 | 2639315.0153 | 1250371.6558
68 | 2639391.829 | 1250208.5804 | 2639377.4187 | 1250207.3506 | 2639360.946 | 1250212.0556 | 2639324.3868 | 1250209.7672 | 2639262.3498 | 1250205.2533 | 2639257.1869 | 1250209.7221 | 2639255.487 | 1250217.9164 | 2639250.5484 | 1250219.3068 | 2639246.8329 | 1250218.8922
69 | 2639320.0786 | 1250406.3589 | 2639317.5118 | 1250399.5707 | 2639315.3166 | 1250392.5181 | 2639312.1199 | 1250381.6786 | 2639311.9767 | 1250375.9627 | 2639315.0153 | 1250371.6558
70 | 2639556.1803 | 1250267.8913 | 2639557.5481 | 1250274.4604 | 2639564.519 | 1250283.0126
71 | 2639564.519 | 1250283.0126 | 2639870.519 | 1250320.9198
72 | 2639320.0786 | 1250406.3589 | 2639298.1182 | 1250412.2618 | 2639288.8881 | 1250414.2576 | 2639282.8258 | 1250416.2674

## bus_geodata
| x | y | coords
0 | 2638742.8662 | 1251291.6562
1 | 2638753.1491 | 1251293.6222
2 | 2638705.1121 | 1251264.5562
3 | 2638700.7989 | 1251252.3865
4 | 2638711.8644 | 1251251.1134
5 | 2638707.5261 | 1251248.5612
6 | 2638731.5655 | 1251241.8344
7 | 2639124.9232 | 1251177.0294
8 | 2639132.331 | 1251159.6442
9 | 2639118.8517 | 1251191.5545
10 | 2639109.3777 | 1251141.9479
11 | 2639108.6114 | 1251183.161
12 | 2639107.4304 | 1251140.932
13 | 2639056.7011 | 1251157.7
14 | 2638949.3119 | 1251088.3493
15 | 2638955.6043 | 1251106.501
16 | 2638948.9112 | 1251086.7104
17 | 2638939.2659 | 1251120.1904
18 | 2638985.9633 | 1251122.6186
19 | 2638938.524 | 1251036.093
20 | 2638974.8975 | 1251084.5018
21 | 2638923.9127 | 1251130.9905
22 | 2638990.3864 | 1251093.4726
23 | 2639049.9021 | 1251154.4287
24 | 2638934.4488 | 1251018.5392
25 | 2639296.3395 | 1250977.2082
26 | 2639289.1008 | 1250964.2049
27 | 2639257.6606 | 1250954.9488
28 | 2639249.2536 | 1250951.5512
29 | 2638919.6286 | 1251133.4906
30 | 2638900.7471 | 1251142.1871
31 | 2638782.323 | 1251227.6913
32 | 2638788.0775 | 1251224.8937
33 | 2638769.6769 | 1251220.9887
34 | 2638804.5933 | 1251197.7097
35 | 2638850.9267 | 1251209.5723
36 | 2638743.904 | 1251211.7962
37 | 2638851.6304 | 1251207.5945
38 | 2638853.8274 | 1251201.4193
39 | 2638809.5579 | 1251188.0095
40 | 2639204.5975 | 1250932.9027
41 | 2639033.8588 | 1251110.292
42 | 2638858.1024 | 1251151.4417
43 | 2638894.602 | 1251165.3957
44 | 2638938.0353 | 1250855.9712
45 | 2638925.0024 | 1250876.8186
46 | 2638987.5707 | 1250704.5195
47 | 2638923.1349 | 1250879.8805
48 | 2639280.3394 | 1250417.0917
49 | 2638911.7976 | 1250912.1054
50 | 2638858.0729 | 1251151.4479
51 | 2638902.8388 | 1250955.281
52 | 2638902.3542 | 1250965.1457
53 | 2639023.1783 | 1251159.4453
54 | 2638830.8422 | 1251163.4963
55 | 2638843.1549 | 1251156.2763
56 | 2638823.354 | 1251170.1414
57 | 2638800.0781 | 1251180.0094
58 | 2639524.3788 | 1250081.9218
59 | 2639539.2565 | 1250119.5016
60 | 2639221.6336 | 1250143.2445
61 | 2639219.2483 | 1250152.8631
62 | 2639213.445 | 1250185.1609
63 | 2639215.9052 | 1250167.2663
64 | 2639235.7313 | 1250175.7575
65 | 2639391.829 | 1250208.5804
66 | 2639467.3726 | 1250177.6729
67 | 2639315.0153 | 1250371.6558
68 | 2639246.8329 | 1250218.8922
69 | 2639556.1803 | 1250267.8913
70 | 2639564.519 | 1250283.0126
71 | 2639870.519 | 1250320.9198
72 | 2639282.8258 | 1250416.2674
73 | 2639320.0786 | 1250406.3589
74 | 2638948.9112 | 1251086.7104

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99174 | -0.15908 | 0.0015813 | 0.00039631
1 | 0.99169 | -0.16 | 0.0049758 | 0.0012471
2 | 0.99205 | -0.15307 | 0 | 0
3 | 0.99213 | -0.15145 | 0 | 0
4 | 0.99222 | -0.14972 | 0 | 0
5 | 0.99218 | -0.15052 | 0.0023787 | 0.00059617
6 | 0.9924 | -0.14624 | 0.0014559 | 0.00036489
7 | 0.99806 | -0.037317 | 0.00031998 | 8.0195e-05
8 | 0.99798 | -0.038753 | 0.00049967 | 0.00012523
9 | 0.99813 | -0.036032 | 0 | 0
10 | 0.99788 | -0.040865 | 0.00051452 | 0.00012895
11 | 0.99818 | -0.034951 | 0.00054922 | 0.00013765
12 | 0.99787 | -0.040993 | 0.00047841 | 0.0001199
13 | 0.99846 | -0.029673 | 0 | 0
14 | 0.99993 | -0.001365 | 0.00060057 | 0.00015052
15 | 0.99913 | -0.016745 | 0 | 0
16 | 1 | 0 | -0.058024 | -0.014191
17 | 0.99838 | -0.031063 | 0.0015827 | 0.00039667
18 | 0.99889 | -0.021287 | 0.00134 | 0.00033583
19 | 0.99958 | -0.0080938 | 0.00048361 | 0.00012121
20 | 0.99998 | -0.00037291 | 0 | 0
21 | 0.99775 | -0.043137 | 0.0019317 | 0.00048414
22 | 0.99997 | -0.00062756 | 0.0003865 | 9.6866e-05
23 | 0.99849 | -0.028951 | 0.00066748 | 0.00016729
24 | 0.99944 | -0.010768 | 0.0009639 | 0.00024158
25 | 0.99713 | -0.055272 | 0.00037033 | 9.2814e-05
26 | 0.99714 | -0.055175 | 0 | 0
27 | 0.99715 | -0.054961 | 0.00028719 | 7.1977e-05
28 | 0.99715 | -0.054857 | 0.0021798 | 0.00054631
29 | 0.99759 | -0.046163 | 0.00025275 | 6.3346e-05
30 | 0.99693 | -0.058766 | 0 | 0
31 | 0.9929 | -0.13655 | 0 | 0
32 | 0.99299 | -0.1349 | 0 | 0
33 | 0.99284 | -0.13761 | 0.0018529 | 0.00046437
34 | 0.99368 | -0.12139 | 0.0023428 | 0.00058716
35 | 0.99235 | -0.14729 | 0.0012365 | 0.00030989
36 | 0.99279 | -0.13876 | 0.002359 | 0.00059121
37 | 0.99233 | -0.1476 | 0.0075003 | 0.0018798
38 | 0.99233 | -0.14767 | 0.0006148 | 0.00015408
39 | 0.99395 | -0.11633 | 0 | 0
40 | 0.99728 | -0.052433 | 0 | 0
41 | 0.99995 | -0.00097956 | 0.00042782 | 0.00010722
42 | 0.9956 | -0.084348 | 0.0011964 | 0.00029984
43 | 0.99691 | -0.059303 | 0.0012234 | 0.00030663
44 | 0.99831 | -0.032752 | 0.0010362 | 0.00025969
45 | 0.99846 | -0.029859 | 0.00020112 | 5.0405e-05
46 | 0.99748 | -0.048843 | 0 | 0
47 | 0.99848 | -0.029425 | 0 | 0
48 | 0.99538 | -0.089751 | 0 | 0
49 | 0.9987 | -0.025255 | 0 | 0
50 | 0.9956 | -0.084365 | 0.00068387 | 0.00017139
51 | 0.99867 | -0.025725 | 0.00019275 | 4.8307e-05
52 | 0.99867 | -0.025795 | 0.00040394 | 0.00010124
53 | 0.99845 | -0.029824 | 0.00025451 | 6.3786e-05
54 | 0.99477 | -0.10037 | 0.0006965 | 0.00017456
55 | 0.99515 | -0.093077 | 0.0025262 | 0.00063314
56 | 0.99451 | -0.10536 | 0.00073505 | 0.00018422
57 | 0.99393 | -0.11659 | 0.0011851 | 0.00029702
58 | 0.99423 | -0.11217 | 0.00056355 | 0.00014124
59 | 0.99426 | -0.11176 | 0 | 0
60 | 0.99381 | -0.1203 | 0.00064461 | 0.00016155
61 | 0.99382 | -0.12019 | 0.00079846 | 0.00020011
62 | 0.99387 | -0.11911 | 0.00019468 | 4.8792e-05
63 | 0.99384 | -0.11981 | 0.00072622 | 0.00018201
64 | 0.99394 | -0.11787 | 0 | 0
65 | 0.99442 | -0.10848 | 0 | 0
66 | 0.99434 | -0.11013 | 0 | 0
67 | 0.995 | -0.097079 | 0.0017683 | 0.00044317
68 | 0.99405 | -0.11565 | 0.00026236 | 6.5753e-05
69 | 0.9942 | -0.11287 | 0 | 0
70 | 0.9942 | -0.11297 | 0.00018934 | 4.7453e-05
71 | 0.99416 | -0.1137 | 0.00012846 | 3.2195e-05
72 | 0.99537 | -0.090013 | 0.00035371 | 8.8649e-05
73 | 0.99518 | -0.093622 | 0 | 0
74 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0049761 | 0.0012471 | -0.0049758 | -0.0012471 | 2.1886e-07 | 4.9796e-09 | 0.0074661 | 0.0074662 | 0.0074662 | 0.99174 | -0.15908 | 0.99169 | -0.16 | 2.0511
1 | -0.0065573 | -0.0016434 | 0.0065592 | 0.0016439 | 1.8756e-06 | 5.3345e-07 | 0.0098387 | 0.0098385 | 0.0098387 | 0.99174 | -0.15908 | 0.99205 | -0.15307 | 2.7029
2 | -0.0065592 | -0.0016439 | 0.0065597 | 0.001644 | 5.0744e-07 | 1.4425e-07 | 0.0098385 | 0.0098384 | 0.0098385 | 0.99205 | -0.15307 | 0.99213 | -0.15145 | 2.7029
3 | -0.0065597 | -0.001644 | 0.00656 | 0.0016441 | 2.9015e-07 | 8.2465e-08 | 0.0098384 | 0.0098384 | 0.0098384 | 0.99213 | -0.15145 | 0.99218 | -0.15052 | 2.7029
4 | 0.0089391 | 0.0022404 | -0.0089387 | -0.0022403 | 3.3922e-07 | 1.5209e-07 | 0.013406 | 0.013406 | 0.013406 | 0.99222 | -0.14972 | 0.99218 | -0.15052 | 3.6829
5 | -0.0089391 | -0.0022404 | 0.0089406 | 0.0022411 | 1.4838e-06 | 6.6522e-07 | 0.013406 | 0.013406 | 0.013406 | 0.99222 | -0.14972 | 0.9924 | -0.14624 | 3.6829
6 | -0.010397 | -0.002606 | 0.010401 | 0.0026084 | 4.8037e-06 | 2.3929e-06 | 0.015589 | 0.015589 | 0.015589 | 0.9924 | -0.14624 | 0.9929 | -0.13655 | 4.2826
7 | 0.0043325 | 0.0010818 | -0.0043322 | -0.0010818 | 2.9555e-07 | -5.7792e-08 | 0.0064579 | 0.006458 | 0.006458 | 0.99806 | -0.037317 | 0.99798 | -0.038753 | 1.7742
8 | -0.0046525 | -0.001162 | 0.0046528 | 0.0011619 | 2.8393e-07 | -2.4037e-08 | 0.006935 | 0.0069349 | 0.006935 | 0.99806 | -0.037317 | 0.99813 | -0.036032 | 1.9052
9 | 0.0038325 | 0.0009566 | -0.0038321 | -0.00095676 | 3.8452e-07 | -1.6436e-07 | 0.005713 | 0.0057131 | 0.0057131 | 0.99798 | -0.038753 | 0.99788 | -0.040865 | 1.5695
10 | -0.0046528 | -0.0011619 | 0.004653 | 0.0011619 | 2.3903e-07 | -2.0261e-08 | 0.0069349 | 0.0069349 | 0.0069349 | 0.99813 | -0.036032 | 0.99818 | -0.034951 | 1.9052
11 | 0.0033176 | 0.00082781 | -0.0033176 | -0.00082783 | 2.0147e-08 | -1.5797e-08 | 0.0049459 | 0.0049459 | 0.0049459 | 0.99788 | -0.040865 | 0.99787 | -0.040993 | 1.3588
12 | -0.0052022 | -0.0012996 | 0.0052035 | 0.0012996 | 1.3049e-06 | 7.8302e-08 | 0.0077536 | 0.0077533 | 0.0077536 | 0.99818 | -0.034951 | 0.99846 | -0.029673 | 2.1301
13 | 0.0028392 | 0.00070793 | -0.0028376 | -0.00070994 | 1.5428e-06 | -2.0102e-06 | 0.0042325 | 0.0042336 | 0.0042336 | 0.99787 | -0.040993 | 0.99728 | -0.052433 | 1.1631
14 | 0.00025451 | 6.3344e-05 | -0.00025451 | -6.3786e-05 | 1.8288e-09 | -4.4234e-07 | 0.00037915 | 0.00037931 | 0.00037931 | 0.99846 | -0.029673 | 0.99845 | -0.029824 | 0.1042
15 | -0.005458 | -0.001363 | 0.0054582 | 0.001363 | 1.8713e-07 | 2.1078e-08 | 0.0081325 | 0.0081325 | 0.0081325 | 0.99846 | -0.029673 | 0.99849 | -0.028951 | 2.2342
16 | 0.046013 | 0.01161 | -0.045979 | -0.011588 | 3.3859e-05 | 2.1418e-05 | 0.0685 | 0.0685 | 0.0685 | 0.99993 | -0.001365 | 0.99913 | -0.016745 | 18.8187
17 | -0.046613 | -0.01176 | 0.046616 | 0.011762 | 3.0467e-06 | 1.9278e-06 | 0.069394 | 0.069394 | 0.069394 | 0.99993 | -0.001365 | 1 | 0 | 19.0642
18 | 0.038509 | 0.0097211 | -0.038483 | -0.0097045 | 2.6394e-05 | 1.6612e-05 | 0.057377 | 0.057377 | 0.057377 | 0.99913 | -0.016745 | 0.99838 | -0.031063 | 15.763
19 | 0.0074695 | 0.0018672 | -0.0074679 | -0.0018666 | 1.6131e-06 | 5.7713e-07 | 0.011123 | 0.011123 | 0.011123 | 0.99913 | -0.016745 | 0.99889 | -0.021287 | 3.0558
20 | 0.0089437 | 0.0022259 | -0.0089403 | -0.0022244 | 3.4293e-06 | 1.5171e-06 | 0.013303 | 0.013303 | 0.013303 | 1 | 0 | 0.99958 | -0.0080938 | 3.6547
21 | 0.00081435 | 0.00020291 | -0.00081434 | -0.00020325 | 1.4412e-08 | -3.3435e-07 | 0.0012114 | 0.0012115 | 0.0012115 | 1 | 0 | 0.99998 | -0.00037291 | 0.33282
22 | 0.0369 | 0.0093078 | -0.036879 | -0.0092944 | 2.1317e-05 | 1.3397e-05 | 0.055018 | 0.055018 | 0.055018 | 0.99838 | -0.031063 | 0.99775 | -0.043137 | 15.1149
23 | 0.0061279 | 0.0015308 | -0.0061257 | -0.0015303 | 2.2314e-06 | 4.9341e-07 | 0.0091268 | 0.0091272 | 0.0091272 | 0.99889 | -0.021287 | 0.99849 | -0.028951 | 2.5075
24 | 0.0084566 | 0.0021032 | -0.0084556 | -0.0021027 | 1.0708e-06 | 4.4896e-07 | 0.012583 | 0.012583 | 0.012583 | 0.99958 | -0.0080938 | 0.99944 | -0.010768 | 3.4569
25 | 0.00081434 | 0.00020325 | -0.00081433 | -0.00020348 | 9.852e-09 | -2.2851e-07 | 0.0012115 | 0.0012116 | 0.0012116 | 0.99998 | -0.00037291 | 0.99997 | -0.00062756 | 0.33285
26 | 0.034947 | 0.0088103 | -0.034942 | -0.0088071 | 5.0588e-06 | 3.1728e-06 | 0.052137 | 0.052137 | 0.052137 | 0.99775 | -0.043137 | 0.99759 | -0.046163 | 14.3235
27 | 0.00042783 | 0.00010661 | -0.00042782 | -0.00010722 | 7.1585e-09 | -6.1347e-07 | 0.00063642 | 0.00063664 | 0.00063664 | 0.99997 | -0.00062756 | 0.99995 | -0.00097956 | 0.1749
28 | 0.0074917 | 0.0018612 | -0.0074865 | -0.0018593 | 5.1337e-06 | 1.8432e-06 | 0.011148 | 0.011149 | 0.011149 | 0.99944 | -0.010768 | 0.9987 | -0.025255 | 3.0628
29 | -0.00037033 | -9.2814e-05 | 0.00037033 | 9.262e-05 | 1.7112e-09 | -1.9382e-07 | 0.00055265 | 0.00055258 | 0.00055265 | 0.99713 | -0.055272 | 0.99714 | -0.055175 | 0.15183
30 | -0.00037033 | -9.262e-05 | 0.00037034 | 9.2195e-05 | 3.7528e-09 | -4.2523e-07 | 0.00055258 | 0.00055243 | 0.00055258 | 0.99714 | -0.055175 | 0.99715 | -0.054961 | 0.15181
31 | -0.00065753 | -0.00016417 | 0.00065753 | 0.00016406 | 3.2726e-09 | -1.162e-07 | 0.000981 | 0.00098095 | 0.000981 | 0.99715 | -0.054961 | 0.99715 | -0.054857 | 0.2695
32 | -0.0028373 | -0.00071036 | 0.0028376 | 0.00070994 | 3.2733e-07 | -4.2585e-07 | 0.0042338 | 0.0042336 | 0.0042338 | 0.99715 | -0.054857 | 0.99728 | -0.052433 | 1.1631
33 | 0.034689 | 0.0087437 | -0.034668 | -0.0087306 | 2.0905e-05 | 1.3108e-05 | 0.05176 | 0.051761 | 0.051761 | 0.99759 | -0.046163 | 0.99693 | -0.058766 | 14.2199
34 | 0.033445 | 0.0084243 | -0.033404 | -0.0083987 | 4.0864e-05 | 2.5584e-05 | 0.049935 | 0.049935 | 0.049935 | 0.99693 | -0.058766 | 0.9956 | -0.084348 | 13.7183
35 | 0.0012235 | 0.00030632 | -0.0012234 | -0.00030662 | 3.1298e-08 | -3.063e-07 | 0.001826 | 0.0018262 | 0.0018262 | 0.99693 | -0.058766 | 0.99691 | -0.059303 | 0.50169
36 | -0.014613 | -0.0036637 | 0.014615 | 0.0036643 | 1.1481e-06 | 6.5223e-07 | 0.021901 | 0.021901 | 0.021901 | 0.9929 | -0.13655 | 0.99299 | -0.1349 | 6.0168
37 | 0.0042122 | 0.0010553 | -0.004212 | -0.0010553 | 2.1448e-07 | -4.8363e-08 | 0.0063125 | 0.0063125 | 0.0063125 | 0.9929 | -0.13655 | 0.99284 | -0.13761 | 1.7342
38 | -0.023972 | -0.0060106 | 0.023987 | 0.00602 | 1.5435e-05 | 9.4656e-06 | 0.035924 | 0.035923 | 0.035924 | 0.99299 | -0.1349 | 0.99368 | -0.12139 | 9.8691
39 | 0.0093573 | 0.0023463 | -0.0093517 | -0.0023437 | 5.5259e-06 | 2.5678e-06 | 0.014023 | 0.014023 | 0.014023 | 0.99299 | -0.1349 | 0.99235 | -0.14729 | 3.8524
40 | 0.0023591 | 0.00059094 | -0.002359 | -0.00059121 | 1.2831e-07 | -2.7183e-07 | 0.0035356 | 0.0035357 | 0.0035357 | 0.99284 | -0.13761 | 0.99279 | -0.13876 | 0.97135
41 | -0.02633 | -0.0066072 | 0.026336 | 0.0066111 | 6.3606e-06 | 3.9294e-06 | 0.039432 | 0.039432 | 0.039432 | 0.99368 | -0.12139 | 0.99395 | -0.11633 | 10.8329
42 | 0.0081153 | 0.0020338 | -0.0081151 | -0.0020338 | 1.1657e-07 | 4.7486e-08 | 0.012169 | 0.012169 | 0.012169 | 0.99235 | -0.14729 | 0.99233 | -0.1476 | 3.3431
43 | 0.0006148 | 0.000154 | -0.0006148 | -0.00015408 | 2.0889e-09 | -8.3337e-08 | 0.00092187 | 0.0009219 | 0.0009219 | 0.99233 | -0.1476 | 0.99233 | -0.14767 | 0.25327
44 | 0.0011851 | 0.00029687 | -0.0011851 | -0.00029702 | 1.4646e-08 | -1.5143e-07 | 0.0017742 | 0.0017742 | 0.0017742 | 0.99395 | -0.11633 | 0.99393 | -0.11659 | 0.48743
45 | -0.027522 | -0.006908 | 0.027536 | 0.0069169 | 1.4408e-05 | 8.9275e-06 | 0.041206 | 0.041206 | 0.041206 | 0.99395 | -0.11633 | 0.99451 | -0.10536 | 11.3203
46 | 0.032208 | 0.0080989 | -0.032208 | -0.0080989 | 2.6216e-08 | 1.6387e-08 | 0.048147 | 0.048147 | 0.048147 | 0.9956 | -0.084348 | 0.9956 | -0.084365 | 13.2271
47 | -0.0066863 | -0.0016593 | 0.0066872 | 0.0016596 | 9.1472e-07 | 2.639e-07 | 0.0099604 | 0.0099603 | 0.0099604 | 0.99831 | -0.032752 | 0.99846 | -0.029859 | 2.7364
48 | 0.0056501 | 0.0013997 | -0.0056458 | -0.001399 | 4.2921e-06 | 6.3602e-07 | 0.008416 | 0.0084167 | 0.0084167 | 0.99831 | -0.032752 | 0.99748 | -0.048843 | 2.3123
49 | -0.0068883 | -0.00171 | 0.0068885 | 0.0017101 | 1.4158e-07 | 4.3702e-08 | 0.01026 | 0.01026 | 0.01026 | 0.99846 | -0.029859 | 0.99848 | -0.029425 | 2.8187
50 | 0.0056458 | 0.001399 | -0.0056349 | -0.0013974 | 1.0902e-05 | 1.6328e-06 | 0.0084167 | 0.0084186 | 0.0084186 | 0.99748 | -0.048843 | 0.99538 | -0.089751 | 2.3128
51 | -0.0068885 | -0.0017101 | 0.0068898 | 0.0017105 | 1.3588e-06 | 4.1933e-07 | 0.01026 | 0.01026 | 0.01026 | 0.99848 | -0.029425 | 0.9987 | -0.025255 | 2.8187
52 | 0.0056349 | 0.0013974 | -0.0056349 | -0.0013974 | 6.9619e-08 | 1.0507e-08 | 0.0084186 | 0.0084186 | 0.0084186 | 0.99538 | -0.089751 | 0.99537 | -0.090013 | 2.3128
53 | 0.0005967 | 0.00014883 | -0.00059669 | -0.00014942 | 1.3358e-08 | -5.8131e-07 | 0.00088881 | 0.00088902 | 0.00088902 | 0.9987 | -0.025255 | 0.99867 | -0.025725 | 0.24424
54 | 0.031524 | 0.0079275 | -0.031511 | -0.0079193 | 1.3111e-05 | 8.1866e-06 | 0.047125 | 0.047125 | 0.047125 | 0.9956 | -0.084365 | 0.99515 | -0.093077 | 12.9463
55 | 0.00040394 | 0.00010111 | -0.00040394 | -0.00010124 | 1.3416e-09 | -1.2837e-07 | 0.00060182 | 0.00060187 | 0.00060187 | 0.99867 | -0.025725 | 0.99867 | -0.025795 | 0.16535
56 | -0.028974 | -0.0072799 | 0.028984 | 0.0072862 | 1.0088e-05 | 6.2703e-06 | 0.043347 | 0.043347 | 0.043347 | 0.99477 | -0.10037 | 0.99515 | -0.093077 | 11.9086
57 | 0.028278 | 0.0071053 | -0.028271 | -0.0071012 | 6.735e-06 | 4.1801e-06 | 0.042305 | 0.042305 | 0.042305 | 0.99477 | -0.10037 | 0.99451 | -0.10536 | 11.6224
58 | -0.00056355 | -0.00014124 | 0.00056357 | 0.00014071 | 1.109e-08 | -5.3213e-07 | 0.00084344 | 0.00084325 | 0.00084344 | 0.99423 | -0.11217 | 0.99426 | -0.11176 | 0.23171
59 | -0.00088139 | -0.00021369 | 0.00088145 | 0.0002124 | 6.6521e-08 | -1.2852e-06 | 0.0013166 | 0.0013161 | 0.0013166 | 0.99426 | -0.11176 | 0.99434 | -0.11013 | 0.3617
60 | 0.00031782 | 7.2981e-05 | -0.00031781 | -7.5424e-05 | 1.5923e-08 | -2.4428e-06 | 0.00047339 | 0.0004742 | 0.0004742 | 0.99426 | -0.11176 | 0.9942 | -0.11287 | 0.13028
61 | -0.00064461 | -0.00016155 | 0.00064461 | 0.00016143 | 3.4617e-09 | -1.262e-07 | 0.00096516 | 0.00096512 | 0.00096516 | 0.99381 | -0.1203 | 0.99382 | -0.12019 | 0.26515
62 | -0.0014431 | -0.00036154 | 0.0014431 | 0.00036137 | 2.5884e-08 | -1.7503e-07 | 0.0021606 | 0.0021606 | 0.0021606 | 0.99382 | -0.12019 | 0.99384 | -0.11981 | 0.59358
63 | 0.0021694 | 0.00054318 | -0.0021693 | -0.00054337 | 7.238e-08 | -1.9079e-07 | 0.0032478 | 0.0032479 | 0.0032479 | 0.99387 | -0.11911 | 0.99384 | -0.11981 | 0.89228
64 | -0.0023641 | -0.00059198 | 0.0023642 | 0.00059168 | 1.3977e-07 | -2.9616e-07 | 0.0035393 | 0.0035392 | 0.0035393 | 0.99387 | -0.11911 | 0.99394 | -0.11787 | 0.97233
65 | -0.0023642 | -0.00059168 | 0.0023645 | 0.00059115 | 2.4931e-07 | -5.2848e-07 | 0.0035392 | 0.0035389 | 0.0035392 | 0.99394 | -0.11787 | 0.99405 | -0.11565 | 0.9723
66 | 0.00088152 | 0.0002111 | -0.00088145 | -0.0002124 | 6.7263e-08 | -1.3007e-06 | 0.0013157 | 0.0013161 | 0.0013161 | 0.99442 | -0.10848 | 0.99434 | -0.11013 | 0.36158
67 | -0.0035092 | -0.00086658 | 0.0035111 | 0.00086541 | 1.8843e-06 | -1.164e-06 | 0.0052466 | 0.0052458 | 0.0052466 | 0.99442 | -0.10848 | 0.995 | -0.097079 | 1.4414
68 | 0.0026277 | 0.00065547 | -0.0026268 | -0.0006569 | 8.9538e-07 | -1.4305e-06 | 0.0039309 | 0.0039316 | 0.0039316 | 0.99442 | -0.10848 | 0.99405 | -0.11565 | 1.0801
69 | -0.0052794 | -0.0013086 | 0.0052802 | 0.0013087 | 8.6221e-07 | 7.2017e-08 | 0.0078901 | 0.00789 | 0.0078901 | 0.995 | -0.097079 | 0.99518 | -0.093622 | 2.1676
70 | 0.00031781 | 7.5424e-05 | -0.0003178 | -7.5653e-05 | 1.4954e-09 | -2.2897e-07 | 0.0004742 | 0.00047428 | 0.00047428 | 0.9942 | -0.11287 | 0.9942 | -0.11297 | 0.1303
71 | 0.00012847 | 2.82e-05 | -0.00012846 | -3.2195e-05 | 4.2443e-09 | -3.9955e-06 | 0.00019095 | 0.00019228 | 0.00019228 | 0.9942 | -0.11297 | 0.99416 | -0.1137 | 0.052823
72 | 0.0052811 | 0.0013087 | -0.0052802 | -0.0013087 | 9.0038e-07 | 7.5e-08 | 0.0078898 | 0.00789 | 0.00789 | 0.99537 | -0.090013 | 0.99518 | -0.093622 | 2.1676

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.058024 | 0.014191

## res_load
| p_mw | q_mvar
0 | 0.0015813 | 0.00039631
1 | 0.0049758 | 0.0012471
2 | 0.0023787 | 0.00059617
3 | 0.0014559 | 0.00036489
4 | 0.00031998 | 8.0195e-05
5 | 0.00049967 | 0.00012523
6 | 0.00051452 | 0.00012895
7 | 0.00054922 | 0.00013765
8 | 0.00047841 | 0.0001199
9 | 0.00060057 | 0.00015052
10 | 0.0015827 | 0.00039667
11 | 0.00134 | 0.00033583
12 | 0.00048361 | 0.00012121
13 | 0.0019317 | 0.00048414
14 | 0.0003865 | 9.6866e-05
15 | 0.00066748 | 0.00016729
16 | 0.0009639 | 0.00024158
17 | 0.00037033 | 9.2814e-05
18 | 0.00028719 | 7.1977e-05
19 | 0.0021798 | 0.00054631
20 | 0.00025275 | 6.3346e-05
21 | 0.0018529 | 0.00046437
22 | 0.0023428 | 0.00058716
23 | 0.0012365 | 0.00030989
24 | 0.002359 | 0.00059121
25 | 0.0075003 | 0.0018798
26 | 0.0006148 | 0.00015408
27 | 0.00042782 | 0.00010722
28 | 0.0011964 | 0.00029984
29 | 0.0012234 | 0.00030663
30 | 0.0010362 | 0.00025969
31 | 0.00020112 | 5.0405e-05
32 | 0.00068387 | 0.00017139
33 | 0.00019275 | 4.8307e-05
34 | 0.00040394 | 0.00010124
35 | 0.00025451 | 6.3786e-05
36 | 0.0006965 | 0.00017456
37 | 0.0025262 | 0.00063314
38 | 0.00073505 | 0.00018422
39 | 0.0011851 | 0.00029702
40 | 0.00056355 | 0.00014124
41 | 0.00064461 | 0.00016155
42 | 0.00079846 | 0.00020011
43 | 0.00019468 | 4.8792e-05
44 | 0.00072622 | 0.00018201
45 | 0.0017683 | 0.00044317
46 | 0.00026236 | 6.5753e-05
47 | 0.00018934 | 4.7453e-05
48 | 0.00012846 | 3.2195e-05
49 | 0.00035371 | 8.8649e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1