## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_25-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_25-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_25-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_25-1_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_25-1_0_3_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_25-1_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_25-1_0_3_node_44 | 0.4 | n |  | TRUE
7 | bus_LV_25-1_0_3_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_25-1_0_3_node_43 | 0.4 | n |  | TRUE
9 | bus_LV_25-1_0_3_node_42 | 0.4 | n |  | TRUE
10 | bus_LV_25-1_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_25-1_0_3_node_114 | 0.4 | n |  | TRUE
12 | bus_LV_25-1_0_3_node_132 | 0.4 | n |  | TRUE
13 | bus_LV_25-1_0_3_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_25-1_0_3_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_25-1_0_3_node_239 | 0.4 | n |  | TRUE
16 | bus_LV_25-1_0_3_node_50 | 0.4 | n |  | TRUE
17 | bus_LV_25-1_0_3_node_81 | 0.4 | n |  | TRUE
18 | bus_LV_25-1_0_3_node_84 | 0.4 | n |  | TRUE
19 | bus_LV_25-1_0_3_node_51 | 0.4 | n |  | TRUE
20 | bus_LV_25-1_0_3_node_154 | 0.4 | n |  | TRUE
21 | bus_LV_25-1_0_3_node_155 | 0.4 | n |  | TRUE
22 | bus_LV_25-1_0_3_node_57 | 0.4 | n |  | TRUE
23 | bus_LV_25-1_0_3_node_151 | 0.4 | n |  | TRUE
24 | bus_LV_25-1_0_3_node_149 | 0.4 | n |  | TRUE
25 | bus_LV_25-1_0_3_node_115 | 0.4 | n |  | TRUE
26 | bus_LV_25-1_0_3_node_113 | 0.4 | n |  | TRUE
27 | bus_LV_25-1_0_3_node_41 | 0.4 | n |  | TRUE
28 | bus_LV_25-1_0_3_node_36 | 0.4 | n |  | TRUE
29 | bus_LV_25-1_0_3_node_8 | 0.4 | n |  | TRUE
30 | bus_LV_25-1_0_3_node_9 | 0.4 | n |  | TRUE
31 | bus_LV_25-1_0_3_node_10 | 0.4 | n |  | TRUE
32 | bus_LV_25-1_0_3_node_12 | 0.4 | n |  | TRUE
33 | bus_LV_25-1_0_3_node_90 | 0.4 | n |  | TRUE
34 | bus_LV_25-1_0_3_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_25-1_0_3_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_25-1_0_3_node_14 | 0.4 | n |  | TRUE
37 | bus_LV_25-1_0_3_node_89 | 0.4 | n |  | TRUE
38 | bus_LV_25-1_0_3_node_13 | 0.4 | n |  | TRUE
39 | bus_LV_25-1_0_3_node_15 | 0.4 | n |  | TRUE
40 | bus_LV_25-1_0_3_node_17 | 0.4 | n |  | TRUE
41 | bus_LV_25-1_0_3_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_25-1_0_3_node_19 | 0.4 | n |  | TRUE
43 | bus_LV_25-1_0_3_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_25-1_0_3_node_20 | 0.4 | n |  | TRUE
45 | bus_LV_25-1_0_3_node_21 | 0.4 | n |  | TRUE
46 | bus_LV_25-1_0_3_node_22 | 0.4 | n |  | TRUE
47 | bus_LV_25-1_0_3_node_148 | 0.4 | n |  | TRUE
48 | bus_LV_25-1_0_3_node_23 | 0.4 | n |  | TRUE
49 | bus_LV_25-1_0_3_node_134 | 0.4 | n |  | TRUE
50 | bus_LV_25-1_0_3_node_145 | 0.4 | n |  | TRUE
51 | bus_LV_25-1_0_3_node_147 | 0.4 | n |  | TRUE
52 | bus_LV_25-1_0_3_node_24 | 0.4 | n |  | TRUE
53 | bus_LV_25-1_0_3_node_27 | 0.4 | n |  | TRUE
54 | bus_LV_25-1_0_3_node_28 | 0.4 | n |  | TRUE
55 | bus_LV_25-1_0_3_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_25-1_0_3_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_25-1_0_3_node_32 | 0.4 | n |  | TRUE
58 | bus_LV_25-1_0_3_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_25-1_0_3_node_33 | 0.4 | n |  | TRUE
60 | bus_LV_25-1_0_3_node_91 | 0.4 | n |  | TRUE
61 | bus_LV_25-1_0_3_node_88 | 0.4 | n |  | TRUE
62 | bus_LV_25-1_0_3_node_92 | 0.4 | n |  | TRUE
63 | bus_LV_25-1_0_3_node_86 | 0.4 | n |  | TRUE
64 | bus_LV_25-1_0_3_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_25-1_0_3_node_38 | 0.4 | n |  | TRUE
66 | bus_LV_25-1_0_3_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_25-1_0_3_node_238 | 0.4 | n |  | TRUE
68 | bus_LV_25-1_0_3_node_231 | 0.4 | n |  | TRUE
69 | bus_LV_25-1_0_3_node_232 | 0.4 | n |  | TRUE
70 | bus_LV_25-1_0_3_node_94 | 0.4 | n |  | TRUE
71 | bus_LV_25-1_0_3_node_95 | 0.4 | n |  | TRUE
72 | bus_LV_25-1_0_3_node_153 | 0.4 | n |  | TRUE
73 | bus_LV_25-1_0_3_node_152 | 0.4 | n |  | TRUE
74 | bus_LV_25-1_0_3_node_80 | 0.4 | n |  | TRUE
75 | bus_LV_25-1_0_3_node_83 | 0.4 | n |  | TRUE
76 | bus_LV_25-1_0_3_node_75 | 0.4 | n |  | TRUE
77 | bus_LV_25-1_0_3_node_73 | 0.4 | n |  | TRUE
78 | bus_LV_25-1_0_3_node_82 | 0.4 | n |  | TRUE
79 | bus_LV_25-1_0_3_node_150 | 0.4 | n |  | TRUE
80 | bus_LV_25-1_0_3_node_133 | 0.4 | n |  | TRUE
81 | bus_LV_25-1_0_3_node_117 | 0.4 | n |  | TRUE
82 | bus_LV_25-1_0_3_node_67 | 0.4 | n |  | TRUE
83 | bus_LV_25-1_0_3_node_68 | 0.4 | n |  | TRUE
84 | bus_LV_25-1_0_3_node_69 | 0.4 | n |  | TRUE
85 | bus_LV_25-1_0_3_node_70 | 0.4 | n |  | TRUE
86 | bus_LV_25-1_0_3_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_25-1_0_3_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_25-1_0_3_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_25-1_0_3_node_111 | 0.4 | n |  | TRUE
90 | bus_LV_25-1_0_3_node_104 | 0.4 | n |  | TRUE
91 | bus_LV_25-1_0_3_node_105 | 0.4 | n |  | TRUE
92 | bus_LV_25-1_0_3_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_25-1_0_3_node_77 | 0.4 | n |  | TRUE
94 | bus_LV_25-1_0_3_node_78 | 0.4 | n |  | TRUE
95 | bus_LV_25-1_0_3_node_79 | 0.4 | n |  | TRUE
96 | bus_LV_25-1_0_3_node_85 | 0.4 | n |  | TRUE
97 | bus_LV_25-1_0_3_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_25-1_0_3_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_25-1_0_3_node_252 | 0.4 | n |  | TRUE
100 | bus_LV_25-1_0_3_node_103 | 0.4 | n |  | TRUE
101 | bus_LV_25-1_0_3_node_96 | 0.4 | n |  | TRUE
102 | bus_LV_25-1_0_3_node_98 | 0.4 | n |  | TRUE
103 | bus_LV_25-1_0_3_node_99 | 0.4 | n |  | TRUE
104 | bus_LV_25-1_0_3_node_234 | 0.4 | n |  | TRUE
105 | bus_LV_25-1_0_3_node_101 | 0.4 | n |  | TRUE
106 | bus_LV_25-1_0_3_node_100 | 0.4 | n |  | TRUE
107 | bus_LV_25-1_0_3_node_235 | 0.4 | n |  | TRUE
108 | bus_LV_25-1_0_3_node_102 | 0.4 | n |  | TRUE
109 | bus_LV_25-1_0_3_node_237 | 0.4 | n |  | TRUE
110 | bus_LV_25-1_0_3_node_236 | 0.4 | n |  | TRUE
111 | bus_LV_25-1_0_3_node_106 | 0.4 | n |  | TRUE
112 | bus_LV_25-1_0_3_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_25-1_0_3_node_108 | 0.4 | n |  | TRUE
114 | bus_LV_25-1_0_3_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_25-1_0_3_node_110 | 0.4 | n |  | TRUE
116 | bus_LV_25-1_0_3_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_25-1_0_3_node_116 | 0.4 | n |  | TRUE
118 | bus_LV_25-1_0_3_node_118 | 0.4 | n |  | TRUE
119 | bus_LV_25-1_0_3_node_119 | 0.4 | n |  | TRUE
120 | bus_LV_25-1_0_3_node_124 | 0.4 | n |  | TRUE
121 | bus_LV_25-1_0_3_node_135 | 0.4 | n |  | TRUE
122 | bus_LV_25-1_0_3_node_127 | 0.4 | n |  | TRUE
123 | bus_LV_25-1_0_3_node_123 | 0.4 | n |  | TRUE
124 | bus_LV_25-1_0_3_node_136 | 0.4 | n |  | TRUE
125 | bus_LV_25-1_0_3_node_128 | 0.4 | n |  | TRUE
126 | bus_LV_25-1_0_3_node_126 | 0.4 | n |  | TRUE
127 | bus_LV_25-1_0_3_node_120 | 0.4 | n |  | TRUE
128 | bus_LV_25-1_0_3_node_121 | 0.4 | n |  | TRUE
129 | bus_LV_25-1_0_3_node_122 | 0.4 | n |  | TRUE
130 | bus_LV_25-1_0_3_node_125 | 0.4 | n |  | TRUE
131 | bus_LV_25-1_0_3_node_131 | 0.4 | n |  | TRUE
132 | bus_LV_25-1_0_3_node_130 | 0.4 | n |  | TRUE
133 | bus_LV_25-1_0_3_node_129 | 0.4 | n |  | TRUE
134 | bus_LV_25-1_0_3_node_142 | 0.4 | n |  | TRUE
135 | bus_LV_25-1_0_3_node_144 | 0.4 | n |  | TRUE
136 | bus_LV_25-1_0_3_node_139 | 0.4 | n |  | TRUE
137 | bus_LV_25-1_0_3_node_137 | 0.4 | n |  | TRUE
138 | bus_LV_25-1_0_3_node_140 | 0.4 | n |  | TRUE
139 | bus_LV_25-1_0_3_node_138 | 0.4 | n |  | TRUE
140 | bus_LV_25-1_0_3_node_141 | 0.4 | n |  | TRUE
141 | bus_LV_25-1_0_3_node_143 | 0.4 | n |  | TRUE
142 | bus_LV_25-1_0_3_node_146 | 0.4 | n |  | TRUE
143 | bus_LV_25-1_0_3_node_233 | 0.4 | n |  | TRUE
144 | bus_MV_391_0_node_183 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_25-1_0_3_load_0 | 0 | 0.0030267 | 0.00075857 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_25-1_0_3_load_44 | 6 | 0.0021514 | 0.00053919 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_25-1_0_3_load_43 | 8 | 0.0025067 | 0.00062824 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_25-1_0_3_load_42 | 9 | 0.0020522 | 0.00051433 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_25-1_0_3_load_132 | 12 | 0.0029406 | 0.00073699 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_25-1_0_3_load_35 | 13 | 0.0052016 | 0.0013036 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_25-1_0_3_load_29 | 14 | 0.0067226 | 0.0016848 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_25-1_0_3_load_239 | 15 | 0.00090802 | 0.00022757 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_25-1_0_3_load_84 | 18 | 0.001534 | 0.00038446 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_25-1_0_3_load_154 | 20 | 0.0016364 | 0.00041011 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_25-1_0_3_load_155 | 21 | 0.0018667 | 0.00046784 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_25-1_0_3_load_151 | 23 | 0.0016239 | 0.00040699 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_25-1_0_3_load_149 | 24 | 0.0016571 | 0.00041532 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_25-1_0_3_load_115 | 25 | 0.0014177 | 0.00035532 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_25-1_0_3_load_36 | 28 | 0.0013837 | 0.00034679 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_25-1_0_3_load_8 | 29 | 0.00095371 | 0.00023902 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_25-1_0_3_load_9 | 30 | 0.0018149 | 0.00045486 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_25-1_0_3_load_10 | 31 | 0.00083187 | 0.00020849 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_25-1_0_3_load_12 | 32 | 0.00060514 | 0.00015166 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_25-1_0_3_load_90 | 33 | 0.0011748 | 0.00029442 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_25-1_0_3_load_18 | 35 | 0.0074102 | 0.0018572 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_25-1_0_3_load_14 | 36 | 0.0019144 | 0.0004798 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_25-1_0_3_load_89 | 37 | 0.00021894 | 5.4871e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_25-1_0_3_load_13 | 38 | 0.001055 | 0.00026441 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_25-1_0_3_load_15 | 39 | 0.0016209 | 0.00040623 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_25-1_0_3_load_17 | 40 | 0.0012358 | 0.00030972 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_25-1_0_3_load_25 | 41 | 0.0015753 | 0.00039481 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_25-1_0_3_load_26 | 43 | 0.001557 | 0.00039022 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_25-1_0_3_load_20 | 44 | 0.00038428 | 9.6309e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_25-1_0_3_load_22 | 46 | 0.0027081 | 0.00067872 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_25-1_0_3_load_148 | 47 | 0.00059613 | 0.0001494 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_25-1_0_3_load_23 | 48 | 0.00079886 | 0.00020021 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_25-1_0_3_load_147 | 51 | 0.00099067 | 0.00024829 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_25-1_0_3_load_24 | 52 | 0.0028024 | 0.00070234 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_25-1_0_3_load_27 | 53 | 0.001479 | 0.00037067 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_25-1_0_3_load_28 | 54 | 0.000227 | 5.6892e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_25-1_0_3_load_30 | 55 | 0.0015911 | 0.00039877 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_25-1_0_3_load_31 | 56 | 0.00026625 | 6.6729e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_25-1_0_3_load_88 | 61 | 0.0002299 | 5.7618e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_25-1_0_3_load_92 | 62 | 0.00052832 | 0.00013241 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_25-1_0_3_load_86 | 63 | 0.00062154 | 0.00015577 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_25-1_0_3_load_37 | 64 | 0.0047654 | 0.0011943 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_25-1_0_3_load_38 | 65 | 0.0061352 | 0.0015376 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_25-1_0_3_load_238 | 67 | 0.0027982 | 0.0007013 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_25-1_0_3_load_231 | 68 | 0.004176 | 0.0010466 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_25-1_0_3_load_232 | 69 | 0.001593 | 0.00039925 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_25-1_0_3_load_94 | 70 | 0.081808 | 0.020503 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_25-1_0_3_load_153 | 72 | 0.00075072 | 0.00018815 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_25-1_0_3_load_83 | 75 | 0.0011874 | 0.00029759 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_25-1_0_3_load_75 | 76 | 0.0019195 | 0.00048108 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_25-1_0_3_load_73 | 77 | 0.0017951 | 0.00044991 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_25-1_0_3_load_82 | 78 | 0.0011947 | 0.00029941 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_25-1_0_3_load_133 | 80 | 0.001337 | 0.00033509 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_25-1_0_3_load_67 | 82 | 0.0015762 | 0.00039504 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_25-1_0_3_load_68 | 83 | 0.0026422 | 0.00066221 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_25-1_0_3_load_69 | 84 | 0.0013662 | 0.0003424 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_25-1_0_3_load_70 | 85 | 0.0018625 | 0.00046679 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_25-1_0_3_load_71 | 86 | 0.00346 | 0.00086717 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_25-1_0_3_load_74 | 88 | 0.0034287 | 0.00085932 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_25-1_0_3_load_111 | 89 | 0.0013616 | 0.00034126 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_25-1_0_3_load_104 | 90 | 0.0048541 | 0.0012165 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_25-1_0_3_load_76 | 92 | 0.0011557 | 0.00028966 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_25-1_0_3_load_77 | 93 | 0.00072022 | 0.00018051 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_25-1_0_3_load_78 | 94 | 0.0017522 | 0.00043915 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_25-1_0_3_load_79 | 95 | 0.00065604 | 0.00016442 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_25-1_0_3_load_93 | 98 | 0.0024918 | 0.0006245 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_25-1_0_3_load_252 | 99 | 0.0011143 | 0.00027926 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_25-1_0_3_load_98 | 102 | 0.023344 | 0.0058506 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_25-1_0_3_load_234 | 104 | 0.0032964 | 0.00082616 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_25-1_0_3_load_100 | 106 | 0.0057116 | 0.0014315 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_25-1_0_3_load_235 | 107 | 0.0025359 | 0.00063555 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_25-1_0_3_load_237 | 109 | 0.0055481 | 0.0013905 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_25-1_0_3_load_236 | 110 | 0.0022379 | 0.00056088 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_25-1_0_3_load_106 | 111 | 0.0018502 | 0.00046371 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_25-1_0_3_load_107 | 112 | 0.0013235 | 0.0003317 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_25-1_0_3_load_108 | 113 | 0.001669 | 0.00041829 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_25-1_0_3_load_109 | 114 | 0.0012414 | 0.00031113 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_25-1_0_3_load_110 | 115 | 0.0013614 | 0.00034119 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_25-1_0_3_load_112 | 116 | 0.0012431 | 0.00031155 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_25-1_0_3_load_118 | 118 | 0.0013968 | 0.00035008 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_25-1_0_3_load_119 | 119 | 0.0015181 | 0.00038047 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_25-1_0_3_load_124 | 120 | 0.0032504 | 0.00081463 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_25-1_0_3_load_135 | 121 | 0.0010219 | 0.00025611 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_25-1_0_3_load_123 | 123 | 0.0020958 | 0.00052527 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_25-1_0_3_load_128 | 125 | 0.00051883 | 0.00013003 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_25-1_0_3_load_126 | 126 | 0.0021634 | 0.0005422 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_25-1_0_3_load_120 | 127 | 0.0020897 | 0.00052372 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_25-1_0_3_load_121 | 128 | 0.0017895 | 0.0004485 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_25-1_0_3_load_122 | 129 | 0.001982 | 0.00049674 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_25-1_0_3_load_125 | 130 | 0.0021324 | 0.00053443 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_25-1_0_3_load_130 | 132 | 0.0024434 | 0.00061237 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_25-1_0_3_load_129 | 133 | 0.0025749 | 0.00064533 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_25-1_0_3_load_142 | 134 | 0.00099741 | 0.00024997 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_25-1_0_3_load_144 | 135 | 0.00070056 | 0.00017558 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_25-1_0_3_load_139 | 136 | 0.0009664 | 0.0002422 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_25-1_0_3_load_137 | 137 | 0.00070456 | 0.00017658 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_25-1_0_3_load_140 | 138 | 0.00072535 | 0.00018179 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_25-1_0_3_load_138 | 139 | 0.00060772 | 0.00015231 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_25-1_0_3_load_143 | 141 | 0.00072758 | 0.00018235 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_25-1_0_3_load_146 | 142 | 0.00077399 | 0.00019398 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_25-1_0_3_load_233 | 143 | 0.0013441 | 0.00033686 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 100 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_25-1_0_3_line_0 |  | 0 | 1 | 0.0033565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_25-1_0_3_line_1 |  | 0 | 2 | 0.014873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_25-1_0_3_line_2 |  | 1 | 3 | 0.010681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_25-1_0_3_line_3 |  | 2 | 4 | 0.017905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_25-1_0_3_line_4 |  | 3 | 5 | 0.030196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_25-1_0_3_line_5 |  | 3 | 6 | 0.0049993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_25-1_0_3_line_6 |  | 4 | 14 | 0.020172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_25-1_0_3_line_7 |  | 5 | 13 | 0.0061165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_25-1_0_3_line_8 |  | 6 | 7 | 0.022668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_25-1_0_3_line_9 |  | 7 | 8 | 0.015386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_25-1_0_3_line_10 |  | 7 | 9 | 0.016201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_25-1_0_3_line_11 |  | 8 | 15 | 0.0044242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_25-1_0_3_line_12 |  | 10 | 11 | 0.060244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_25-1_0_3_line_13 |  | 10 | 12 | 0.023461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_25-1_0_3_line_14 |  | 11 | 25 | 0.0099967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_25-1_0_3_line_15 |  | 11 | 26 | 0.01924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_25-1_0_3_line_16 |  | 12 | 27 | 0.018958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_25-1_0_3_line_17 |  | 13 | 28 | 0.006988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_25-1_0_3_line_18 |  | 15 | 67 | 0.020108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_25-1_0_3_line_19 |  | 16 | 17 | 0.008758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_25-1_0_3_line_20 |  | 16 | 18 | 0.0070615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_25-1_0_3_line_21 |  | 17 | 21 | 0.060397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_25-1_0_3_line_22 |  | 17 | 74 | 0.016059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_25-1_0_3_line_23 |  | 18 | 75 | 0.020383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_25-1_0_3_line_24 |  | 19 | 20 | 0.065588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_25-1_0_3_line_25 |  | 19 | 21 | 0.0065521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_25-1_0_3_line_26 |  | 20 | 23 | 0.043271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_25-1_0_3_line_27 |  | 22 | 23 | 0.054552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_25-1_0_3_line_28 |  | 22 | 24 | 0.022581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_25-1_0_3_line_29 |  | 24 | 79 | 0.21313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_25-1_0_3_line_30 |  | 25 | 117 | 0.055739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_25-1_0_3_line_31 |  | 26 | 89 | 0.018049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_25-1_0_3_line_32 |  | 26 | 86 | 0.0041611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_25-1_0_3_line_33 |  | 27 | 66 | 0.007991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_25-1_0_3_line_34 |  | 28 | 58 | 0.026487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_25-1_0_3_line_35 |  | 29 | 30 | 0.013026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_25-1_0_3_line_36 |  | 29 | 31 | 0.012068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_25-1_0_3_line_37 |  | 31 | 32 | 0.021746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_25-1_0_3_line_38 |  | 32 | 33 | 0.0038834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_25-1_0_3_line_39 |  | 33 | 37 | 0.012346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_25-1_0_3_line_40 |  | 34 | 35 | 0.023981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_25-1_0_3_line_41 |  | 34 | 36 | 0.038819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_25-1_0_3_line_42 |  | 35 | 42 | 0.020053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_25-1_0_3_line_43 |  | 36 | 38 | 0.007736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_25-1_0_3_line_44 |  | 37 | 61 | 0.012236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_25-1_0_3_line_45 |  | 38 | 39 | 0.015392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_25-1_0_3_line_46 |  | 39 | 40 | 0.0020311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_25-1_0_3_line_47 |  | 40 | 41 | 0.019426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_25-1_0_3_line_48 |  | 41 | 43 | 0.00038277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_25-1_0_3_line_49 |  | 42 | 44 | 0.038865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_25-1_0_3_line_50 |  | 42 | 45 | 0.021987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_25-1_0_3_line_51 |  | 43 | 53 | 0.022198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_25-1_0_3_line_52 |  | 44 | 46 | 0.0099382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_25-1_0_3_line_53 |  | 45 | 47 | 0.0087823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_25-1_0_3_line_54 |  | 46 | 48 | 0.021164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_25-1_0_3_line_55 |  | 47 | 51 | 0.021978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_25-1_0_3_line_56 |  | 48 | 52 | 0.0099694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_25-1_0_3_line_57 |  | 49 | 50 | 0.021417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_25-1_0_3_line_58 |  | 49 | 51 | 0.018585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_25-1_0_3_line_59 |  | 50 | 134 | 0.018831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_25-1_0_3_line_60 |  | 50 | 135 | 0.014938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_25-1_0_3_line_61 |  | 53 | 54 | 0.021087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_25-1_0_3_line_62 |  | 54 | 55 | 0.0026204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_25-1_0_3_line_63 |  | 55 | 56 | 0.021961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_25-1_0_3_line_64 |  | 56 | 57 | 0.008635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_25-1_0_3_line_65 |  | 57 | 58 | 0.01233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_25-1_0_3_line_66 |  | 58 | 60 | 0.011091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_25-1_0_3_line_67 |  | 59 | 60 | 0.012535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_25-1_0_3_line_68 |  | 59 | 61 | 0.039358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_25-1_0_3_line_69 |  | 60 | 62 | 0.021348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_25-1_0_3_line_70 |  | 60 | 63 | 0.036851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_25-1_0_3_line_71 |  | 62 | 99 | 0.012475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_25-1_0_3_line_72 |  | 63 | 96 | 0.025821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_25-1_0_3_line_73 |  | 64 | 65 | 0.041444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_25-1_0_3_line_74 |  | 64 | 66 | 0.0069492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_25-1_0_3_line_75 |  | 67 | 143 | 0.011294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_25-1_0_3_line_76 |  | 68 | 69 | 0.032726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_25-1_0_3_line_77 |  | 69 | 143 | 0.0057433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_25-1_0_3_line_78 |  | 70 | 71 | 0.036571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_25-1_0_3_line_79 |  | 71 | 101 | 0.023332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_25-1_0_3_line_80 |  | 72 | 73 | 0.12696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_25-1_0_3_line_81 |  | 73 | 79 | 0.25007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_25-1_0_3_line_82 |  | 74 | 78 | 0.016471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_25-1_0_3_line_83 |  | 74 | 95 | 0.030504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_25-1_0_3_line_84 |  | 75 | 96 | 0.011662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_25-1_0_3_line_85 |  | 76 | 77 | 0.018865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_25-1_0_3_line_86 |  | 77 | 87 | 0.010428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_25-1_0_3_line_87 |  | 80 | 81 | 0.0031751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_25-1_0_3_line_88 |  | 81 | 120 | 0.015808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_25-1_0_3_line_89 |  | 81 | 117 | 0.031198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_25-1_0_3_line_90 |  | 82 | 83 | 0.0043302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_25-1_0_3_line_91 |  | 82 | 84 | 0.015902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_25-1_0_3_line_92 |  | 83 | 85 | 0.0159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_25-1_0_3_line_93 |  | 84 | 86 | 0.0089937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_25-1_0_3_line_94 |  | 85 | 87 | 0.010726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_25-1_0_3_line_95 |  | 87 | 88 | 0.017642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_25-1_0_3_line_96 |  | 88 | 90 | 0.0017016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_25-1_0_3_line_97 |  | 89 | 114 | 0.0098211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_25-1_0_3_line_98 |  | 90 | 91 | 0.017011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_25-1_0_3_line_99 |  | 91 | 111 | 0.0061876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_25-1_0_3_line_100 |  | 91 | 112 | 0.01104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_25-1_0_3_line_101 |  | 92 | 93 | 0.016844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_25-1_0_3_line_102 |  | 92 | 94 | 0.01728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_25-1_0_3_line_103 |  | 93 | 95 | 0.020828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_25-1_0_3_line_104 |  | 96 | 97 | 0.036396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_25-1_0_3_line_105 |  | 97 | 98 | 0.026394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_25-1_0_3_line_106 |  | 99 | 100 | 0.0082048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_25-1_0_3_line_107 |  | 100 | 109 | 0.0097039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_25-1_0_3_line_108 |  | 101 | 102 | 0.016424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_25-1_0_3_line_109 |  | 102 | 103 | 0.015939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_25-1_0_3_line_110 |  | 103 | 106 | 0.006985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_25-1_0_3_line_111 |  | 103 | 105 | 0.023932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_25-1_0_3_line_112 |  | 104 | 105 | 0.031584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_25-1_0_3_line_113 |  | 105 | 107 | 0.0089203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_25-1_0_3_line_114 |  | 107 | 110 | 0.014718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_25-1_0_3_line_115 |  | 108 | 109 | 0.010991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_25-1_0_3_line_116 |  | 108 | 110 | 0.014749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_25-1_0_3_line_117 |  | 112 | 113 | 0.0083007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_25-1_0_3_line_118 |  | 114 | 115 | 0.010895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_25-1_0_3_line_119 |  | 115 | 116 | 0.0037375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_25-1_0_3_line_120 |  | 117 | 118 | 0.016508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_25-1_0_3_line_121 |  | 117 | 119 | 0.021065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_25-1_0_3_line_122 |  | 118 | 121 | 0.030178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_25-1_0_3_line_123 |  | 119 | 122 | 0.0068517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_25-1_0_3_line_124 |  | 120 | 123 | 0.0039378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_25-1_0_3_line_125 |  | 121 | 124 | 0.0066439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_25-1_0_3_line_126 |  | 122 | 125 | 0.027054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_25-1_0_3_line_127 |  | 122 | 126 | 0.01982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_25-1_0_3_line_128 |  | 123 | 128 | 0.015603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_25-1_0_3_line_129 |  | 124 | 136 | 0.010651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_25-1_0_3_line_130 |  | 124 | 137 | 0.011704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_25-1_0_3_line_131 |  | 125 | 131 | 0.0012011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_25-1_0_3_line_132 |  | 126 | 130 | 0.023059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_25-1_0_3_line_133 |  | 127 | 128 | 0.0055362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_25-1_0_3_line_134 |  | 127 | 129 | 0.012278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_25-1_0_3_line_135 |  | 131 | 132 | 0.016818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_25-1_0_3_line_136 |  | 132 | 133 | 0.022741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_25-1_0_3_line_137 |  | 134 | 140 | 0.0019517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_25-1_0_3_line_138 |  | 135 | 142 | 0.0046833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_25-1_0_3_line_139 |  | 136 | 138 | 0.0084542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_25-1_0_3_line_140 |  | 137 | 139 | 0.011766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_25-1_0_3_line_141 |  | 138 | 140 | 0.014431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_25-1_0_3_line_142 |  | 140 | 141 | 0.02645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_25-1_0_3_trafo_103 | 0.63 MVA 20/0.4 kV | 144 | 100 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2688282.89 | 1280268.6186 | 2688280.9529 | 1280271.3598
1 | 2688270.3431 | 1280280.2852 | 2688275.2307 | 1280279.4577 | 2688280.9529 | 1280271.3598
2 | 2688291.9465 | 1280274.3257 | 2688282.89 | 1280268.6186
3 | 2688256.2158 | 1280287.1352 | 2688257.8091 | 1280285.0795 | 2688259.5939 | 1280282.7709 | 2688265.2451 | 1280278.6075 | 2688270.3431 | 1280280.2852
4 | 2688292.1217 | 1280304.2428 | 2688290.6753 | 1280299.506 | 2688290.4957 | 1280293.4426 | 2688290.7785 | 1280286.5965 | 2688291.3151 | 1280280.3659 | 2688291.9465 | 1280274.3257
5 | 2688291.9465 | 1280274.3257 | 2688293.0359 | 1280269.4466
6 | 2688256.2158 | 1280287.1352 | 2688243.8669 | 1280303.0853
7 | 2688292.1217 | 1280304.2428 | 2688296.2533 | 1280308.7529
8 | 2688299.2043 | 1280247.6672 | 2688297.0989 | 1280253.3183 | 2688295.6447 | 1280258.6233 | 2688294.7084 | 1280261.9565 | 2688293.0359 | 1280269.4466
9 | 2688299.2043 | 1280247.6672 | 2688301.0439 | 1280244.214 | 2688303.1598 | 1280241.3655 | 2688308.0427 | 1280237.3463 | 2688309.391 | 1280236.4831
10 | 2688299.2043 | 1280247.6672 | 2688287.0726 | 1280236.9303
11 | 2688309.391 | 1280236.4831 | 2688313.117 | 1280234.0977
12 | 2688188.8966 | 1280224.7417 | 2688236.4235 | 1280261.9509
13 | 2688236.4235 | 1280261.9509 | 2688250.8924 | 1280243.4823
14 | 2688188.8966 | 1280224.7417 | 2688181.2574 | 1280227.2185 | 2688180.1257 | 1280228.8262
15 | 2688200.6186 | 1280209.4595 | 2688188.8966 | 1280224.7417
16 | 2688262.5843 | 1280228.5584 | 2688250.8924 | 1280243.4823
17 | 2688296.2533 | 1280308.7529 | 2688301.9192 | 1280312.8431
18 | 2688330.0516 | 1280223.2562 | 2688313.117 | 1280234.0977
19 | 2688412.6487 | 1280396.427 | 2688420.3527 | 1280400.635
20 | 2688412.6487 | 1280396.427 | 2688406.8194 | 1280392.4413
21 | 2688420.3527 | 1280400.635 | 2688433.1979 | 1280401.6284 | 2688447.4034 | 1280401.5747 | 2688459.8656 | 1280398.559 | 2688473.957 | 1280393.5995 | 2688478.8687 | 1280391.0221
22 | 2688412.8307 | 1280414.8343 | 2688420.3527 | 1280400.635
23 | 2688390.9287 | 1280379.6977 | 2688403.7187 | 1280390.3212 | 2688406.8194 | 1280392.4413
24 | 2688484.6705 | 1280387.9777 | 2688503.3948 | 1280372.1451 | 2688508.5723 | 1280366.518 | 2688513.4178 | 1280364.9894 | 2688517.8655 | 1280365.9459 | 2688521.7557 | 1280368.5064 | 2688524.1143 | 1280372.0115 | 2688524.7912 | 1280374.9575 | 2688524.1149 | 1280377.9722 | 2688520.7989 | 1280386.1188
25 | 2688484.6705 | 1280387.9777 | 2688478.8687 | 1280391.0221
26 | 2688504.4857 | 1280426.1973 | 2688520.7989 | 1280386.1188
27 | 2688480.0321 | 1280474.7711 | 2688489.3877 | 1280460.5215 | 2688499.5463 | 1280438.3327 | 2688504.4857 | 1280426.1973
28 | 2688480.0321 | 1280474.7711 | 2688465.513 | 1280492.0649
29 | 2688371.4876 | 1280680.1968 | 2688372.0683 | 1280672.5323 | 2688386.8941 | 1280624.5691 | 2688393.7365 | 1280606.5785 | 2688402.3316 | 1280589.9264 | 2688408.0644 | 1280579.8148 | 2688415.1401 | 1280569.8124 | 2688419.5094 | 1280563.9618 | 2688429.8792 | 1280551.6957 | 2688435.8501 | 1280544.7348 | 2688445.4264 | 1280530.2883 | 2688450.4841 | 1280520.6226 | 2688454.763 | 1280509.2882 | 2688459.2131 | 1280499.5688 | 2688465.513 | 1280492.0649
30 | 2688150.2273 | 1280275.8072 | 2688165.4007 | 1280249.7451 | 2688180.1257 | 1280228.8262
31 | 2688200.6186 | 1280209.4595 | 2688186.2875 | 1280198.4875
32 | 2688200.6186 | 1280209.4595 | 2688203.2302 | 1280206.22
33 | 2688267.5164 | 1280222.2601 | 2688262.5843 | 1280228.5584
34 | 2688324.4467 | 1280326.7015 | 2688316.4938 | 1280322.5455 | 2688305.9439 | 1280315.7484 | 2688301.9192 | 1280312.8431
35 | 2688302.8769 | 1280441.5268 | 2688299.3299 | 1280454.0602
36 | 2688302.8769 | 1280441.5268 | 2688306.1631 | 1280429.915
37 | 2688312.0848 | 1280408.9905 | 2688306.1631 | 1280429.915
38 | 2688312.0848 | 1280408.9905 | 2688313.1423 | 1280405.2538
39 | 2688316.5043 | 1280393.3741 | 2688313.1423 | 1280405.2538
40 | 2688200.146 | 1280445.298 | 2688179.745 | 1280432.6922
41 | 2688200.146 | 1280445.298 | 2688228.9248 | 1280419.2469
42 | 2688162.686 | 1280422.1515 | 2688179.745 | 1280432.6922
43 | 2688234.6601 | 1280414.0552 | 2688228.9248 | 1280419.2469
44 | 2688319.8364 | 1280381.6002 | 2688316.5043 | 1280393.3741
45 | 2688234.6601 | 1280414.0552 | 2688246.0709 | 1280403.7259
46 | 2688247.5767 | 1280402.3628 | 2688246.0709 | 1280403.7259
47 | 2688261.9785 | 1280389.326 | 2688247.5767 | 1280402.3628
48 | 2688262.2623 | 1280389.0692 | 2688261.9785 | 1280389.326
49 | 2688162.686 | 1280422.1515 | 2688180.8438 | 1280387.7886
50 | 2688142.5534 | 1280413.6989 | 2688150.0183 | 1280415.323 | 2688159.3672 | 1280420.0557 | 2688162.686 | 1280422.1515
51 | 2688262.2623 | 1280389.0692 | 2688278.7194 | 1280374.1719
52 | 2688185.8041 | 1280379.2041 | 2688184.4091 | 1280381.0412 | 2688180.8438 | 1280387.7886
53 | 2688142.5534 | 1280413.6989 | 2688134.554 | 1280410.0741
54 | 2688185.8041 | 1280379.2041 | 2688198.6031 | 1280362.3491
55 | 2688114.5357 | 1280401.0031 | 2688134.554 | 1280410.0741
56 | 2688198.6031 | 1280362.3491 | 2688204.6321 | 1280354.4094
57 | 2688104.745 | 1280373.1327 | 2688097.6073 | 1280393.3322
58 | 2688097.6073 | 1280393.3322 | 2688114.5357 | 1280401.0031
59 | 2688104.745 | 1280373.1327 | 2688111.0611 | 1280355.3922
60 | 2688104.745 | 1280373.1327 | 2688090.4377 | 1280368.8381
61 | 2688294.3524 | 1280360.0206 | 2688278.7194 | 1280374.1719
62 | 2688296.295 | 1280358.2621 | 2688294.3524 | 1280360.0206
63 | 2688296.295 | 1280358.2621 | 2688312.5763 | 1280343.5239
64 | 2688318.978 | 1280337.729 | 2688312.5763 | 1280343.5239
65 | 2688324.4467 | 1280326.7015 | 2688321.75 | 1280331.2094 | 2688318.978 | 1280337.729
66 | 2688334.3388 | 1280331.7762 | 2688324.4467 | 1280326.7015
67 | 2688334.3388 | 1280331.7762 | 2688331.1384 | 1280341.8257 | 2688330.5539 | 1280343.7297
68 | 2688330.5539 | 1280343.7297 | 2688319.8364 | 1280381.6002
69 | 2688334.3388 | 1280331.7762 | 2688336.2388 | 1280327.8013 | 2688341.7831 | 1280316.2411 | 2688344.2594 | 1280312.946
70 | 2688334.3388 | 1280331.7762 | 2688342.5445 | 1280336.6032 | 2688362.6108 | 1280355.159
71 | 2688351.7541 | 1280302.9731 | 2688344.2594 | 1280312.946
72 | 2688381.9578 | 1280372.2463 | 2688373.3736 | 1280365.1116 | 2688362.6108 | 1280355.159
73 | 2688271.8027 | 1280216.7903 | 2688297.366 | 1280184.1694
74 | 2688267.5164 | 1280222.2601 | 2688271.8027 | 1280216.7903
75 | 2688330.0516 | 1280223.2562 | 2688339.5631 | 1280217.1668
76 | 2688371.9621 | 1280196.4249 | 2688344.4001 | 1280214.0702
77 | 2688344.4001 | 1280214.0702 | 2688339.5631 | 1280217.1668
78 | 2688436.1841 | 1280232.173 | 2688464.5705 | 1280255.2305
79 | 2688436.1841 | 1280232.173 | 2688428.469 | 1280241.2095 | 2688418.8349 | 1280234.9486
80 | 2688505.1534 | 1280594.1389 | 2688516.3513 | 1280585.7553 | 2688546.9408 | 1280570.5904 | 2688560.0028 | 1280559.1323 | 2688573.9723 | 1280541.2713 | 2688590.9953 | 1280508.1765 | 2688591.7229 | 1280506.7974
81 | 2688371.4876 | 1280680.1968 | 2688389.7867 | 1280688.1223 | 2688415.5773 | 1280697.8617 | 2688483.2625 | 1280721.3524 | 2688488.9304 | 1280671.05 | 2688490.2653 | 1280659.1821 | 2688494.8617 | 1280613.2118 | 2688498.7984 | 1280601.1606 | 2688505.1534 | 1280594.1389
82 | 2688412.8307 | 1280414.8343 | 2688425.1453 | 1280425.773
83 | 2688412.8307 | 1280414.8343 | 2688395.8959 | 1280440.2057
84 | 2688381.9578 | 1280372.2463 | 2688390.9287 | 1280379.6977
85 | 2688244.8814 | 1280154.6627 | 2688256.8155 | 1280140.0527
86 | 2688238.2846 | 1280162.7387 | 2688244.8814 | 1280154.6627
87 | 2688122.9681 | 1280260.6424 | 2688120.1469 | 1280259.1856
88 | 2688122.9681 | 1280260.6424 | 2688132.2861 | 1280247.8722
89 | 2688122.9681 | 1280260.6424 | 2688144.0822 | 1280271.3115 | 2688150.2273 | 1280275.8072
90 | 2688218.8556 | 1280186.8383 | 2688221.5734 | 1280183.4672
91 | 2688218.8556 | 1280186.8383 | 2688208.875 | 1280199.2183
92 | 2688231.5528 | 1280171.0888 | 2688221.5734 | 1280183.4672
93 | 2688208.875 | 1280199.2183 | 2688203.2302 | 1280206.22
94 | 2688238.2846 | 1280162.7387 | 2688231.5528 | 1280171.0888
95 | 2688238.2846 | 1280162.7387 | 2688224.4575 | 1280151.7816
96 | 2688223.1238 | 1280150.7248 | 2688224.4575 | 1280151.7816
97 | 2688178.4894 | 1280192.5172 | 2688186.2875 | 1280198.4875
98 | 2688209.7914 | 1280140.1599 | 2688223.1238 | 1280150.7248
99 | 2688209.7914 | 1280140.1599 | 2688213.426 | 1280135.1523
100 | 2688209.7914 | 1280140.1599 | 2688203.0399 | 1280148.8951
101 | 2688374.9819 | 1280471.5386 | 2688384.3331 | 1280457.5289
102 | 2688365.3887 | 1280485.911 | 2688374.9819 | 1280471.5386
103 | 2688384.3331 | 1280457.5289 | 2688395.8959 | 1280440.2057
104 | 2688381.9578 | 1280372.2463 | 2688383.9753 | 1280369.9524 | 2688386.0243 | 1280367.5588 | 2688389.8523 | 1280365.2587 | 2688391.5601 | 1280363.5829 | 2688392.3313 | 1280362.7493 | 2688392.8055 | 1280359.1755 | 2688394.1894 | 1280357.0611 | 2688397.4262 | 1280353.1063 | 2688404.5743 | 1280344.8063
105 | 2688404.5743 | 1280344.8063 | 2688411.0154 | 1280337.0629 | 2688406.405 | 1280333.4352 | 2688411.503 | 1280326.5947 | 2688412.6595 | 1280325.0564
106 | 2688356.6834 | 1280296.4141 | 2688351.7541 | 1280302.9731
107 | 2688356.6834 | 1280296.4141 | 2688362.5164 | 1280288.659
108 | 2688418.8349 | 1280234.9486 | 2688407.9132 | 1280247.2146
109 | 2688397.6746 | 1280259.4301 | 2688405.462 | 1280250.0833 | 2688407.2364 | 1280247.9747 | 2688407.9132 | 1280247.2146
110 | 2688397.6746 | 1280259.4301 | 2688403.291 | 1280263.6067
111 | 2688390.3194 | 1280247.9767 | 2688393.2457 | 1280255.2157 | 2688393.8313 | 1280264.7548 | 2688397.6746 | 1280259.4301
112 | 2688390.3194 | 1280247.9767 | 2688392.6973 | 1280243.6976 | 2688402.3383 | 1280218.8112
113 | 2688390.3194 | 1280247.9767 | 2688385.988 | 1280255.7748
114 | 2688385.988 | 1280255.7748 | 2688382.4292 | 1280262.1817 | 2688377.9879 | 1280268.0875
115 | 2688369.1232 | 1280279.8752 | 2688362.5164 | 1280288.659
116 | 2688369.1232 | 1280279.8752 | 2688377.9879 | 1280268.0875
117 | 2688197.9637 | 1280155.4627 | 2688203.0399 | 1280148.8951
118 | 2688178.4894 | 1280192.5172 | 2688169.8384 | 1280185.8939
119 | 2688166.8707 | 1280183.6218 | 2688169.8384 | 1280185.8939
120 | 2688150.2273 | 1280275.8072 | 2688142.225 | 1280290.2456
121 | 2688150.2273 | 1280275.8072 | 2688155.1838 | 1280279.4176 | 2688167.8245 | 1280287.3668
122 | 2688142.225 | 1280290.2456 | 2688137.4272 | 1280298.9022 | 2688127.9418 | 1280316.8285
123 | 2688173.6247 | 1280291.0143 | 2688167.8245 | 1280287.3668
124 | 2688134.6071 | 1280244.6912 | 2688132.2861 | 1280247.8722
125 | 2688124.8344 | 1280322.701 | 2688127.9418 | 1280316.8285
126 | 2688173.6247 | 1280291.0143 | 2688196.6218 | 1280305.2646
127 | 2688173.6247 | 1280291.0143 | 2688184.5234 | 1280274.4598
128 | 2688143.8041 | 1280232.0867 | 2688134.6071 | 1280244.6912
129 | 2688124.8344 | 1280322.701 | 2688120.3739 | 1280332.3732
130 | 2688124.8344 | 1280322.701 | 2688113.7579 | 1280318.9197
131 | 2688197.6428 | 1280305.8972 | 2688196.6218 | 1280305.2646
132 | 2688197.2032 | 1280255.1999 | 2688184.5234 | 1280274.4598
133 | 2688147.0673 | 1280227.6145 | 2688143.8041 | 1280232.0867
134 | 2688154.3042 | 1280217.6963 | 2688147.0673 | 1280227.6145
135 | 2688197.6428 | 1280305.8972 | 2688207.119 | 1280292.0032
136 | 2688219.9326 | 1280273.2159 | 2688207.119 | 1280292.0032
137 | 2688111.7157 | 1280353.5535 | 2688111.0611 | 1280355.3922
138 | 2688085.9522 | 1280367.4917 | 2688090.4377 | 1280368.8381
139 | 2688120.3739 | 1280332.3732 | 2688119.0739 | 1280335.1922 | 2688117.0838 | 1280340.1581
140 | 2688102.6226 | 1280315.1182 | 2688113.7579 | 1280318.9197
141 | 2688111.7157 | 1280353.5535 | 2688117.0838 | 1280340.1581
142 | 2688086.4936 | 1280345.3475 | 2688111.7157 | 1280353.5535

## bus_geodata
| x | y | coords
0 | 2688280.9529 | 1280271.3598
1 | 2688282.89 | 1280268.6186
2 | 2688270.3431 | 1280280.2852
3 | 2688291.9465 | 1280274.3257
4 | 2688256.2158 | 1280287.1352
5 | 2688292.1217 | 1280304.2428
6 | 2688293.0359 | 1280269.4466
7 | 2688299.2043 | 1280247.6672
8 | 2688309.391 | 1280236.4831
9 | 2688287.0726 | 1280236.9303
10 | 2688236.4235 | 1280261.9509
11 | 2688188.8966 | 1280224.7417
12 | 2688250.8924 | 1280243.4823
13 | 2688296.2532 | 1280308.7529
14 | 2688243.8669 | 1280303.0853
15 | 2688313.117 | 1280234.0977
16 | 2688412.6487 | 1280396.427
17 | 2688420.3527 | 1280400.635
18 | 2688406.8194 | 1280392.4413
19 | 2688484.6705 | 1280387.9777
20 | 2688520.7989 | 1280386.1188
21 | 2688478.8687 | 1280391.0221
22 | 2688480.0321 | 1280474.7711
23 | 2688504.4857 | 1280426.1973
24 | 2688465.513 | 1280492.0649
25 | 2688180.1257 | 1280228.8262
26 | 2688200.6186 | 1280209.4595
27 | 2688262.5843 | 1280228.5584
28 | 2688301.9192 | 1280312.8431
29 | 2688302.8769 | 1280441.5268
30 | 2688299.3299 | 1280454.0602
31 | 2688306.1631 | 1280429.915
32 | 2688312.0848 | 1280408.9905
33 | 2688313.1423 | 1280405.2538
34 | 2688200.146 | 1280445.298
35 | 2688179.745 | 1280432.6922
36 | 2688228.9248 | 1280419.2469
37 | 2688316.5043 | 1280393.3741
38 | 2688234.6601 | 1280414.0552
39 | 2688246.0709 | 1280403.7259
40 | 2688247.5767 | 1280402.3629
41 | 2688261.9785 | 1280389.326
42 | 2688162.686 | 1280422.1515
43 | 2688262.2623 | 1280389.0692
44 | 2688180.8438 | 1280387.7886
45 | 2688142.5534 | 1280413.6989
46 | 2688185.8041 | 1280379.2041
47 | 2688134.554 | 1280410.0741
48 | 2688198.6031 | 1280362.3491
49 | 2688097.6073 | 1280393.3322
50 | 2688104.745 | 1280373.1327
51 | 2688114.5357 | 1280401.0031
52 | 2688204.6321 | 1280354.4094
53 | 2688278.7194 | 1280374.1719
54 | 2688294.3524 | 1280360.0206
55 | 2688296.295 | 1280358.2621
56 | 2688312.5763 | 1280343.5239
57 | 2688318.978 | 1280337.729
58 | 2688324.4467 | 1280326.7015
59 | 2688330.5539 | 1280343.7297
60 | 2688334.3388 | 1280331.7762
61 | 2688319.8364 | 1280381.6002
62 | 2688344.2594 | 1280312.946
63 | 2688362.6108 | 1280355.159
64 | 2688271.8027 | 1280216.7903
65 | 2688297.366 | 1280184.1694
66 | 2688267.5164 | 1280222.2601
67 | 2688330.0516 | 1280223.2562
68 | 2688371.9621 | 1280196.4249
69 | 2688344.4001 | 1280214.0702
70 | 2688464.5705 | 1280255.2305
71 | 2688436.1841 | 1280232.173
72 | 2688591.7229 | 1280506.7974
73 | 2688505.1534 | 1280594.1389
74 | 2688412.8307 | 1280414.8343
75 | 2688390.9287 | 1280379.6977
76 | 2688256.8155 | 1280140.0527
77 | 2688244.8814 | 1280154.6627
78 | 2688425.1453 | 1280425.773
79 | 2688371.4876 | 1280680.1968
80 | 2688120.1469 | 1280259.1856
81 | 2688122.9681 | 1280260.6424
82 | 2688218.8556 | 1280186.8383
83 | 2688221.5734 | 1280183.4672
84 | 2688208.875 | 1280199.2183
85 | 2688231.5528 | 1280171.0888
86 | 2688203.2302 | 1280206.22
87 | 2688238.2846 | 1280162.7387
88 | 2688224.4575 | 1280151.7816
89 | 2688186.2875 | 1280198.4875
90 | 2688223.1238 | 1280150.7248
91 | 2688209.7914 | 1280140.1599
92 | 2688374.9819 | 1280471.5386
93 | 2688384.3331 | 1280457.5289
94 | 2688365.3887 | 1280485.911
95 | 2688395.8959 | 1280440.2057
96 | 2688381.9578 | 1280372.2463
97 | 2688404.5743 | 1280344.8063
98 | 2688412.6595 | 1280325.0564
99 | 2688351.7541 | 1280302.9731
100 | 2688356.6834 | 1280296.4141
101 | 2688418.8349 | 1280234.9486
102 | 2688407.9132 | 1280247.2146
103 | 2688397.6746 | 1280259.4301
104 | 2688402.3383 | 1280218.8112
105 | 2688390.3194 | 1280247.9767
106 | 2688403.291 | 1280263.6067
107 | 2688385.988 | 1280255.7748
108 | 2688369.1232 | 1280279.8752
109 | 2688362.5164 | 1280288.659
110 | 2688377.9879 | 1280268.0875
111 | 2688213.426 | 1280135.1523
112 | 2688203.0399 | 1280148.8951
113 | 2688197.9637 | 1280155.4627
114 | 2688178.4894 | 1280192.5172
115 | 2688169.8384 | 1280185.8939
116 | 2688166.8707 | 1280183.6218
117 | 2688150.2273 | 1280275.8072
118 | 2688142.225 | 1280290.2456
119 | 2688167.8245 | 1280287.3668
120 | 2688132.2861 | 1280247.8722
121 | 2688127.9418 | 1280316.8285
122 | 2688173.6247 | 1280291.0143
123 | 2688134.6071 | 1280244.6912
124 | 2688124.8344 | 1280322.701
125 | 2688196.6218 | 1280305.2646
126 | 2688184.5234 | 1280274.4598
127 | 2688147.0673 | 1280227.6145
128 | 2688143.8041 | 1280232.0867
129 | 2688154.3042 | 1280217.6963
130 | 2688197.2032 | 1280255.1999
131 | 2688197.6428 | 1280305.8972
132 | 2688207.119 | 1280292.0032
133 | 2688219.9326 | 1280273.2159
134 | 2688111.0611 | 1280355.3922
135 | 2688090.4377 | 1280368.8381
136 | 2688120.3739 | 1280332.3732
137 | 2688113.758 | 1280318.9197
138 | 2688117.0838 | 1280340.1581
139 | 2688102.6226 | 1280315.1182
140 | 2688111.7157 | 1280353.5535
141 | 2688086.4936 | 1280345.3475
142 | 2688085.9522 | 1280367.4917
143 | 2688339.5631 | 1280217.1668
144 | 2688367.7206 | 1280302.2733

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99395 | -0.11532 | 0.0030267 | 0.00075857
1 | 0.99398 | -0.11474 | 0 | 0
2 | 0.99386 | -0.11708 | 0 | 0
3 | 0.99408 | -0.1129 | 0 | 0
4 | 0.99375 | -0.1192 | 0 | 0
5 | 0.99483 | -0.098379 | 0 | 0
6 | 0.994 | -0.11445 | 0.0021514 | 0.00053919
7 | 0.99368 | -0.1206 | 0 | 0
8 | 0.99349 | -0.12422 | 0.0025067 | 0.00062824
9 | 0.99365 | -0.12119 | 0.0020522 | 0.00051433
10 | 0.97168 | -0.54587 | 0 | 0
11 | 0.97246 | -0.53048 | 0 | 0
12 | 0.97138 | -0.55187 | 0.0029406 | 0.00073699
13 | 0.99498 | -0.09544 | 0.0052016 | 0.0013036
14 | 0.99363 | -0.1216 | 0.0067226 | 0.0016848
15 | 0.99345 | -0.12507 | 0.00090802 | 0.00022757
16 | 0.99516 | -0.092346 | 0 | 0
17 | 0.99505 | -0.094357 | 0 | 0
18 | 0.99524 | -0.090725 | 0.001534 | 0.00038446
19 | 0.9946 | -0.10306 | 0 | 0
20 | 0.99427 | -0.10964 | 0.0016364 | 0.00041011
21 | 0.99464 | -0.1024 | 0.0018667 | 0.00046784
22 | 0.99399 | -0.11507 | 0 | 0
23 | 0.99411 | -0.11273 | 0.0016239 | 0.00040699
24 | 0.99394 | -0.11604 | 0.0016571 | 0.00041532
25 | 0.9729 | -0.52186 | 0.0014177 | 0.00035532
26 | 0.97187 | -0.54218 | 0 | 0
27 | 0.97119 | -0.55569 | 0 | 0
28 | 0.99519 | -0.091444 | 0.0013837 | 0.00034679
29 | 0.99623 | -0.071689 | 0.00095371 | 0.00023902
30 | 0.9962 | -0.072104 | 0.0018149 | 0.00045486
31 | 0.99626 | -0.071102 | 0.00083187 | 0.00020849
32 | 0.99633 | -0.069727 | 0.00060514 | 0.00015166
33 | 0.99634 | -0.06944 | 0.0011748 | 0.00029442
34 | 0.98772 | -0.23349 | 0 | 0
35 | 0.98665 | -0.25418 | 0.0074102 | 0.0018572
36 | 0.98947 | -0.2001 | 0.0019144 | 0.0004798
37 | 0.9964 | -0.068273 | 0.00021894 | 5.4871e-05
38 | 0.98982 | -0.19333 | 0.001055 | 0.00026441
39 | 0.99053 | -0.17973 | 0.0016209 | 0.00040623
40 | 0.99063 | -0.1779 | 0.0012358 | 0.00030972
41 | 0.99155 | -0.16027 | 0.0015753 | 0.00039481
42 | 0.98582 | -0.27018 | 0 | 0
43 | 0.99157 | -0.15992 | 0.001557 | 0.00039022
44 | 0.98558 | -0.27485 | 0.00038428 | 9.6309e-05
45 | 0.98497 | -0.28643 | 0 | 0
46 | 0.98552 | -0.27597 | 0.0027081 | 0.00067872
47 | 0.98463 | -0.29293 | 0.00059613 | 0.0001494
48 | 0.98545 | -0.27734 | 0.00079886 | 0.00020021
49 | 0.9831 | -0.32262 | 0 | 0
50 | 0.98229 | -0.33822 | 0 | 0
51 | 0.9838 | -0.30909 | 0.00099067 | 0.00024829
52 | 0.98542 | -0.27784 | 0.0028024 | 0.00070234
53 | 0.99266 | -0.1392 | 0.001479 | 0.00037067
54 | 0.99371 | -0.11928 | 0.000227 | 5.6892e-05
55 | 0.99384 | -0.11681 | 0.0015911 | 0.00039877
56 | 0.99494 | -0.095763 | 0.00026625 | 6.6729e-05
57 | 0.99538 | -0.087481 | 0 | 0
58 | 0.99601 | -0.075668 | 0 | 0
59 | 0.99667 | -0.063041 | 0 | 0
60 | 0.99674 | -0.061759 | 0 | 0
61 | 0.99646 | -0.06707 | 0.0002299 | 5.7618e-05
62 | 0.99839 | -0.030427 | 0.00052832 | 0.00013241
63 | 0.99611 | -0.073976 | 0.00062154 | 0.00015577
64 | 0.97104 | -0.5587 | 0.0047654 | 0.0011943
65 | 0.9708 | -0.5634 | 0.0061352 | 0.0015376
66 | 0.97111 | -0.5573 | 0 | 0
67 | 0.99327 | -0.12859 | 0.0027982 | 0.0007013
68 | 0.99304 | -0.13301 | 0.004176 | 0.0010466
69 | 0.99316 | -0.13059 | 0.001593 | 0.00039925
70 | 0.98381 | -0.31144 | 0.081808 | 0.020503
71 | 0.98657 | -0.25771 | 0 | 0
72 | 0.99353 | -0.12396 | 0.00075072 | 0.00018815
73 | 0.99362 | -0.12227 | 0 | 0
74 | 0.99497 | -0.095907 | 0 | 0
75 | 0.99551 | -0.085497 | 0.0011874 | 0.00029759
76 | 0.97061 | -0.56701 | 0.0019195 | 0.00048108
77 | 0.97065 | -0.56634 | 0.0017951 | 0.00044991
78 | 0.99496 | -0.096254 | 0.0011947 | 0.00029941
79 | 0.99379 | -0.11892 | 0 | 0
80 | 0.97504 | -0.47974 | 0.001337 | 0.00033509
81 | 0.97504 | -0.47967 | 0 | 0
82 | 0.97122 | -0.55508 | 0.0015762 | 0.00039504
83 | 0.97113 | -0.55679 | 0.0026422 | 0.00066221
84 | 0.97156 | -0.54834 | 0.0013662 | 0.0003424
85 | 0.97085 | -0.56229 | 0.0018625 | 0.00046679
86 | 0.97176 | -0.54431 | 0.00346 | 0.00086717
87 | 0.97068 | -0.56563 | 0 | 0
88 | 0.97047 | -0.56991 | 0.0034287 | 0.00085932
89 | 0.97178 | -0.54391 | 0.0013616 | 0.00034126
90 | 0.97045 | -0.57022 | 0.0048541 | 0.0012165
91 | 0.97038 | -0.57174 | 0 | 0
92 | 0.99474 | -0.1004 | 0.0011557 | 0.00028966
93 | 0.99479 | -0.099541 | 0.00072022 | 0.00018051
94 | 0.99471 | -0.10094 | 0.0017522 | 0.00043915
95 | 0.99485 | -0.098209 | 0.00065604 | 0.00016442
96 | 0.99568 | -0.082263 | 0 | 0
97 | 0.9956 | -0.083859 | 0 | 0
98 | 0.99554 | -0.085015 | 0.0024918 | 0.0006245
99 | 0.99936 | -0.012108 | 0.0011143 | 0.00027926
100 | 1 | 0 | -0.29946 | -0.076232
101 | 0.98833 | -0.22359 | 0 | 0
102 | 0.98957 | -0.19964 | 0.023344 | 0.0058506
103 | 0.99111 | -0.16986 | 0 | 0
104 | 0.99346 | -0.12473 | 0.0032964 | 0.00082616
105 | 0.99355 | -0.1229 | 0 | 0
106 | 0.99107 | -0.17057 | 0.0057116 | 0.0014315
107 | 0.99449 | -0.10493 | 0.0025359 | 0.00063555
108 | 0.99768 | -0.043942 | 0 | 0
109 | 0.99889 | -0.021079 | 0.0055481 | 0.0013905
110 | 0.99607 | -0.07471 | 0.0022379 | 0.00056088
111 | 0.97037 | -0.57195 | 0.0018502 | 0.00046371
112 | 0.97035 | -0.57235 | 0.0013235 | 0.0003317
113 | 0.97033 | -0.57261 | 0.001669 | 0.00041829
114 | 0.97175 | -0.54461 | 0.0012414 | 0.00031113
115 | 0.97172 | -0.54514 | 0.0013614 | 0.00034119
116 | 0.97172 | -0.54522 | 0.0012431 | 0.00031155
117 | 0.97541 | -0.47249 | 0 | 0
118 | 0.97652 | -0.4507 | 0.0013968 | 0.00035008
119 | 0.97519 | -0.47688 | 0.0015181 | 0.00038047
120 | 0.97488 | -0.48292 | 0.0032504 | 0.00081463
121 | 0.97859 | -0.41023 | 0.0010219 | 0.00025611
122 | 0.97512 | -0.47811 | 0 | 0
123 | 0.97485 | -0.48349 | 0.0020958 | 0.00052527
124 | 0.97905 | -0.40122 | 0 | 0
125 | 0.97498 | -0.48086 | 0.00051883 | 0.00013003
126 | 0.97504 | -0.47967 | 0.0021634 | 0.0005422
127 | 0.97474 | -0.48558 | 0.0020897 | 0.00052372
128 | 0.97477 | -0.48517 | 0.0017895 | 0.0004485
129 | 0.97472 | -0.48603 | 0.001982 | 0.00049674
130 | 0.975 | -0.48057 | 0.0021324 | 0.00053443
131 | 0.97498 | -0.48097 | 0 | 0
132 | 0.9749 | -0.48252 | 0.0024434 | 0.00061237
133 | 0.97485 | -0.48359 | 0.0025749 | 0.00064533
134 | 0.9816 | -0.35172 | 0.00099741 | 0.00024997
135 | 0.98227 | -0.33862 | 0.00070056 | 0.00017558
136 | 0.9798 | -0.38654 | 0.0009664 | 0.0002422
137 | 0.97904 | -0.4015 | 0.00070456 | 0.00017658
138 | 0.98041 | -0.37476 | 0.00072535 | 0.00018179
139 | 0.97903 | -0.40163 | 0.00060772 | 0.00015231
140 | 0.98145 | -0.35448 | 0 | 0
141 | 0.98144 | -0.35483 | 0.00072758 | 0.00018235
142 | 0.98227 | -0.33869 | 0.00077399 | 0.00019398
143 | 0.99319 | -0.13001 | 0.0013441 | 0.00033686
144 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0097514 | -0.002444 | 0.0097516 | 0.0024441 | 2.6825e-07 | 1.2817e-07 | 0.014599 | 0.014598 | 0.014599 | 0.99395 | -0.11532 | 0.99398 | -0.11474 | 4.0106
1 | 0.0067246 | 0.0016854 | -0.0067241 | -0.0016853 | 5.6526e-07 | 1.6902e-07 | 0.010067 | 0.010067 | 0.010067 | 0.99395 | -0.11532 | 0.99386 | -0.11708 | 2.7658
2 | -0.0097516 | -0.0024441 | 0.0097525 | 0.0024446 | 8.5361e-07 | 4.0785e-07 | 0.014598 | 0.014598 | 0.014598 | 0.99398 | -0.11474 | 0.99408 | -0.1129 | 4.0106
3 | 0.0067241 | 0.0016853 | -0.0067234 | -0.0016851 | 6.8052e-07 | 2.0353e-07 | 0.010067 | 0.010067 | 0.010067 | 0.99386 | -0.11708 | 0.99375 | -0.1192 | 2.7658
4 | -0.027293 | -0.0068434 | 0.027312 | 0.0068551 | 1.8901e-05 | 1.1705e-05 | 0.040856 | 0.040856 | 0.040856 | 0.99408 | -0.1129 | 0.99483 | -0.098379 | 11.2242
5 | 0.017541 | 0.0043989 | -0.01754 | -0.0043981 | 1.2926e-06 | 7.6244e-07 | 0.026258 | 0.026258 | 0.026258 | 0.99408 | -0.1129 | 0.994 | -0.11445 | 7.2137
6 | 0.0067234 | 0.0016851 | -0.0067226 | -0.0016848 | 7.6669e-07 | 2.2937e-07 | 0.010067 | 0.010068 | 0.010068 | 0.99375 | -0.1192 | 0.99363 | -0.1216 | 2.7658
7 | -0.027312 | -0.0068551 | 0.027316 | 0.0068575 | 3.8286e-06 | 2.3709e-06 | 0.040856 | 0.040856 | 0.040856 | 0.99483 | -0.098379 | 0.99498 | -0.09544 | 11.2242
8 | 0.015388 | 0.0038589 | -0.015384 | -0.0038563 | 4.5113e-06 | 2.5935e-06 | 0.023037 | 0.023037 | 0.023037 | 0.994 | -0.11445 | 0.99368 | -0.1206 | 6.3289
9 | 0.013332 | 0.0033422 | -0.013329 | -0.0033409 | 2.2997e-06 | 1.2725e-06 | 0.019964 | 0.019964 | 0.019964 | 0.99368 | -0.1206 | 0.99349 | -0.12422 | 5.4847
10 | 0.0020522 | 0.00051415 | -0.0020522 | -0.00051433 | 5.7377e-08 | -1.7313e-07 | 0.0030731 | 0.0030732 | 0.0030732 | 0.99368 | -0.1206 | 0.99365 | -0.12119 | 0.84429
11 | 0.010823 | 0.0027127 | -0.010822 | -0.0027125 | 4.3593e-07 | 2.2171e-07 | 0.01621 | 0.01621 | 0.01621 | 0.99349 | -0.12422 | 0.99345 | -0.12507 | 4.4532
12 | -0.01385 | -0.0034734 | 0.01386 | 0.0034791 | 1.0163e-05 | 5.7578e-06 | 0.02121 | 0.02121 | 0.02121 | 0.97168 | -0.54587 | 0.97246 | -0.53048 | 5.827
13 | 0.01385 | 0.0034734 | -0.013846 | -0.0034711 | 3.9581e-06 | 2.2427e-06 | 0.02121 | 0.021211 | 0.021211 | 0.97168 | -0.54587 | 0.97138 | -0.55187 | 5.8271
14 | -0.046862 | -0.011766 | 0.046881 | 0.011778 | 1.9279e-05 | 1.2215e-05 | 0.071713 | 0.071713 | 0.071713 | 0.97246 | -0.53048 | 0.9729 | -0.52186 | 19.7015
15 | 0.033002 | 0.0082865 | -0.032983 | -0.008275 | 1.8402e-05 | 1.1539e-05 | 0.050503 | 0.050503 | 0.050503 | 0.97246 | -0.53048 | 0.97187 | -0.54218 | 13.8745
16 | 0.010905 | 0.0027341 | -0.010903 | -0.0027331 | 1.9842e-06 | 1.0352e-06 | 0.016706 | 0.016706 | 0.016706 | 0.97138 | -0.55187 | 0.97119 | -0.55569 | 4.5896
17 | -0.032518 | -0.0081612 | 0.032524 | 0.008165 | 6.1985e-06 | 3.8763e-06 | 0.048635 | 0.048635 | 0.048635 | 0.99498 | -0.09544 | 0.99519 | -0.091444 | 13.3613
18 | 0.0099141 | 0.0024849 | -0.0099124 | -0.0024841 | 1.6628e-06 | 8.0386e-07 | 0.01485 | 0.01485 | 0.01485 | 0.99345 | -0.12507 | 0.99327 | -0.12859 | 4.0796
19 | 0.013022 | 0.0032545 | -0.013021 | -0.0032538 | 1.2448e-06 | 6.829e-07 | 0.019469 | 0.019469 | 0.019469 | 0.99516 | -0.092346 | 0.99505 | -0.094357 | 5.3485
20 | -0.013022 | -0.0032545 | 0.013023 | 0.003255 | 1.0037e-06 | 5.506e-07 | 0.019469 | 0.019469 | 0.019469 | 0.99516 | -0.092346 | 0.99524 | -0.090725 | 5.3485
21 | 0.007541 | 0.0018814 | -0.0075381 | -0.0018803 | 2.8787e-06 | 1.0582e-06 | 0.011274 | 0.011274 | 0.011274 | 0.99505 | -0.094357 | 0.99464 | -0.1024 | 3.0973
22 | 0.0054802 | 0.0013724 | -0.0054798 | -0.0013724 | 4.0441e-07 | 5.0238e-08 | 0.0081948 | 0.0081948 | 0.0081948 | 0.99505 | -0.094357 | 0.99497 | -0.095907 | 2.2513
23 | -0.014557 | -0.0036395 | 0.014561 | 0.0036416 | 3.6199e-06 | 2.0518e-06 | 0.021762 | 0.021762 | 0.021762 | 0.99524 | -0.090725 | 0.99551 | -0.085497 | 5.9786
24 | 0.0056712 | 0.0014124 | -0.0056694 | -0.0014122 | 1.7693e-06 | 2.8146e-07 | 0.0084815 | 0.0084818 | 0.0084818 | 0.9946 | -0.10306 | 0.99427 | -0.10964 | 2.3302
25 | -0.0056712 | -0.0014124 | 0.0056714 | 0.0014125 | 1.7675e-07 | 2.8081e-08 | 0.0084815 | 0.0084814 | 0.0084815 | 0.9946 | -0.10306 | 0.99464 | -0.1024 | 2.3301
26 | 0.004033 | 0.0010021 | -0.0040324 | -0.0010022 | 5.9058e-07 | -1.8314e-07 | 0.0060328 | 0.006033 | 0.006033 | 0.99427 | -0.10964 | 0.99411 | -0.11273 | 1.6574
27 | -0.0024083 | -0.00059578 | 0.0024085 | 0.00059524 | 2.6547e-07 | -5.3729e-07 | 0.0036025 | 0.0036022 | 0.0036025 | 0.99399 | -0.11507 | 0.99411 | -0.11273 | 0.98969
28 | 0.0024083 | 0.00059578 | -0.0024082 | -0.000596 | 1.099e-07 | -2.2234e-07 | 0.0036025 | 0.0036026 | 0.0036026 | 0.99399 | -0.11507 | 0.99394 | -0.11604 | 0.98972
29 | 0.000751 | 0.00018068 | -0.0007509 | -0.00018338 | 1.0065e-07 | -2.6975e-06 | 0.0011217 | 0.0011227 | 0.0011227 | 0.99394 | -0.11604 | 0.99379 | -0.11892 | 0.30842
30 | -0.048299 | -0.012133 | 0.048413 | 0.012206 | 0.00011409 | 7.2326e-05 | 0.073882 | 0.073881 | 0.073882 | 0.9729 | -0.52186 | 0.97541 | -0.47249 | 20.2972
31 | 0.0052081 | 0.001305 | -0.0052077 | -0.0013049 | 4.3037e-07 | 5.18e-08 | 0.007974 | 0.0079741 | 0.0079741 | 0.97187 | -0.54218 | 0.97178 | -0.54391 | 2.1907
32 | 0.027775 | 0.00697 | -0.027772 | -0.0069682 | 2.8224e-06 | 1.7548e-06 | 0.042529 | 0.042529 | 0.042529 | 0.97187 | -0.54218 | 0.97176 | -0.54431 | 11.6839
33 | 0.010903 | 0.0027331 | -0.010903 | -0.0027327 | 8.3633e-07 | 4.3638e-07 | 0.016706 | 0.016706 | 0.016706 | 0.97119 | -0.55569 | 0.97111 | -0.5573 | 4.5896
34 | -0.033908 | -0.0085118 | 0.033933 | 0.0085278 | 2.5536e-05 | 1.5998e-05 | 0.050704 | 0.050704 | 0.050704 | 0.99519 | -0.091444 | 0.99601 | -0.075668 | 13.9297
35 | 0.0018149 | 0.00045471 | -0.0018149 | -0.00045486 | 3.5896e-08 | -1.4662e-07 | 0.0027108 | 0.0027109 | 0.0027109 | 0.99623 | -0.071689 | 0.9962 | -0.072104 | 0.74475
36 | -0.0027686 | -0.00069373 | 0.0027687 | 0.00069363 | 7.7389e-08 | -1.076e-07 | 0.0041353 | 0.0041353 | 0.0041353 | 0.99623 | -0.071689 | 0.99626 | -0.071102 | 1.1361
37 | -0.0036006 | -0.00090211 | 0.0036008 | 0.00090198 | 2.3584e-07 | -1.3225e-07 | 0.0053778 | 0.0053777 | 0.0053778 | 0.99626 | -0.071102 | 0.99633 | -0.069727 | 1.4774
38 | -0.004206 | -0.0010536 | 0.004206 | 0.0010536 | 5.746e-08 | -1.38e-08 | 0.0062815 | 0.0062814 | 0.0062815 | 0.99633 | -0.069727 | 0.99634 | -0.06944 | 1.7257
39 | -0.0053808 | -0.0013481 | 0.0053811 | 0.0013481 | 2.9898e-07 | 3.0543e-08 | 0.0080359 | 0.0080359 | 0.0080359 | 0.99634 | -0.06944 | 0.9964 | -0.068273 | 2.2077
40 | 0.097559 | 0.024878 | -0.097462 | -0.024816 | 9.7332e-05 | 6.168e-05 | 0.14713 | 0.14713 | 0.14713 | 0.98772 | -0.23349 | 0.98665 | -0.25418 | 20.2097
41 | -0.097559 | -0.024878 | 0.097716 | 0.024978 | 0.00015755 | 9.9837e-05 | 0.14713 | 0.14713 | 0.14713 | 0.98772 | -0.23349 | 0.98947 | -0.2001 | 20.2097
42 | 0.090051 | 0.022959 | -0.089982 | -0.022915 | 6.9493e-05 | 4.3964e-05 | 0.13595 | 0.13595 | 0.13595 | 0.98665 | -0.25418 | 0.98582 | -0.27018 | 18.6746
43 | -0.099631 | -0.025458 | 0.099663 | 0.025478 | 3.2639e-05 | 2.069e-05 | 0.15001 | 0.15001 | 0.15001 | 0.98947 | -0.2001 | 0.98982 | -0.19333 | 20.6051
44 | -0.0056 | -0.001403 | 0.0056004 | 0.001403 | 3.2091e-07 | 4.5995e-08 | 0.0083628 | 0.0083628 | 0.0083628 | 0.9964 | -0.068273 | 0.99646 | -0.06707 | 2.2975
45 | -0.10072 | -0.025743 | 0.10078 | 0.025785 | 6.6318e-05 | 4.2048e-05 | 0.15159 | 0.15159 | 0.15159 | 0.98982 | -0.19333 | 0.99053 | -0.17973 | 20.8229
46 | -0.10241 | -0.026191 | 0.10241 | 0.026197 | 9.0348e-06 | 5.7299e-06 | 0.15403 | 0.15403 | 0.15403 | 0.99053 | -0.17973 | 0.99063 | -0.1779 | 21.1574
47 | -0.10365 | -0.026506 | 0.10374 | 0.026563 | 8.8507e-05 | 5.6144e-05 | 0.15588 | 0.15588 | 0.15588 | 0.99063 | -0.1779 | 0.99155 | -0.16027 | 21.4124
48 | -0.10531 | -0.026957 | 0.10532 | 0.026958 | 1.7973e-06 | 1.1404e-06 | 0.15825 | 0.15825 | 0.15825 | 0.99155 | -0.16027 | 0.99157 | -0.15992 | 21.7371
49 | 0.0066958 | 0.0016779 | -0.0066943 | -0.0016775 | 1.4887e-06 | 4.5739e-07 | 0.010107 | 0.010107 | 0.010107 | 0.98582 | -0.27018 | 0.98558 | -0.27485 | 2.7766
50 | 0.083286 | 0.021237 | -0.083221 | -0.021196 | 6.5289e-05 | 4.1224e-05 | 0.12584 | 0.12584 | 0.12584 | 0.98582 | -0.27018 | 0.98497 | -0.28643 | 17.2864
51 | -0.10687 | -0.027349 | 0.10698 | 0.027417 | 0.00010733 | 6.8117e-05 | 0.16058 | 0.16058 | 0.16058 | 0.99157 | -0.15992 | 0.99266 | -0.1392 | 22.058
52 | 0.00631 | 0.0015812 | -0.0063097 | -0.0015811 | 3.3824e-07 | 8.9833e-08 | 0.0095267 | 0.0095268 | 0.0095268 | 0.98558 | -0.27485 | 0.98552 | -0.27597 | 2.6172
53 | 0.083221 | 0.021196 | -0.083195 | -0.021179 | 2.6078e-05 | 1.6467e-05 | 0.12584 | 0.12584 | 0.12584 | 0.98497 | -0.28643 | 0.98463 | -0.29293 | 17.2864
54 | 0.0036015 | 0.00090235 | -0.0036013 | -0.00090247 | 2.3468e-07 | -1.1945e-07 | 0.0054378 | 0.0054379 | 0.0054379 | 0.98552 | -0.27597 | 0.98545 | -0.27734 | 1.4939
55 | 0.082599 | 0.02103 | -0.082534 | -0.020989 | 6.433e-05 | 4.0613e-05 | 0.12494 | 0.12494 | 0.12494 | 0.98463 | -0.29293 | 0.9838 | -0.30909 | 17.1627
56 | 0.0028025 | 0.00070226 | -0.0028024 | -0.00070234 | 6.6946e-08 | -8.4165e-08 | 0.0042316 | 0.0042317 | 0.0042317 | 0.98545 | -0.27734 | 0.98542 | -0.27784 | 1.1626
57 | 0.08149 | 0.020708 | -0.081429 | -0.020669 | 6.1195e-05 | 3.8622e-05 | 0.12345 | 0.12345 | 0.12345 | 0.9831 | -0.32262 | 0.98229 | -0.33822 | 16.9569
58 | -0.08149 | -0.020708 | 0.081544 | 0.020741 | 5.3104e-05 | 3.3515e-05 | 0.12345 | 0.12345 | 0.12345 | 0.9831 | -0.32262 | 0.9838 | -0.30909 | 16.9569
59 | 0.079955 | 0.0203 | -0.079903 | -0.020267 | 5.1877e-05 | 3.2725e-05 | 0.12121 | 0.12121 | 0.12121 | 0.98229 | -0.33822 | 0.9816 | -0.35172 | 16.6501
60 | 0.0014746 | 0.00036933 | -0.0014746 | -0.0003695 | 2.7949e-08 | -1.712e-07 | 0.0022337 | 0.0022337 | 0.0022337 | 0.98229 | -0.33822 | 0.98227 | -0.33862 | 0.61367
61 | -0.10846 | -0.027787 | 0.10856 | 0.027854 | 0.00010479 | 6.6519e-05 | 0.1628 | 0.1628 | 0.1628 | 0.99266 | -0.1392 | 0.99371 | -0.11928 | 22.3625
62 | -0.10879 | -0.027911 | 0.1088 | 0.027919 | 1.3076e-05 | 8.3008e-06 | 0.16314 | 0.16314 | 0.16314 | 0.99371 | -0.11928 | 0.99384 | -0.11681 | 22.4092
63 | -0.1104 | -0.028318 | 0.11051 | 0.02839 | 0.00011281 | 7.1631e-05 | 0.16552 | 0.16552 | 0.16552 | 0.99384 | -0.11681 | 0.99494 | -0.095763 | 22.7364
64 | -0.11077 | -0.028456 | 0.11082 | 0.028485 | 4.4571e-05 | 2.8301e-05 | 0.16592 | 0.16592 | 0.16592 | 0.99494 | -0.095763 | 0.99538 | -0.087481 | 22.7911
65 | -0.11082 | -0.028485 | 0.11088 | 0.028525 | 6.3644e-05 | 4.0411e-05 | 0.16592 | 0.16592 | 0.16592 | 0.99538 | -0.087481 | 0.99601 | -0.075668 | 22.7911
66 | -0.14482 | -0.037053 | 0.14491 | 0.037115 | 9.7584e-05 | 6.2165e-05 | 0.21662 | 0.21662 | 0.21662 | 0.99601 | -0.075668 | 0.99674 | -0.061759 | 29.7558
67 | -0.0058314 | -0.0014608 | 0.0058317 | 0.0014609 | 3.5627e-07 | 6.4644e-08 | 0.0087059 | 0.0087058 | 0.0087059 | 0.99667 | -0.063041 | 0.99674 | -0.061759 | 2.3917
68 | 0.0058314 | 0.0014608 | -0.0058303 | -0.0014606 | 1.1187e-06 | 2.0313e-07 | 0.0087059 | 0.0087061 | 0.0087061 | 0.99667 | -0.063041 | 0.99646 | -0.06707 | 2.3918
69 | -0.16963 | -0.043307 | 0.16989 | 0.043471 | 0.00025726 | 0.00016409 | 0.25352 | 0.25352 | 0.25352 | 0.99674 | -0.061759 | 0.99839 | -0.030427 | 34.8237
70 | 0.018883 | 0.004731 | -0.018872 | -0.0047245 | 1.0981e-05 | 6.5479e-06 | 0.028189 | 0.028189 | 0.028189 | 0.99674 | -0.061759 | 0.99611 | -0.073976 | 7.7443
71 | -0.17041 | -0.043603 | 0.17056 | 0.0437 | 0.00015127 | 9.6486e-05 | 0.2543 | 0.2543 | 0.2543 | 0.99839 | -0.030427 | 0.99936 | -0.012108 | 34.9319
72 | 0.01825 | 0.0045687 | -0.018243 | -0.0045644 | 7.196e-06 | 4.2694e-06 | 0.027261 | 0.027261 | 0.027261 | 0.99611 | -0.073976 | 0.99568 | -0.082263 | 7.4893
73 | 0.0061365 | 0.001538 | -0.0061352 | -0.0015376 | 1.3743e-06 | 3.6703e-07 | 0.0094037 | 0.0094038 | 0.0094038 | 0.97104 | -0.5587 | 0.9708 | -0.5634 | 2.5835
74 | -0.010902 | -0.0027323 | 0.010903 | 0.0027327 | 7.273e-07 | 3.795e-07 | 0.016706 | 0.016706 | 0.016706 | 0.97104 | -0.5587 | 0.97111 | -0.5573 | 4.5896
75 | 0.0071142 | 0.0017828 | -0.0071137 | -0.0017826 | 4.8106e-07 | 1.6171e-07 | 0.010658 | 0.010658 | 0.010658 | 0.99327 | -0.12859 | 0.99319 | -0.13001 | 2.928
76 | -0.004176 | -0.0010466 | 0.0041765 | 0.0010465 | 4.8053e-07 | -1.159e-07 | 0.0062575 | 0.0062574 | 0.0062575 | 0.99304 | -0.13301 | 0.99316 | -0.13059 | 1.7191
77 | -0.0057695 | -0.0014457 | 0.0057696 | 0.0014458 | 1.6093e-07 | 2.867e-08 | 0.0086441 | 0.0086441 | 0.0086441 | 0.99316 | -0.13059 | 0.99319 | -0.13001 | 2.3748
78 | -0.081808 | -0.020503 | 0.082018 | 0.020637 | 0.00020997 | 0.00013391 | 0.12374 | 0.12373 | 0.12374 | 0.98381 | -0.31144 | 0.98657 | -0.25771 | 33.9932
79 | -0.082018 | -0.020637 | 0.082152 | 0.020722 | 0.00013396 | 8.5434e-05 | 0.12373 | 0.12373 | 0.12373 | 0.98657 | -0.25771 | 0.98833 | -0.22359 | 33.9931
80 | -0.00075072 | -0.00018815 | 0.00075078 | 0.00018654 | 6.0155e-08 | -1.6058e-06 | 0.0011244 | 0.0011238 | 0.0011244 | 0.99353 | -0.12396 | 0.99362 | -0.12227 | 0.30889
81 | -0.00075078 | -0.00018654 | 0.0007509 | 0.00018338 | 1.1831e-07 | -3.1638e-06 | 0.0011238 | 0.0011227 | 0.0011238 | 0.99362 | -0.12227 | 0.99379 | -0.11892 | 0.30873
82 | 0.0011947 | 0.00029921 | -0.0011947 | -0.00029941 | 1.9717e-08 | -2.013e-07 | 0.0017866 | 0.0017867 | 0.0017867 | 0.99497 | -0.095907 | 0.99496 | -0.096254 | 0.49084
83 | 0.0042851 | 0.0010732 | -0.0042846 | -0.0010733 | 4.6976e-07 | -9.5485e-08 | 0.0064082 | 0.0064084 | 0.0064084 | 0.99497 | -0.095907 | 0.99485 | -0.098209 | 1.7605
84 | -0.015748 | -0.0039391 | 0.015751 | 0.0039405 | 2.4227e-06 | 1.3989e-06 | 0.023537 | 0.023537 | 0.023537 | 0.99551 | -0.085497 | 0.99568 | -0.082263 | 6.4662
85 | -0.0019195 | -0.00048108 | 0.0019196 | 0.00048089 | 6.126e-08 | -1.9396e-07 | 0.0029428 | 0.0029427 | 0.0029428 | 0.97061 | -0.56701 | 0.97065 | -0.56634 | 0.80845
86 | -0.0037147 | -0.00093079 | 0.0037149 | 0.00093074 | 1.2681e-07 | -4.7738e-08 | 0.0056947 | 0.0056946 | 0.0056947 | 0.97065 | -0.56634 | 0.97068 | -0.56563 | 1.5645
87 | -0.001337 | -0.00033509 | 0.001337 | 0.00033506 | 4.9572e-09 | -3.6429e-08 | 0.0020405 | 0.0020405 | 0.0020405 | 0.97504 | -0.47974 | 0.97504 | -0.47967 | 0.56057
88 | 0.01121 | 0.0028098 | -0.011208 | -0.0028089 | 1.735e-06 | 9.1327e-07 | 0.017108 | 0.017108 | 0.017108 | 0.97504 | -0.47967 | 0.97488 | -0.48292 | 4.6999
89 | -0.012547 | -0.0031449 | 0.012551 | 0.0031472 | 4.2895e-06 | 2.356e-06 | 0.019148 | 0.019148 | 0.019148 | 0.97504 | -0.47967 | 0.97541 | -0.47249 | 5.2605
90 | 0.021358 | 0.0053562 | -0.021356 | -0.0053552 | 1.7389e-06 | 1.0593e-06 | 0.032724 | 0.032724 | 0.032724 | 0.97122 | -0.55508 | 0.97113 | -0.55679 | 8.99
91 | -0.022934 | -0.0057513 | 0.022941 | 0.0057558 | 7.363e-06 | 4.5155e-06 | 0.035139 | 0.035139 | 0.035139 | 0.97122 | -0.55508 | 0.97156 | -0.54834 | 9.6535
92 | 0.018714 | 0.004693 | -0.018709 | -0.00469 | 4.9028e-06 | 2.9411e-06 | 0.028675 | 0.028675 | 0.028675 | 0.97113 | -0.55679 | 0.97085 | -0.56229 | 7.8778
93 | -0.024308 | -0.0060982 | 0.024312 | 0.0061011 | 4.675e-06 | 2.8806e-06 | 0.037231 | 0.037231 | 0.037231 | 0.97156 | -0.54834 | 0.97176 | -0.54431 | 10.2283
94 | 0.016846 | 0.0042232 | -0.016844 | -0.0042217 | 2.6816e-06 | 1.5836e-06 | 0.025821 | 0.025821 | 0.025821 | 0.97085 | -0.56229 | 0.97068 | -0.56563 | 7.0936
95 | 0.013129 | 0.0032909 | -0.013126 | -0.0032894 | 2.6798e-06 | 1.497e-06 | 0.020126 | 0.020126 | 0.020126 | 0.97068 | -0.56563 | 0.97047 | -0.56991 | 5.5292
96 | 0.0096974 | 0.0024301 | -0.0096973 | -0.00243 | 1.4107e-07 | 6.9263e-08 | 0.014869 | 0.014869 | 0.014869 | 0.97047 | -0.56991 | 0.97045 | -0.57022 | 4.0849
97 | 0.0038461 | 0.00096369 | -0.0038459 | -0.00096373 | 1.2773e-07 | -3.9925e-08 | 0.0058891 | 0.0058892 | 0.0058892 | 0.97178 | -0.54391 | 0.97175 | -0.54461 | 1.6179
98 | 0.0048432 | 0.0012135 | -0.0048428 | -0.0012135 | 3.5179e-07 | 1.4982e-08 | 0.0074261 | 0.0074261 | 0.0074261 | 0.97045 | -0.57022 | 0.97038 | -0.57174 | 2.0401
99 | 0.0018502 | 0.00046364 | -0.0018502 | -0.00046371 | 1.8678e-08 | -6.4484e-08 | 0.0028372 | 0.0028372 | 0.0028372 | 0.97038 | -0.57174 | 0.97037 | -0.57195 | 0.77946
100 | 0.0029926 | 0.00074982 | -0.0029925 | -0.0007499 | 8.7184e-08 | -8.0583e-08 | 0.0045889 | 0.004589 | 0.004589 | 0.97038 | -0.57174 | 0.97035 | -0.57235 | 1.2607
101 | -0.002908 | -0.00072861 | 0.0029081 | 0.00072847 | 1.1952e-07 | -1.4218e-07 | 0.00435 | 0.0043499 | 0.00435 | 0.99474 | -0.1004 | 0.99479 | -0.099541 | 1.195
102 | 0.0017523 | 0.00043895 | -0.0017522 | -0.00043915 | 4.452e-08 | -1.9582e-07 | 0.0026211 | 0.0026212 | 0.0026212 | 0.99474 | -0.1004 | 0.99471 | -0.10094 | 0.72011
103 | -0.0036283 | -0.00090897 | 0.0036286 | 0.00090885 | 2.3005e-07 | -1.2319e-07 | 0.0054272 | 0.0054271 | 0.0054272 | 0.99479 | -0.099541 | 0.99485 | -0.098209 | 1.491
104 | 0.0024921 | 0.0006239 | -0.0024919 | -0.00062425 | 1.8931e-07 | -3.5218e-07 | 0.0037242 | 0.0037243 | 0.0037243 | 0.99568 | -0.082263 | 0.9956 | -0.083859 | 1.0232
105 | 0.0024919 | 0.00062425 | -0.0024918 | -0.0006245 | 1.373e-07 | -2.5534e-07 | 0.0037243 | 0.0037245 | 0.0037245 | 0.9956 | -0.083859 | 0.99554 | -0.085015 | 1.0232
106 | -0.17168 | -0.043979 | 0.17178 | 0.044043 | 0.00010079 | 6.4292e-05 | 0.25596 | 0.25596 | 0.25596 | 0.99936 | -0.012108 | 1 | 0 | 35.1597
107 | 0.12603 | 0.032188 | -0.1259 | -0.032106 | 0.00012828 | 8.197e-05 | 0.18775 | 0.18775 | 0.18775 | 1 | 0 | 0.99889 | -0.021079 | 51.5802
108 | -0.082152 | -0.020722 | 0.082246 | 0.020783 | 9.4294e-05 | 6.0138e-05 | 0.12373 | 0.12373 | 0.12373 | 0.98833 | -0.22359 | 0.98957 | -0.19964 | 33.9931
109 | -0.10559 | -0.026633 | 0.10574 | 0.026729 | 0.0001508 | 9.6308e-05 | 0.15884 | 0.15884 | 0.15884 | 0.98957 | -0.19964 | 0.99111 | -0.16986 | 43.6366
110 | 0.0057118 | 0.0014315 | -0.0057116 | -0.0014315 | 1.9263e-07 | 3.3269e-08 | 0.0085755 | 0.0085755 | 0.0085755 | 0.99111 | -0.16986 | 0.99107 | -0.17057 | 2.3559
111 | -0.11145 | -0.028161 | 0.1117 | 0.028322 | 0.00025153 | 0.00016067 | 0.16741 | 0.16741 | 0.16741 | 0.99111 | -0.16986 | 0.99355 | -0.1229 | 45.9925
112 | -0.0032964 | -0.00082616 | 0.0032967 | 0.00082593 | 2.8873e-07 | -2.2421e-07 | 0.0049374 | 0.0049373 | 0.0049374 | 0.99346 | -0.12473 | 0.99355 | -0.1229 | 1.3564
113 | -0.115 | -0.029147 | 0.1151 | 0.029211 | 9.9365e-05 | 6.3478e-05 | 0.17235 | 0.17235 | 0.17235 | 0.99355 | -0.1229 | 0.99449 | -0.10493 | 47.3489
114 | -0.11764 | -0.029847 | 0.11781 | 0.029956 | 0.00017125 | 0.00010941 | 0.17614 | 0.17614 | 0.17614 | 0.99449 | -0.10493 | 0.99607 | -0.07471 | 48.3912
115 | -0.12022 | -0.030631 | 0.12036 | 0.030715 | 0.00013278 | 8.4836e-05 | 0.17949 | 0.17949 | 0.17949 | 0.99768 | -0.043942 | 0.99889 | -0.021079 | 49.3097
116 | 0.12022 | 0.030631 | -0.12005 | -0.030517 | 0.00017818 | 0.00011384 | 0.17949 | 0.17949 | 0.17949 | 0.99768 | -0.043942 | 0.99607 | -0.07471 | 49.3097
117 | 0.001669 | 0.0004182 | -0.001669 | -0.00041829 | 2.0391e-08 | -8.9485e-08 | 0.0025594 | 0.0025594 | 0.0025594 | 0.97035 | -0.57235 | 0.97033 | -0.57261 | 0.70315
118 | 0.0026045 | 0.0006526 | -0.0026045 | -0.0006527 | 6.4988e-08 | -9.338e-08 | 0.0039882 | 0.0039883 | 0.0039883 | 0.97175 | -0.54461 | 0.97172 | -0.54514 | 1.0957
119 | 0.0012431 | 0.00031151 | -0.0012431 | -0.00031155 | 5.0788e-09 | -4.3049e-08 | 0.0019036 | 0.0019036 | 0.0019036 | 0.97172 | -0.54514 | 0.97172 | -0.54522 | 0.52297
120 | -0.07232 | -0.018199 | 0.072395 | 0.018247 | 7.5385e-05 | 4.804e-05 | 0.11035 | 0.11035 | 0.11035 | 0.97541 | -0.47249 | 0.97652 | -0.4507 | 30.3167
121 | 0.011356 | 0.002846 | -0.011353 | -0.0028448 | 2.3705e-06 | 1.2543e-06 | 0.017323 | 0.017323 | 0.017323 | 0.97541 | -0.47249 | 0.97519 | -0.47688 | 4.7592
122 | -0.073792 | -0.018597 | 0.073935 | 0.018688 | 0.00014318 | 9.1258e-05 | 0.11248 | 0.11248 | 0.11248 | 0.97652 | -0.4507 | 0.97859 | -0.41023 | 30.9014
123 | 0.0098351 | 0.0024643 | -0.0098345 | -0.002464 | 5.7865e-07 | 2.8486e-07 | 0.015007 | 0.015007 | 0.015007 | 0.97519 | -0.47688 | 0.97512 | -0.47811 | 4.1228
124 | 0.0079579 | 0.0019943 | -0.0079576 | -0.0019942 | 2.1786e-07 | 9.0336e-08 | 0.012147 | 0.012147 | 0.012147 | 0.97488 | -0.48292 | 0.97485 | -0.48349 | 3.337
125 | -0.074957 | -0.018944 | 0.07499 | 0.018965 | 3.2399e-05 | 2.0652e-05 | 0.11403 | 0.11403 | 0.11403 | 0.97859 | -0.41023 | 0.97905 | -0.40122 | 31.3283
126 | 0.0055383 | 0.0013877 | -0.0055376 | -0.0013876 | 7.2463e-07 | 1.2632e-07 | 0.0084512 | 0.0084514 | 0.0084514 | 0.97512 | -0.47811 | 0.97498 | -0.48086 | 2.3218
127 | 0.0042962 | 0.0010764 | -0.0042959 | -0.0010764 | 3.1944e-07 | -4.2788e-08 | 0.0065558 | 0.0065559 | 0.0065559 | 0.97512 | -0.47811 | 0.97504 | -0.47967 | 1.8011
128 | 0.0058618 | 0.0014689 | -0.0058613 | -0.0014688 | 4.6843e-07 | 1.0527e-07 | 0.0089474 | 0.0089475 | 0.0089475 | 0.97485 | -0.48349 | 0.97477 | -0.48517 | 2.4581
129 | -0.076302 | -0.019294 | 0.076356 | 0.019328 | 5.3773e-05 | 3.4281e-05 | 0.11603 | 0.11603 | 0.11603 | 0.97905 | -0.40122 | 0.9798 | -0.38654 | 31.8762
130 | 0.0013123 | 0.00032861 | -0.0013123 | -0.00032874 | 1.7459e-08 | -1.3601e-07 | 0.0019944 | 0.0019945 | 0.0019945 | 0.97905 | -0.40122 | 0.97904 | -0.4015 | 0.54793
131 | 0.0050188 | 0.0012575 | -0.0050188 | -0.0012575 | 2.6425e-08 | 1.933e-09 | 0.0076595 | 0.0076595 | 0.0076595 | 0.97498 | -0.48086 | 0.97498 | -0.48097 | 2.1043
132 | 0.0021325 | 0.0005342 | -0.0021324 | -0.00053443 | 9.1579e-08 | -2.2898e-07 | 0.0032543 | 0.0032544 | 0.0032544 | 0.97504 | -0.47967 | 0.975 | -0.48057 | 0.89406
133 | -0.0040717 | -0.0010203 | 0.0040718 | 0.0010203 | 8.021e-08 | -1.7676e-08 | 0.0062157 | 0.0062157 | 0.0062157 | 0.97474 | -0.48558 | 0.97477 | -0.48517 | 1.7076
134 | 0.0019821 | 0.00049661 | -0.001982 | -0.00049674 | 4.2151e-08 | -1.2606e-07 | 0.0030257 | 0.0030257 | 0.0030257 | 0.97474 | -0.48558 | 0.97472 | -0.48603 | 0.83125
135 | 0.0050188 | 0.0012575 | -0.0050184 | -0.0012575 | 3.7001e-07 | 2.7087e-08 | 0.0076595 | 0.0076596 | 0.0076596 | 0.97498 | -0.48097 | 0.9749 | -0.48252 | 2.1043
136 | 0.002575 | 0.00064513 | -0.0025749 | -0.00064533 | 1.3173e-07 | -1.9923e-07 | 0.0039302 | 0.0039303 | 0.0039303 | 0.9749 | -0.48252 | 0.97485 | -0.48359 | 1.0798
137 | 0.078905 | 0.020017 | -0.078895 | -0.02001 | 1.0487e-05 | 6.6869e-06 | 0.1197 | 0.1197 | 0.1197 | 0.9816 | -0.35172 | 0.98145 | -0.35448 | 32.8848
138 | 0.00077399 | 0.00019392 | -0.00077399 | -0.00019398 | 2.4143e-09 | -5.7736e-08 | 0.0011725 | 0.0011725 | 0.0011725 | 0.98227 | -0.33862 | 0.98227 | -0.33869 | 0.32211
139 | -0.077322 | -0.01957 | 0.077366 | 0.019598 | 4.3768e-05 | 2.7905e-05 | 0.1175 | 0.1175 | 0.1175 | 0.9798 | -0.38654 | 0.98041 | -0.37476 | 32.2794
140 | 0.00060772 | 0.00015216 | -0.00060772 | -0.00015231 | 3.7642e-09 | -1.4555e-07 | 0.00092361 | 0.00092367 | 0.00092367 | 0.97904 | -0.4015 | 0.97903 | -0.40163 | 0.25375
141 | -0.078091 | -0.01978 | 0.078167 | 0.019828 | 7.6117e-05 | 4.8532e-05 | 0.1186 | 0.1186 | 0.1186 | 0.98041 | -0.37476 | 0.98145 | -0.35448 | 32.5818
142 | 0.0007276 | 0.00018202 | -0.00072758 | -0.00018235 | 1.2069e-08 | -3.2652e-07 | 0.001103 | 0.0011031 | 0.0011031 | 0.98145 | -0.35448 | 0.98144 | -0.35483 | 0.30306

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29946 | 0.076232

## res_load
| p_mw | q_mvar
0 | 0.0030267 | 0.00075857
1 | 0.0021514 | 0.00053919
2 | 0.0025067 | 0.00062824
3 | 0.0020522 | 0.00051433
4 | 0.0029406 | 0.00073699
5 | 0.0052016 | 0.0013036
6 | 0.0067226 | 0.0016848
7 | 0.00090802 | 0.00022757
8 | 0.001534 | 0.00038446
9 | 0.0016364 | 0.00041011
10 | 0.0018667 | 0.00046784
11 | 0.0016239 | 0.00040699
12 | 0.0016571 | 0.00041532
13 | 0.0014177 | 0.00035532
14 | 0.0013837 | 0.00034679
15 | 0.00095371 | 0.00023902
16 | 0.0018149 | 0.00045486
17 | 0.00083187 | 0.00020849
18 | 0.00060514 | 0.00015166
19 | 0.0011748 | 0.00029442
20 | 0.0074102 | 0.0018572
21 | 0.0019144 | 0.0004798
22 | 0.00021894 | 5.4871e-05
23 | 0.001055 | 0.00026441
24 | 0.0016209 | 0.00040623
25 | 0.0012358 | 0.00030972
26 | 0.0015753 | 0.00039481
27 | 0.001557 | 0.00039022
28 | 0.00038428 | 9.6309e-05
29 | 0.0027081 | 0.00067872
30 | 0.00059613 | 0.0001494
31 | 0.00079886 | 0.00020021
32 | 0.00099067 | 0.00024829
33 | 0.0028024 | 0.00070234
34 | 0.001479 | 0.00037067
35 | 0.000227 | 5.6892e-05
36 | 0.0015911 | 0.00039877
37 | 0.00026625 | 6.6729e-05
38 | 0.0002299 | 5.7618e-05
39 | 0.00052832 | 0.00013241
40 | 0.00062154 | 0.00015577
41 | 0.0047654 | 0.0011943
42 | 0.0061352 | 0.0015376
43 | 0.0027982 | 0.0007013
44 | 0.004176 | 0.0010466
45 | 0.001593 | 0.00039925
46 | 0.081808 | 0.020503
47 | 0.00075072 | 0.00018815
48 | 0.0011874 | 0.00029759
49 | 0.0019195 | 0.00048108
50 | 0.0017951 | 0.00044991
51 | 0.0011947 | 0.00029941
52 | 0.001337 | 0.00033509
53 | 0.0015762 | 0.00039504
54 | 0.0026422 | 0.00066221
55 | 0.0013662 | 0.0003424
56 | 0.0018625 | 0.00046679
57 | 0.00346 | 0.00086717
58 | 0.0034287 | 0.00085932
59 | 0.0013616 | 0.00034126
60 | 0.0048541 | 0.0012165
61 | 0.0011557 | 0.00028966
62 | 0.00072022 | 0.00018051
63 | 0.0017522 | 0.00043915
64 | 0.00065604 | 0.00016442
65 | 0.0024918 | 0.0006245
66 | 0.0011143 | 0.00027926
67 | 0.023344 | 0.0058506
68 | 0.0032964 | 0.00082616
69 | 0.0057116 | 0.0014315
70 | 0.0025359 | 0.00063555
71 | 0.0055481 | 0.0013905
72 | 0.0022379 | 0.00056088
73 | 0.0018502 | 0.00046371
74 | 0.0013235 | 0.0003317
75 | 0.001669 | 0.00041829
76 | 0.0012414 | 0.00031113
77 | 0.0013614 | 0.00034119
78 | 0.0012431 | 0.00031155
79 | 0.0013968 | 0.00035008
80 | 0.0015181 | 0.00038047
81 | 0.0032504 | 0.00081463
82 | 0.0010219 | 0.00025611
83 | 0.0020958 | 0.00052527
84 | 0.00051883 | 0.00013003
85 | 0.0021634 | 0.0005422
86 | 0.0020897 | 0.00052372
87 | 0.0017895 | 0.0004485
88 | 0.001982 | 0.00049674
89 | 0.0021324 | 0.00053443
90 | 0.0024434 | 0.00061237
91 | 0.0025749 | 0.00064533
92 | 0.00099741 | 0.00024997
93 | 0.00070056 | 0.00017558
94 | 0.0009664 | 0.0002422
95 | 0.00070456 | 0.00017658
96 | 0.00072535 | 0.00018179
97 | 0.00060772 | 0.00015231
98 | 0.00072758 | 0.00018235
99 | 0.00077399 | 0.00019398
100 | 0.0013441 | 0.00033686

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1