## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2516-1_1_4_node_22 | 0.4 | n |  | TRUE
1 | bus_LV_2516-1_1_4_node_134 | 0.4 | n |  | TRUE
2 | bus_LV_2516-1_1_4_node_135 | 0.4 | n |  | TRUE
3 | bus_LV_2516-1_1_4_node_24 | 0.4 | n |  | TRUE
4 | bus_LV_2516-1_1_4_node_25 | 0.4 | n |  | TRUE
5 | bus_LV_2516-1_1_4_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_2516-1_1_4_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_2516-1_1_4_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_2516-1_1_4_node_59 | 0.4 | n |  | TRUE
9 | bus_LV_2516-1_1_4_node_75 | 0.4 | n |  | TRUE
10 | bus_LV_2516-1_1_4_node_60 | 0.4 | n |  | TRUE
11 | bus_LV_2516-1_1_4_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_2516-1_1_4_node_77 | 0.4 | n |  | TRUE
13 | bus_LV_2516-1_1_4_node_73 | 0.4 | n |  | TRUE
14 | bus_LV_2516-1_1_4_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_2516-1_1_4_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_2516-1_1_4_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_2516-1_1_4_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_2516-1_1_4_node_91 | 0.4 | n |  | TRUE
19 | bus_LV_2516-1_1_4_node_88 | 0.4 | n |  | TRUE
20 | bus_LV_2516-1_1_4_node_126 | 0.4 | n |  | TRUE
21 | bus_LV_2516-1_1_4_node_89 | 0.4 | n |  | TRUE
22 | bus_LV_2516-1_1_4_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_2516-1_1_4_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_2516-1_1_4_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_2516-1_1_4_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_2516-1_1_4_node_38 | 0.4 | n |  | TRUE
27 | bus_LV_2516-1_1_4_node_111 | 0.4 | n |  | TRUE
28 | bus_LV_2516-1_1_4_node_108 | 0.4 | n |  | TRUE
29 | bus_LV_2516-1_1_4_node_128 | 0.4 | n |  | TRUE
30 | bus_LV_2516-1_1_4_node_113 | 0.4 | n |  | TRUE
31 | bus_LV_2516-1_1_4_node_109 | 0.4 | n |  | TRUE
32 | bus_LV_2516-1_1_4_node_145 | 0.4 | n |  | TRUE
33 | bus_LV_2516-1_1_4_node_112 | 0.4 | n |  | TRUE
34 | bus_LV_2516-1_1_4_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_2516-1_1_4_node_40 | 0.4 | n |  | TRUE
36 | bus_LV_2516-1_1_4_node_41 | 0.4 | n |  | TRUE
37 | bus_LV_2516-1_1_4_node_43 | 0.4 | n |  | TRUE
38 | bus_LV_2516-1_1_4_node_90 | 0.4 | n |  | TRUE
39 | bus_LV_2516-1_1_4_node_44 | 0.4 | n |  | TRUE
40 | bus_LV_2516-1_1_4_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_2516-1_1_4_node_46 | 0.4 | n |  | TRUE
42 | bus_LV_2516-1_1_4_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_2516-1_1_4_node_97 | 0.4 | n |  | TRUE
44 | bus_LV_2516-1_1_4_node_104 | 0.4 | n |  | TRUE
45 | bus_LV_2516-1_1_4_node_64 | 0.4 | n |  | TRUE
46 | bus_LV_2516-1_1_4_node_48 | 0.4 | n |  | TRUE
47 | bus_LV_2516-1_1_4_node_49 | 0.4 | n |  | TRUE
48 | bus_LV_2516-1_1_4_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_2516-1_1_4_node_51 | 0.4 | n |  | TRUE
50 | bus_LV_2516-1_1_4_node_124 | 0.4 | n |  | TRUE
51 | bus_LV_2516-1_1_4_node_125 | 0.4 | n |  | TRUE
52 | bus_LV_2516-1_1_4_node_83 | 0.4 | n |  | TRUE
53 | bus_LV_2516-1_1_4_node_115 | 0.4 | n |  | TRUE
54 | bus_LV_2516-1_1_4_node_57 | 0.4 | n |  | TRUE
55 | bus_LV_2516-1_1_4_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_2516-1_1_4_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_2516-1_1_4_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_2516-1_1_4_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_2516-1_1_4_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_2516-1_1_4_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_2516-1_1_4_node_86 | 0.4 | n |  | TRUE
62 | bus_LV_2516-1_1_4_node_71 | 0.4 | n |  | TRUE
63 | bus_LV_2516-1_1_4_node_142 | 0.4 | n |  | TRUE
64 | bus_LV_2516-1_1_4_node_84 | 0.4 | n |  | TRUE
65 | bus_LV_2516-1_1_4_node_72 | 0.4 | n |  | TRUE
66 | bus_LV_2516-1_1_4_node_141 | 0.4 | n |  | TRUE
67 | bus_LV_2516-1_1_4_node_117 | 0.4 | n |  | TRUE
68 | bus_LV_2516-1_1_4_node_116 | 0.4 | n |  | TRUE
69 | bus_LV_2516-1_1_4_node_61 | 0.4 | n |  | TRUE
70 | bus_LV_2516-1_1_4_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_2516-1_1_4_node_63 | 0.4 | n |  | TRUE
72 | bus_LV_2516-1_1_4_node_65 | 0.4 | n |  | TRUE
73 | bus_LV_2516-1_1_4_node_81 | 0.4 | n |  | TRUE
74 | bus_LV_2516-1_1_4_node_82 | 0.4 | n |  | TRUE
75 | bus_LV_2516-1_1_4_node_66 | 0.4 | n |  | TRUE
76 | bus_LV_2516-1_1_4_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_2516-1_1_4_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_2516-1_1_4_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_2516-1_1_4_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_2516-1_1_4_node_98 | 0.4 | n |  | TRUE
81 | bus_LV_2516-1_1_4_node_94 | 0.4 | n |  | TRUE
82 | bus_LV_2516-1_1_4_node_143 | 0.4 | n |  | TRUE
83 | bus_LV_2516-1_1_4_node_137 | 0.4 | n |  | TRUE
84 | bus_LV_2516-1_1_4_node_93 | 0.4 | n |  | TRUE
85 | bus_LV_2516-1_1_4_node_144 | 0.4 | n |  | TRUE
86 | bus_LV_2516-1_1_4_node_99 | 0.4 | n |  | TRUE
87 | bus_LV_2516-1_1_4_node_107 | 0.4 | n |  | TRUE
88 | bus_LV_2516-1_1_4_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_2516-1_1_4_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_2516-1_1_4_node_138 | 0.4 | n |  | TRUE
91 | bus_LV_2516-1_1_4_node_123 | 0.4 | n |  | TRUE
92 | bus_LV_2516-1_1_4_node_105 | 0.4 | n |  | TRUE
93 | bus_LV_2516-1_1_4_node_103 | 0.4 | n |  | TRUE
94 | bus_LV_2516-1_1_4_node_110 | 0.4 | n |  | TRUE
95 | bus_LV_2516-1_1_4_node_78 | 0.4 | n |  | TRUE
96 | bus_LV_2516-1_1_4_node_79 | 0.4 | n |  | TRUE
97 | bus_LV_2516-1_1_4_node_80 | 0.4 | n |  | TRUE
98 | bus_LV_2516-1_1_4_node_120 | 0.4 | n |  | TRUE
99 | bus_LV_2516-1_1_4_node_140 | 0.4 | n |  | TRUE
100 | bus_LV_2516-1_1_4_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_2516-1_1_4_node_87 | 0.4 | n |  | TRUE
102 | bus_LV_2516-1_1_4_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_2516-1_1_4_node_131 | 0.4 | n |  | TRUE
104 | bus_LV_2516-1_1_4_node_127 | 0.4 | n |  | TRUE
105 | bus_LV_2516-1_1_4_node_129 | 0.4 | n |  | TRUE
106 | bus_LV_2516-1_1_4_node_95 | 0.4 | n |  | TRUE
107 | bus_LV_2516-1_1_4_node_96 | 0.4 | n |  | TRUE
108 | bus_LV_2516-1_1_4_node_121 | 0.4 | n |  | TRUE
109 | bus_LV_2516-1_1_4_node_122 | 0.4 | n |  | TRUE
110 | bus_LV_2516-1_1_4_node_147 | 0.4 | n |  | TRUE
111 | bus_LV_2516-1_1_4_node_102 | 0.4 | n |  | TRUE
112 | bus_LV_2516-1_1_4_node_106 | 0.4 | n |  | TRUE
113 | bus_LV_2516-1_1_4_node_100 | 0.4 | n |  | TRUE
114 | bus_LV_2516-1_1_4_node_101 | 0.4 | n |  | TRUE
115 | bus_LV_2516-1_1_4_node_148 | 0.4 | n |  | TRUE
116 | bus_LV_2516-1_1_4_node_114 | 0.4 | n |  | TRUE
117 | bus_LV_2516-1_1_4_node_118 | 0.4 | n |  | TRUE
118 | bus_LV_2516-1_1_4_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_2516-1_1_4_node_133 | 0.4 | n |  | TRUE
120 | bus_LV_2516-1_1_4_node_130 | 0.4 | n |  | TRUE
121 | bus_LV_2516-1_1_4_node_132 | 0.4 | n |  | TRUE
122 | bus_LV_2516-1_1_4_node_136 | 0.4 | n |  | TRUE
123 | bus_LV_2516-1_1_4_node_146 | 0.4 | n |  | TRUE
124 | bus_LV_2516-1_1_4_node_149 | 0.4 | n |  | TRUE
125 | bus_MV_392_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2516-1_1_4_load_22 | 0 | 0.0015875 | 0.00039787 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2516-1_1_4_load_134 | 1 | 0.0013293 | 0.00033315 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2516-1_1_4_load_135 | 2 | 0.00054328 | 0.00013616 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2516-1_1_4_load_24 | 3 | 0.00093115 | 0.00023337 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2516-1_1_4_load_25 | 4 | 0.0032607 | 0.0008172 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2516-1_1_4_load_26 | 5 | 0.00076182 | 0.00019093 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2516-1_1_4_load_27 | 6 | 0.0042686 | 0.0010698 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2516-1_1_4_load_28 | 7 | 0.021097 | 0.0052874 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2516-1_1_4_load_32 | 11 | 0.00072576 | 0.00018189 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2516-1_1_4_load_73 | 13 | 0.0033008 | 0.00082725 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2516-1_1_4_load_29 | 14 | 0.0016125 | 0.00040414 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2516-1_1_4_load_30 | 15 | 0.00088914 | 0.00022284 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2516-1_1_4_load_31 | 16 | 0.002177 | 0.0005456 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2516-1_1_4_load_91 | 18 | 0.0022036 | 0.00055228 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2516-1_1_4_load_88 | 19 | 0.0021999 | 0.00055134 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2516-1_1_4_load_126 | 20 | 0.0044752 | 0.0011216 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2516-1_1_4_load_89 | 21 | 0.00098587 | 0.00024708 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2516-1_1_4_load_34 | 22 | 0.00080437 | 0.00020159 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2516-1_1_4_load_36 | 23 | 0.00090237 | 0.00022615 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2516-1_1_4_load_35 | 24 | 0.0013102 | 0.00032836 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2516-1_1_4_load_111 | 27 | 0.0018504 | 0.00046374 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2516-1_1_4_load_108 | 28 | 0.0009617 | 0.00024102 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2516-1_1_4_load_113 | 30 | 0.0011789 | 0.00029547 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2516-1_1_4_load_109 | 31 | 0.0059239 | 0.0014847 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2516-1_1_4_load_145 | 32 | 0.00082364 | 0.00020642 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2516-1_1_4_load_112 | 33 | 0.0012941 | 0.00032433 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2516-1_1_4_load_39 | 34 | 0.0058788 | 0.0014734 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2516-1_1_4_load_40 | 35 | 0.0013211 | 0.0003311 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2516-1_1_4_load_90 | 38 | 0.0025002 | 0.0006266 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2516-1_1_4_load_44 | 39 | 0.0010715 | 0.00026854 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2516-1_1_4_load_45 | 40 | 0.0014101 | 0.00035341 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2516-1_1_4_load_46 | 41 | 0.00032801 | 8.2207e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2516-1_1_4_load_47 | 42 | 0.00086534 | 0.00021687 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2516-1_1_4_load_64 | 45 | 0.0017031 | 0.00042683 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2516-1_1_4_load_48 | 46 | 0.0014285 | 0.00035801 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2516-1_1_4_load_49 | 47 | 0.0024882 | 0.00062359 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2516-1_1_4_load_50 | 48 | 0.0015655 | 0.00039235 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2516-1_1_4_load_115 | 53 | 0.0017885 | 0.00044824 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2516-1_1_4_load_57 | 54 | 0.001292 | 0.00032381 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2516-1_1_4_load_52 | 55 | 0.00076899 | 0.00019273 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2516-1_1_4_load_53 | 56 | 0.0020208 | 0.00050645 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2516-1_1_4_load_56 | 59 | 0.0013786 | 0.0003455 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2516-1_1_4_load_58 | 60 | 0.0016193 | 0.00040585 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2516-1_1_4_load_86 | 61 | 0.0035021 | 0.00087772 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2516-1_1_4_load_71 | 62 | 0.0029183 | 0.00073139 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2516-1_1_4_load_142 | 63 | 0.00095249 | 0.00023872 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2516-1_1_4_load_84 | 64 | 0.0019133 | 0.00047952 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2516-1_1_4_load_72 | 65 | 0.00077779 | 0.00019493 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2516-1_1_4_load_141 | 66 | 0.0013185 | 0.00033044 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2516-1_1_4_load_117 | 67 | 0.0020181 | 0.00050579 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2516-1_1_4_load_116 | 68 | 0.00092317 | 0.00023137 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2516-1_1_4_load_61 | 69 | 0.0024142 | 0.00060506 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2516-1_1_4_load_62 | 70 | 0.0016269 | 0.00040773 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2516-1_1_4_load_63 | 71 | 0.0032191 | 0.00080679 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2516-1_1_4_load_65 | 72 | 0.0011422 | 0.00028627 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2516-1_1_4_load_81 | 73 | 0.0022403 | 0.00056148 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2516-1_1_4_load_82 | 74 | 0.0013545 | 0.00033948 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2516-1_1_4_load_66 | 75 | 0.00080033 | 0.00020058 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2516-1_1_4_load_67 | 76 | 0.00088652 | 0.00022218 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2516-1_1_4_load_98 | 80 | 0.00083984 | 0.00021048 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2516-1_1_4_load_94 | 81 | 0.0012576 | 0.00031519 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2516-1_1_4_load_143 | 82 | 0.00092821 | 0.00023263 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2516-1_1_4_load_137 | 83 | 0.00084937 | 0.00021287 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2516-1_1_4_load_93 | 84 | 0.0012657 | 0.00031721 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2516-1_1_4_load_99 | 86 | 0.0062696 | 0.0015713 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2516-1_1_4_load_107 | 87 | 0.0013191 | 0.00033059 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2516-1_1_4_load_74 | 88 | 0.0023623 | 0.00059204 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2516-1_1_4_load_76 | 89 | 0.087311 | 0.021882 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2516-1_1_4_load_123 | 91 | 0.0061474 | 0.0015407 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2516-1_1_4_load_105 | 92 | 0.0069608 | 0.0017446 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2516-1_1_4_load_103 | 93 | 0.0039668 | 0.00099418 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2516-1_1_4_load_110 | 94 | 0.010939 | 0.0027416 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2516-1_1_4_load_78 | 95 | 0.030877 | 0.0077384 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2516-1_1_4_load_79 | 96 | 0.014139 | 0.0035434 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2516-1_1_4_load_80 | 97 | 0.01928 | 0.0048321 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2516-1_1_4_load_85 | 100 | 0.002063 | 0.00051705 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2516-1_1_4_load_87 | 101 | 0.0019659 | 0.00049269 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2516-1_1_4_load_92 | 102 | 0.0014231 | 0.00035667 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2516-1_1_4_load_127 | 104 | 0.00095936 | 0.00024044 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2516-1_1_4_load_129 | 105 | 0.0010871 | 0.00027246 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2516-1_1_4_load_95 | 106 | 0.00094043 | 0.0002357 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2516-1_1_4_load_96 | 107 | 0.00084375 | 0.00021146 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2516-1_1_4_load_121 | 108 | 0.00084621 | 0.00021208 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2516-1_1_4_load_122 | 109 | 0.00048396 | 0.00012129 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2516-1_1_4_load_147 | 110 | 0.0011167 | 0.00027987 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2516-1_1_4_load_106 | 112 | 0.0026423 | 0.00066223 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2516-1_1_4_load_100 | 113 | 0.0065758 | 0.0016481 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2516-1_1_4_load_101 | 114 | 0.0072918 | 0.0018275 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2516-1_1_4_load_148 | 115 | 0.025468 | 0.0063828 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2516-1_1_4_load_114 | 116 | 0.0018183 | 0.00045572 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2516-1_1_4_load_119 | 118 | 0.00044823 | 0.00011234 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2516-1_1_4_load_133 | 119 | 0.0016864 | 0.00042266 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2516-1_1_4_load_130 | 120 | 0.0010117 | 0.00025356 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2516-1_1_4_load_132 | 121 | 0.0021847 | 0.00054755 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2516-1_1_4_load_136 | 122 | 0.002416 | 0.0006055 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2516-1_1_4_load_146 | 123 | 0.00088839 | 0.00022265 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2516-1_1_4_load_149 | 124 | 0.00064092 | 0.00016063 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 88 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2516-1_1_4_line_0 |  | 0 | 1 | 0.63155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2516-1_1_4_line_1 |  | 1 | 2 | 0.011692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2516-1_1_4_line_2 |  | 2 | 122 | 0.0022349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2516-1_1_4_line_3 |  | 3 | 4 | 0.0050825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2516-1_1_4_line_4 |  | 3 | 5 | 0.00023672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2516-1_1_4_line_5 |  | 4 | 6 | 0.00095858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2516-1_1_4_line_6 |  | 5 | 7 | 0.023468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2516-1_1_4_line_7 |  | 6 | 8 | 0.05862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2516-1_1_4_line_8 |  | 7 | 9 | 0.011927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2516-1_1_4_line_9 |  | 8 | 10 | 0.003655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2516-1_1_4_line_10 |  | 8 | 11 | 0.0082794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2516-1_1_4_line_11 |  | 9 | 12 | 0.024665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2516-1_1_4_line_12 |  | 9 | 13 | 0.02777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2516-1_1_4_line_13 |  | 10 | 67 | 0.032428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2516-1_1_4_line_14 |  | 11 | 15 | 0.03198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2516-1_1_4_line_15 |  | 12 | 91 | 0.027178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2516-1_1_4_line_16 |  | 12 | 92 | 0.033536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2516-1_1_4_line_17 |  | 13 | 88 | 0.0058524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2516-1_1_4_line_18 |  | 14 | 15 | 0.0034002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_2516-1_1_4_line_19 |  | 14 | 16 | 0.018055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2516-1_1_4_line_20 |  | 16 | 17 | 0.024083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_2516-1_1_4_line_21 |  | 17 | 18 | 0.016004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2516-1_1_4_line_22 |  | 17 | 19 | 0.018958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2516-1_1_4_line_23 |  | 18 | 20 | 0.013099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2516-1_1_4_line_24 |  | 19 | 21 | 0.026989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2516-1_1_4_line_25 |  | 20 | 104 | 0.024984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2516-1_1_4_line_26 |  | 21 | 38 | 0.03397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2516-1_1_4_line_27 |  | 22 | 23 | 0.030961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2516-1_1_4_line_28 |  | 23 | 26 | 0.011973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2516-1_1_4_line_29 |  | 24 | 25 | 0.035542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2516-1_1_4_line_30 |  | 25 | 27 | 0.012163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2516-1_1_4_line_31 |  | 25 | 28 | 0.020157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2516-1_1_4_line_32 |  | 26 | 29 | 0.028898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2516-1_1_4_line_33 |  | 26 | 30 | 0.026336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2516-1_1_4_line_34 |  | 28 | 31 | 0.032321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2516-1_1_4_line_35 |  | 29 | 32 | 0.019998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2516-1_1_4_line_36 |  | 30 | 33 | 0.005354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2516-1_1_4_line_37 |  | 31 | 94 | 0.002266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2516-1_1_4_line_38 |  | 32 | 79 | 0.017964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2516-1_1_4_line_39 |  | 33 | 116 | 0.018879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2516-1_1_4_line_40 |  | 34 | 35 | 0.021712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2516-1_1_4_line_41 |  | 34 | 36 | 0.027715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2516-1_1_4_line_42 |  | 36 | 37 | 0.046647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2516-1_1_4_line_43 |  | 37 | 38 | 0.054496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2516-1_1_4_line_44 |  | 39 | 40 | 0.0061281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2516-1_1_4_line_45 |  | 39 | 41 | 0.0079759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2516-1_1_4_line_46 |  | 41 | 42 | 0.00033081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2516-1_1_4_line_47 |  | 42 | 43 | 0.011955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2516-1_1_4_line_48 |  | 43 | 44 | 0.023523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2516-1_1_4_line_49 |  | 43 | 45 | 0.025756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2516-1_1_4_line_50 |  | 44 | 110 | 0.034284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2516-1_1_4_line_51 |  | 44 | 111 | 0.004168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2516-1_1_4_line_52 |  | 45 | 70 | 0.0034024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2516-1_1_4_line_53 |  | 46 | 47 | 0.00082915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2516-1_1_4_line_54 |  | 46 | 48 | 0.024166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2516-1_1_4_line_55 |  | 47 | 49 | 0.01624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2516-1_1_4_line_56 |  | 49 | 50 | 0.005896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2516-1_1_4_line_57 |  | 49 | 51 | 0.01396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2516-1_1_4_line_58 |  | 50 | 52 | 0.012114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2516-1_1_4_line_59 |  | 50 | 53 | 0.022695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2516-1_1_4_line_60 |  | 51 | 54 | 0.0055427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2516-1_1_4_line_61 |  | 52 | 74 | 0.028668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2516-1_1_4_line_62 |  | 53 | 116 | 0.00805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2516-1_1_4_line_63 |  | 54 | 57 | 0.024403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2516-1_1_4_line_64 |  | 55 | 56 | 0.0032135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2516-1_1_4_line_65 |  | 55 | 57 | 0.026791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2516-1_1_4_line_66 |  | 56 | 58 | 0.0019084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2516-1_1_4_line_67 |  | 57 | 59 | 0.013841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2516-1_1_4_line_68 |  | 57 | 60 | 0.013855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2516-1_1_4_line_69 |  | 58 | 61 | 0.021455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2516-1_1_4_line_70 |  | 59 | 62 | 0.002495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2516-1_1_4_line_71 |  | 60 | 63 | 0.0088574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2516-1_1_4_line_72 |  | 61 | 64 | 0.023132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2516-1_1_4_line_73 |  | 62 | 65 | 0.0047439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2516-1_1_4_line_74 |  | 63 | 66 | 0.020474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2516-1_1_4_line_75 |  | 64 | 100 | 0.0068257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2516-1_1_4_line_76 |  | 65 | 86 | 0.011117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2516-1_1_4_line_77 |  | 66 | 122 | 0.0094164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2516-1_1_4_line_78 |  | 67 | 68 | 0.029653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2516-1_1_4_line_79 |  | 68 | 117 | 0.029119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2516-1_1_4_line_80 |  | 69 | 70 | 0.015015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2516-1_1_4_line_81 |  | 69 | 71 | 0.012789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2516-1_1_4_line_82 |  | 71 | 72 | 0.0076171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2516-1_1_4_line_83 |  | 72 | 73 | 0.014217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2516-1_1_4_line_84 |  | 73 | 74 | 0.013223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2516-1_1_4_line_85 |  | 75 | 76 | 0.010557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2516-1_1_4_line_86 |  | 75 | 77 | 0.014523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2516-1_1_4_line_87 |  | 77 | 78 | 0.035689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2516-1_1_4_line_88 |  | 77 | 79 | 0.015071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2516-1_1_4_line_89 |  | 78 | 80 | 0.016173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2516-1_1_4_line_90 |  | 78 | 81 | 0.00080448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2516-1_1_4_line_91 |  | 79 | 82 | 0.028955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2516-1_1_4_line_92 |  | 80 | 83 | 0.010459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2516-1_1_4_line_93 |  | 81 | 84 | 0.021404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2516-1_1_4_line_94 |  | 82 | 85 | 0.0098783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2516-1_1_4_line_95 |  | 84 | 106 | 0.013013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2516-1_1_4_line_96 |  | 85 | 123 | 0.0085898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2516-1_1_4_line_97 |  | 86 | 87 | 0.008145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2516-1_1_4_line_98 |  | 87 | 112 | 0.018059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2516-1_1_4_line_99 |  | 88 | 89 | 0.040634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_2516-1_1_4_line_100 |  | 89 | 90 | 0.041189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_2516-1_1_4_line_101 |  | 90 | 93 | 0.013154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_2516-1_1_4_line_102 |  | 91 | 94 | 0.0063722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2516-1_1_4_line_103 |  | 93 | 114 | 0.011152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_2516-1_1_4_line_104 |  | 95 | 96 | 0.089292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2516-1_1_4_line_105 |  | 96 | 97 | 0.0044009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2516-1_1_4_line_106 |  | 97 | 98 | 0.26565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_2516-1_1_4_line_107 |  | 98 | 99 | 0.061505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_2516-1_1_4_line_108 |  | 99 | 104 | 0.032915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
109 | LV_2516-1_1_4_line_109 |  | 100 | 101 | 0.010427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2516-1_1_4_line_110 |  | 101 | 102 | 0.060033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2516-1_1_4_line_111 |  | 102 | 103 | 0.018061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2516-1_1_4_line_112 |  | 103 | 105 | 0.015562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2516-1_1_4_line_113 |  | 105 | 120 | 0.025909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2516-1_1_4_line_114 |  | 106 | 107 | 0.016554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2516-1_1_4_line_115 |  | 107 | 108 | 0.01048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2516-1_1_4_line_116 |  | 108 | 109 | 0.00032534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2516-1_1_4_line_117 |  | 110 | 115 | 0.0022472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2516-1_1_4_line_118 |  | 111 | 113 | 0.039679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2516-1_1_4_line_119 |  | 113 | 114 | 0.014349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2516-1_1_4_line_120 |  | 117 | 118 | 0.025532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2516-1_1_4_line_121 |  | 118 | 119 | 0.0065634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2516-1_1_4_line_122 |  | 120 | 121 | 0.0023782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2516-1_1_4_line_123 |  | 123 | 124 | 0.013283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2516-1_1_4_trafo_74 | 0.63 MVA 20/0.4 kV | 125 | 88 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2613260.6289 | 1230093.7054 | 2612668.8829 | 1229873.0513
1 | 2613272.1081 | 1230095.9276 | 2613260.6289 | 1230093.7054
2 | 2613272.1081 | 1230095.9276 | 2613274.3022 | 1230096.3523
3 | 2613459.35 | 1230412.6467 | 2613460.2025 | 1230417.6572
4 | 2613459.3103 | 1230412.4133 | 2613459.35 | 1230412.6467
5 | 2613460.2025 | 1230417.6572 | 2613460.3633 | 1230418.6022
6 | 2613459.3103 | 1230412.4133 | 2613457.8773 | 1230403.9903 | 2613455.4479 | 1230389.2655
7 | 2613482.468 | 1230471.7752 | 2613473.4004 | 1230459.1694 | 2613471.1736 | 1230455.8624 | 2613469.0911 | 1230452.3667 | 2613466.5661 | 1230446.9689 | 2613464.1603 | 1230439.0476 | 2613462.2426 | 1230429.6488 | 2613460.3633 | 1230418.6022
8 | 2613453.5063 | 1230377.4979 | 2613455.4479 | 1230389.2655
9 | 2613484.5364 | 1230474.7928 | 2613482.468 | 1230471.7752
10 | 2613482.468 | 1230471.7752 | 2613485.4629 | 1230470.3589 | 2613487.6682 | 1230469.7746 | 2613490.0469 | 1230469.5132 | 2613490.3385 | 1230469.5308
11 | 2613449.494 | 1230353.1632 | 2613453.5063 | 1230377.4979
12 | 2613453.5063 | 1230377.4979 | 2613460.4005 | 1230376.6241 | 2613463.3087 | 1230376.7196 | 2613466.3893 | 1230377.6048 | 2613470.0058 | 1230379.2917 | 2613474.7678 | 1230380.1808 | 2613478.0247 | 1230380.0992 | 2613480.5939 | 1230379.6223
13 | 2613484.5364 | 1230474.7928 | 2613489.2465 | 1230481.8632 | 2613503.6795 | 1230500.9533
14 | 2613490.3385 | 1230469.5308 | 2613492.9094 | 1230469.6864 | 2613496.9219 | 1230470.407 | 2613521.4021 | 1230476.9059
15 | 2613449.494 | 1230353.1632 | 2613422.6805 | 1230357.6022
16 | 2613449.494 | 1230353.1632 | 2613447.1803 | 1230341.3287 | 2613445.6688 | 1230336.478 | 2613443.7319 | 1230332.2489 | 2613438.0042 | 1230321.9947
17 | 2613480.5939 | 1230379.6223 | 2613482.6998 | 1230379.2315 | 2613486.2318 | 1230378.0943 | 2613486.2318 | 1230378.0943
18 | 2613524.6884 | 1230477.7784 | 2613521.4021 | 1230476.9059
19 | 2613524.6884 | 1230477.7784 | 2613532.149 | 1230479.759 | 2613538.0464 | 1230480.9175 | 2613542.3514 | 1230481.3442
20 | 2613566.4239 | 1230481.5267 | 2613544.475 | 1230481.5546 | 2613542.3514 | 1230481.3442
21 | 2613566.4239 | 1230481.5267 | 2613567.1491 | 1230492.3237 | 2613567.7433 | 1230497.4725 | 2613567.7433 | 1230497.4725
22 | 2613566.4239 | 1230481.5267 | 2613569.7095 | 1230462.8551
23 | 2613567.7433 | 1230497.4725 | 2613568.7942 | 1230501.6441 | 2613570.6996 | 1230506.3512 | 2613572.256 | 1230509.7288
24 | 2613569.7095 | 1230462.8551 | 2613572.4394 | 1230447.3421 | 2613574.8498 | 1230439.8097 | 2613576.1284 | 1230436.7365
25 | 2613572.256 | 1230509.7288 | 2613576.3972 | 1230518.716 | 2613583.2229 | 1230532.1725
26 | 2613594.0836 | 1230408.0129 | 2613592.0447 | 1230412.199 | 2613585.9875 | 1230421.3351 | 2613580.5554 | 1230428.7383 | 2613577.2944 | 1230433.934 | 2613576.1284 | 1230436.7365
27 | 2613323.6965 | 1230268.4809 | 2613320.9345 | 1230264.789 | 2613309.3669 | 1230248.7203 | 2613305.433 | 1230243.4823
28 | 2613298.2433 | 1230233.9089 | 2613305.433 | 1230243.4823
29 | 2613374.4717 | 1230334.0056 | 2613352.5946 | 1230305.9943
30 | 2613381.4997 | 1230324.1599 | 2613380.191 | 1230326.8252 | 2613379.0355 | 1230328.7349 | 2613374.4717 | 1230334.0056
31 | 2613374.4717 | 1230334.0056 | 2613386.8421 | 1230349.9207
32 | 2613293.1281 | 1230262.3479 | 2613294.8244 | 1230252.2456 | 2613297.3381 | 1230239.0544 | 2613298.2433 | 1230233.9089
33 | 2613298.2433 | 1230233.9089 | 2613302.8317 | 1230207.9761
34 | 2613386.8421 | 1230349.9207 | 2613392.4081 | 1230357.0818 | 2613394.2747 | 1230358.9426 | 2613396.0366 | 1230360.214 | 2613397.5272 | 1230360.8399 | 2613399.6244 | 1230361.1782 | 2613402.5182 | 1230360.9401 | 2613414.1584 | 1230359.0131
35 | 2613293.1281 | 1230262.3479 | 2613288.5603 | 1230281.8167
36 | 2613303.7645 | 1230202.704 | 2613302.8317 | 1230207.9761
37 | 2613414.1584 | 1230359.0131 | 2613416.394 | 1230358.643
38 | 2613284.4569 | 1230299.3062 | 2613288.5603 | 1230281.8167
39 | 2613303.7645 | 1230202.704 | 2613307.0538 | 1230184.1134
40 | 2613656.1257 | 1230369.484 | 2613665.9782 | 1230388.8322
41 | 2613643.5494 | 1230344.7872 | 2613656.1257 | 1230369.484
42 | 2613599.0547 | 1230353.8133 | 2613616.8808 | 1230355.1103 | 2613620.7592 | 1230354.8523 | 2613623.6918 | 1230354.2142 | 2613626.284 | 1230353.3529 | 2613629.9839 | 1230351.6826 | 2613633.4036 | 1230350.0005 | 2613643.5494 | 1230344.7872
43 | 2613599.0547 | 1230353.8133 | 2613595.3463 | 1230402.4896 | 2613594.2895 | 1230407.5902 | 2613594.0836 | 1230408.0129
44 | 2613378.5604 | 1230266.9858 | 2613378.5604 | 1230266.9858 | 2613377.4153 | 1230267.5947 | 2613375.8095 | 1230267.6689 | 2613374.5833 | 1230267.2882 | 2613372.927 | 1230266.2787
45 | 2613383.2603 | 1230260.5536 | 2613379.6386 | 1230265.7764 | 2613378.5604 | 1230266.9858
46 | 2613383.2603 | 1230260.5536 | 2613383.4488 | 1230260.2818
47 | 2613390.2614 | 1230250.4577 | 2613383.4488 | 1230260.2818
48 | 2613390.2614 | 1230250.4577 | 2613401.1219 | 1230260.8882 | 2613405.7841 | 1230265.8128 | 2613406.8035 | 1230267.1937
49 | 2613390.2614 | 1230250.4577 | 2613381.1538 | 1230241.9433 | 2613373.4893 | 1230231.5755 | 2613373.2787 | 1230231.2407
50 | 2613406.8035 | 1230267.1937 | 2613393.9518 | 1230298.9777
51 | 2613409.2726 | 1230270.5568 | 2613406.8035 | 1230267.1937
52 | 2613371.4665 | 1230228.3611 | 2613373.2787 | 1230231.2407
53 | 2613297.0152 | 1230144.9733 | 2613297.8303 | 1230145.1254
54 | 2613273.2595 | 1230140.542 | 2613297.0152 | 1230144.9733
55 | 2613313.7948 | 1230148.1034 | 2613297.8303 | 1230145.1254
56 | 2613313.7948 | 1230148.1034 | 2613312.5171 | 1230153.8595
57 | 2613313.7948 | 1230148.1034 | 2613315.3327 | 1230141.1804 | 2613316.0265 | 1230139.1252 | 2613317.1895 | 1230137.2822 | 2613318.6861 | 1230135.251
58 | 2613324.0685 | 1230150.1052 | 2613312.5171 | 1230153.8595
59 | 2613312.5171 | 1230153.8595 | 2613311.9585 | 1230156.3931 | 2613308.4564 | 1230176.1865
60 | 2613318.6861 | 1230135.251 | 2613318.7173 | 1230131.4711 | 2613319.0678 | 1230129.7437
61 | 2613324.0685 | 1230150.1052 | 2613335.632 | 1230171.4994 | 2613337.9515 | 1230175.1784
62 | 2613307.0538 | 1230184.1134 | 2613308.4564 | 1230176.1865
63 | 2613325.9461 | 1230106.35 | 2613319.935 | 1230125.4702 | 2613319.0678 | 1230129.7437
64 | 2613334.1357 | 1230080.8415 | 2613335.118 | 1230077.7818
65 | 2613325.9461 | 1230106.35 | 2613334.1357 | 1230080.8415
66 | 2613335.7014 | 1230075.9647 | 2613335.118 | 1230077.7818
67 | 2613325.9461 | 1230106.35 | 2613339.0059 | 1230110.9351
68 | 2613325.9461 | 1230106.35 | 2613312.3433 | 1230103.7166
69 | 2613335.7014 | 1230075.9647 | 2613342.1471 | 1230055.5007
70 | 2613339.0059 | 1230110.9351 | 2613341.36 | 1230111.7617
71 | 2613303.6473 | 1230102.0332 | 2613312.3433 | 1230103.7166
72 | 2613349.0967 | 1230033.4368 | 2613342.1471 | 1230055.5007
73 | 2613345.836 | 1230113.3332 | 2613341.36 | 1230111.7617
74 | 2613303.6473 | 1230102.0332 | 2613283.547 | 1230098.142
75 | 2613349.0967 | 1230033.4368 | 2613351.1473 | 1230026.9264
76 | 2613356.3251 | 1230117.0158 | 2613345.836 | 1230113.3332
77 | 2613283.547 | 1230098.142 | 2613274.3022 | 1230096.3523
78 | 2613521.5628 | 1230524.607 | 2613503.6795 | 1230500.9533
79 | 2613539.3643 | 1230547.6493 | 2613528.837 | 1230534.2285 | 2613521.5628 | 1230524.607
80 | 2613363.4693 | 1230215.6531 | 2613371.4665 | 1230228.3611
81 | 2613363.4693 | 1230215.6531 | 2613363.127 | 1230215.1091 | 2613356.6488 | 1230204.834
82 | 2613356.6488 | 1230204.834 | 2613352.5864 | 1230198.3907
83 | 2613345.0038 | 1230186.364 | 2613352.5864 | 1230198.3907
84 | 2613345.0038 | 1230186.364 | 2613337.9515 | 1230175.1784
85 | 2613307.8 | 1230313.8612 | 2613318.2034 | 1230315.6582
86 | 2613293.4885 | 1230311.3891 | 2613307.8 | 1230313.8612
87 | 2613314.8817 | 1230339.9983 | 2613293.4885 | 1230311.3891
88 | 2613284.4569 | 1230299.3062 | 2613293.4885 | 1230311.3891
89 | 2613314.8817 | 1230339.9983 | 2613330.877 | 1230342.3906
90 | 2613314.8817 | 1230339.9983 | 2613315.3634 | 1230340.6426
91 | 2613284.4569 | 1230299.3062 | 2613277.1886 | 1230327.3339
92 | 2613330.877 | 1230342.3906 | 2613341.2208 | 1230343.9376
93 | 2613328.1794 | 1230357.7855 | 2613315.3634 | 1230340.6426
94 | 2613274.7089 | 1230336.8959 | 2613277.1886 | 1230327.3339
95 | 2613328.1794 | 1230357.7855 | 2613334.7796 | 1230366.6141 | 2613336.1859 | 1230367.7179 | 2613336.3748 | 1230367.7915
96 | 2613274.7089 | 1230336.8959 | 2613275.5853 | 1230344.6692 | 2613275.5485 | 1230345.4356
97 | 2613356.3251 | 1230117.0158 | 2613364.0102 | 1230119.714
98 | 2613381.052 | 1230125.6898 | 2613374.6102 | 1230123.4356 | 2613364.0102 | 1230119.714
99 | 2613488.5066 | 1230340.2895 | 2613492.6061 | 1230365.9792 | 2613492.5986 | 1230369.2701 | 2613491.7126 | 1230372.57 | 2613489.6759 | 1230375.6339 | 2613486.2318 | 1230378.0943
100 | 2613482.0161 | 1230299.6156 | 2613488.5066 | 1230340.2895
101 | 2613482.0161 | 1230299.6156 | 2613474.8043 | 1230296.8866 | 2613469.7538 | 1230294.8574
102 | 2613422.6805 | 1230357.6022 | 2613416.394 | 1230358.643
103 | 2613459.4056 | 1230290.6996 | 2613469.7538 | 1230294.8574
104 | 2613885.6417 | 1230824.0532 | 2613862.8077 | 1230810.9489 | 2613807.2826 | 1230781.2585
105 | 2613807.2826 | 1230781.2585 | 2613803.4017 | 1230779.1833
106 | 2613592.7971 | 1230617.279 | 2613803.4017 | 1230779.1833
107 | 2613592.7971 | 1230617.279 | 2613603.975 | 1230581.0272 | 2613605.4505 | 1230574.9825 | 2613606.0128 | 1230570.8479 | 2613605.9767 | 1230566.7565 | 2613605.1081 | 1230562.3964 | 2613603.2698 | 1230558.1341
108 | 2613603.2698 | 1230558.1341 | 2613590.4656 | 1230543.574 | 2613584.6233 | 1230534.9333 | 2613583.2229 | 1230532.1725
109 | 2613351.1473 | 1230026.9264 | 2613354.2798 | 1230016.9813
110 | 2613385.5797 | 1229966.9602 | 2613379.7175 | 1229973.6909 | 2613368.9379 | 1229984.362 | 2613363.8151 | 1229992.2442 | 2613359.3542 | 1230002.2179 | 2613355.4133 | 1230013.3824 | 2613354.2798 | 1230016.9813
111 | 2613397.4418 | 1229953.3407 | 2613385.5797 | 1229966.9602
112 | 2613397.4418 | 1229953.3407 | 2613408.894 | 1229963.8779
113 | 2613408.894 | 1229963.8779 | 2613427.9602 | 1229981.4206
114 | 2613352.595 | 1230370.9366 | 2613337.9945 | 1230368.4224 | 2613336.3748 | 1230367.7915
115 | 2613352.595 | 1230370.9366 | 2613362.9231 | 1230372.7151
116 | 2613362.9231 | 1230372.7151 | 2613363.2437 | 1230372.7703
117 | 2613393.1094 | 1230301.061 | 2613393.9518 | 1230298.9777
118 | 2613409.2726 | 1230270.5568 | 2613446.0909 | 1230285.3499
119 | 2613459.4056 | 1230290.6996 | 2613446.0909 | 1230285.3499
120 | 2613539.3643 | 1230547.6493 | 2613556.9628 | 1230529.1518
121 | 2613561.4868 | 1230524.3967 | 2613556.9628 | 1230529.1518
122 | 2613429.7103 | 1229983.0309 | 2613427.9602 | 1229981.4206
123 | 2613273.5313 | 1230358.5357 | 2613274.6648 | 1230353.3056 | 2613275.3868 | 1230348.8045 | 2613275.5485 | 1230345.4356

## bus_geodata
| x | y | coords
0 | 2612668.8829 | 1229873.0513
1 | 2613260.6289 | 1230093.7054
2 | 2613272.1081 | 1230095.9276
3 | 2613459.35 | 1230412.6467
4 | 2613460.2025 | 1230417.6572
5 | 2613459.3103 | 1230412.4133
6 | 2613460.3633 | 1230418.6022
7 | 2613455.4479 | 1230389.2655
8 | 2613482.468 | 1230471.7752
9 | 2613453.5063 | 1230377.4979
10 | 2613484.5364 | 1230474.7928
11 | 2613490.3385 | 1230469.5308
12 | 2613449.494 | 1230353.1632
13 | 2613480.5939 | 1230379.6223
14 | 2613524.6884 | 1230477.7784
15 | 2613521.4021 | 1230476.9059
16 | 2613542.3514 | 1230481.3442
17 | 2613566.4239 | 1230481.5267
18 | 2613567.7433 | 1230497.4725
19 | 2613569.7095 | 1230462.8551
20 | 2613572.256 | 1230509.7288
21 | 2613576.1284 | 1230436.7365
22 | 2613323.6965 | 1230268.4809
23 | 2613305.433 | 1230243.4823
24 | 2613352.5946 | 1230305.9943
25 | 2613374.4717 | 1230334.0056
26 | 2613298.2433 | 1230233.9089
27 | 2613381.4997 | 1230324.1599
28 | 2613386.8421 | 1230349.9207
29 | 2613293.1281 | 1230262.3479
30 | 2613302.8317 | 1230207.9761
31 | 2613414.1584 | 1230359.0131
32 | 2613288.5603 | 1230281.8167
33 | 2613303.7645 | 1230202.704
34 | 2613656.1257 | 1230369.484
35 | 2613665.9782 | 1230388.8322
36 | 2613643.5494 | 1230344.7872
37 | 2613599.0547 | 1230353.8133
38 | 2613594.0836 | 1230408.0129
39 | 2613378.5604 | 1230266.9858
40 | 2613372.927 | 1230266.2787
41 | 2613383.2603 | 1230260.5536
42 | 2613383.4488 | 1230260.2818
43 | 2613390.2614 | 1230250.4577
44 | 2613406.8035 | 1230267.1937
45 | 2613373.2787 | 1230231.2407
46 | 2613297.0152 | 1230144.9733
47 | 2613297.8303 | 1230145.1254
48 | 2613273.2595 | 1230140.542
49 | 2613313.7948 | 1230148.1034
50 | 2613312.5171 | 1230153.8595
51 | 2613318.6861 | 1230135.251
52 | 2613324.0685 | 1230150.1052
53 | 2613308.4564 | 1230176.1865
54 | 2613319.0678 | 1230129.7437
55 | 2613334.1357 | 1230080.8415
56 | 2613335.118 | 1230077.7818
57 | 2613325.9461 | 1230106.35
58 | 2613335.7014 | 1230075.9647
59 | 2613339.0059 | 1230110.9351
60 | 2613312.3433 | 1230103.7166
61 | 2613342.1471 | 1230055.5007
62 | 2613341.36 | 1230111.7617
63 | 2613303.6473 | 1230102.0332
64 | 2613349.0967 | 1230033.4368
65 | 2613345.836 | 1230113.3332
66 | 2613283.547 | 1230098.142
67 | 2613503.6795 | 1230500.9533
68 | 2613521.5628 | 1230524.607
69 | 2613363.4693 | 1230215.6531
70 | 2613371.4665 | 1230228.3611
71 | 2613356.6488 | 1230204.834
72 | 2613352.5864 | 1230198.3907
73 | 2613345.0038 | 1230186.364
74 | 2613337.9515 | 1230175.1784
75 | 2613307.8 | 1230313.8612
76 | 2613318.2034 | 1230315.6582
77 | 2613293.4885 | 1230311.3891
78 | 2613314.8817 | 1230339.9983
79 | 2613284.4569 | 1230299.3062
80 | 2613330.877 | 1230342.3906
81 | 2613315.3634 | 1230340.6426
82 | 2613277.1886 | 1230327.3339
83 | 2613341.2208 | 1230343.9376
84 | 2613328.1794 | 1230357.7855
85 | 2613274.7089 | 1230336.8959
86 | 2613356.3251 | 1230117.0158
87 | 2613364.0102 | 1230119.714
88 | 2613486.2318 | 1230378.0943
89 | 2613488.5066 | 1230340.2895
90 | 2613482.0161 | 1230299.6156
91 | 2613422.6805 | 1230357.6022
92 | 2613438.0042 | 1230321.9947
93 | 2613469.7538 | 1230294.8574
94 | 2613416.394 | 1230358.643
95 | 2613885.6417 | 1230824.0532
96 | 2613807.2826 | 1230781.2585
97 | 2613803.4017 | 1230779.1833
98 | 2613592.7971 | 1230617.279
99 | 2613603.2698 | 1230558.1341
100 | 2613351.1473 | 1230026.9264
101 | 2613354.2798 | 1230016.9813
102 | 2613385.5797 | 1229966.9602
103 | 2613397.4418 | 1229953.3407
104 | 2613583.2229 | 1230532.1725
105 | 2613408.894 | 1229963.8779
106 | 2613336.3748 | 1230367.7915
107 | 2613352.595 | 1230370.9366
108 | 2613362.9231 | 1230372.7151
109 | 2613363.2437 | 1230372.7703
110 | 2613393.9518 | 1230298.9777
111 | 2613409.2726 | 1230270.5568
112 | 2613381.052 | 1230125.6898
113 | 2613446.0909 | 1230285.3499
114 | 2613459.4056 | 1230290.6996
115 | 2613393.1094 | 1230301.061
116 | 2613307.0538 | 1230184.1134
117 | 2613539.3643 | 1230547.6493
118 | 2613556.9628 | 1230529.1518
119 | 2613561.4868 | 1230524.3967
120 | 2613427.9602 | 1229981.4206
121 | 2613429.7103 | 1229983.0309
122 | 2613274.3022 | 1230096.3523
123 | 2613275.5485 | 1230345.4356
124 | 2613273.5313 | 1230358.5357
125 | 2613453.5063 | 1230377.4979

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97099 | -0.56055 | 0.0015875 | 0.00039787
1 | 0.97192 | -0.54192 | 0.0013293 | 0.00033315
2 | 0.97195 | -0.54128 | 0.00054328 | 0.00013616
3 | 0.99568 | -0.082001 | 0.00093115 | 0.00023337
4 | 0.99544 | -0.086599 | 0.0032607 | 0.0008172
5 | 0.99569 | -0.081785 | 0.00076182 | 0.00019093
6 | 0.9954 | -0.087438 | 0.0042686 | 0.0010698
7 | 0.99683 | -0.060237 | 0.021097 | 0.0052874
8 | 0.99281 | -0.13673 | 0 | 0
9 | 0.99752 | -0.047101 | 0 | 0
10 | 0.99279 | -0.13706 | 0 | 0
11 | 0.99246 | -0.14334 | 0.00072576 | 0.00018189
12 | 0.99676 | -0.061844 | 0 | 0
13 | 0.99956 | -0.0083208 | 0.0033008 | 0.00082725
14 | 0.991 | -0.17138 | 0.0016125 | 0.00040414
15 | 0.99114 | -0.16871 | 0.00088914 | 0.00022284
16 | 0.99027 | -0.18534 | 0.002177 | 0.0005456
17 | 0.98932 | -0.20351 | 0 | 0
18 | 0.98879 | -0.21378 | 0.0022036 | 0.00055228
19 | 0.9891 | -0.20787 | 0.0021999 | 0.00055134
20 | 0.98836 | -0.22192 | 0.0044752 | 0.0011216
21 | 0.98883 | -0.21301 | 0.00098587 | 0.00024708
22 | 0.97309 | -0.51885 | 0.00080437 | 0.00020159
23 | 0.97311 | -0.51839 | 0.00090237 | 0.00022615
24 | 0.99572 | -0.081824 | 0.0013102 | 0.00032836
25 | 0.99576 | -0.081005 | 0 | 0
26 | 0.97313 | -0.51801 | 0 | 0
27 | 0.99574 | -0.081401 | 0.0018504 | 0.00046374
28 | 0.99582 | -0.079885 | 0.0009617 | 0.00024102
29 | 0.9728 | -0.52456 | 0 | 0
30 | 0.97348 | -0.51122 | 0.0011789 | 0.00029547
31 | 0.99594 | -0.077542 | 0.0059239 | 0.0014847
32 | 0.97257 | -0.52909 | 0.00082364 | 0.00020642
33 | 0.97355 | -0.50973 | 0.0012941 | 0.00032433
34 | 0.98768 | -0.23546 | 0.0058788 | 0.0014734
35 | 0.98765 | -0.23597 | 0.0013211 | 0.0003311
36 | 0.98786 | -0.23189 | 0 | 0
37 | 0.98817 | -0.22589 | 0 | 0
38 | 0.98853 | -0.21889 | 0.0025002 | 0.0006266
39 | 0.9837 | -0.3115 | 0.0010715 | 0.00026854
40 | 0.98369 | -0.31166 | 0.0014101 | 0.00035341
41 | 0.98372 | -0.31115 | 0.00032801 | 8.2207e-05
42 | 0.98372 | -0.31113 | 0.00086534 | 0.00021687
43 | 0.98376 | -0.31034 | 0 | 0
44 | 0.98567 | -0.27343 | 0 | 0
45 | 0.98175 | -0.34921 | 0.0017031 | 0.00042683
46 | 0.97404 | -0.49999 | 0.0014285 | 0.00035801
47 | 0.97405 | -0.49995 | 0.0024882 | 0.00062359
48 | 0.97401 | -0.50069 | 0.0015655 | 0.00039235
49 | 0.97413 | -0.49831 | 0 | 0
50 | 0.9744 | -0.49292 | 0 | 0
51 | 0.97355 | -0.50969 | 0 | 0
52 | 0.97519 | -0.47738 | 0 | 0
53 | 0.97398 | -0.5013 | 0.0017885 | 0.00044824
54 | 0.97332 | -0.51421 | 0.001292 | 0.00032381
55 | 0.97189 | -0.54242 | 0.00076899 | 0.00019273
56 | 0.97184 | -0.54344 | 0.0020208 | 0.00050645
57 | 0.97234 | -0.53355 | 0 | 0
58 | 0.97182 | -0.54397 | 0 | 0
59 | 0.97215 | -0.53746 | 0.0013786 | 0.0003455
60 | 0.97222 | -0.53605 | 0.0016193 | 0.00040585
61 | 0.97151 | -0.54998 | 0.0035021 | 0.00087772
62 | 0.97211 | -0.5381 | 0.0029183 | 0.00073139
63 | 0.97215 | -0.53739 | 0.00095249 | 0.00023872
64 | 0.97126 | -0.55496 | 0.0019133 | 0.00047952
65 | 0.97206 | -0.53906 | 0.00077779 | 0.00019493
66 | 0.97201 | -0.54011 | 0.0013185 | 0.00033044
67 | 0.99264 | -0.13997 | 0.0020181 | 0.00050579
68 | 0.99256 | -0.14157 | 0.00092317 | 0.00023137
69 | 0.98037 | -0.37608 | 0.0024142 | 0.00060506
70 | 0.9815 | -0.35425 | 0.0016269 | 0.00040773
71 | 0.97944 | -0.39416 | 0.0032191 | 0.00080679
72 | 0.97891 | -0.4045 | 0.0011422 | 0.00028627
73 | 0.97794 | -0.42353 | 0.0022403 | 0.00056148
74 | 0.97706 | -0.44072 | 0.0013545 | 0.00033948
75 | 0.97223 | -0.53585 | 0.00080033 | 0.00020058
76 | 0.97222 | -0.53602 | 0.00088652 | 0.00022218
77 | 0.97225 | -0.5354 | 0 | 0
78 | 0.97201 | -0.54022 | 0 | 0
79 | 0.97238 | -0.53289 | 0 | 0
80 | 0.97198 | -0.54072 | 0.00083984 | 0.00021048
81 | 0.972 | -0.5403 | 0.0012576 | 0.00031519
82 | 0.97231 | -0.5342 | 0.00092821 | 0.00023263
83 | 0.97197 | -0.54089 | 0.00084937 | 0.00021287
84 | 0.97192 | -0.54203 | 0.0012657 | 0.00031721
85 | 0.9723 | -0.53448 | 0 | 0
86 | 0.97196 | -0.54116 | 0.0062696 | 0.0015713
87 | 0.97193 | -0.54176 | 0.0013191 | 0.00033059
88 | 1 | 0 | -0.38864 | -0.098885
89 | 0.9959 | -0.077883 | 0.087311 | 0.021882
90 | 0.99338 | -0.12567 | 0 | 0
91 | 0.99608 | -0.074792 | 0.0061474 | 0.0015407
92 | 0.99654 | -0.065941 | 0.0069608 | 0.0017446
93 | 0.99258 | -0.14099 | 0.0039668 | 0.00099418
94 | 0.99596 | -0.077141 | 0.010939 | 0.0027416
95 | 0.97409 | -0.49979 | 0.030877 | 0.0077384
96 | 0.97665 | -0.44928 | 0.014139 | 0.0035434
97 | 0.97684 | -0.44566 | 0.01928 | 0.0048321
98 | 0.98478 | -0.2909 | 0 | 0
99 | 0.98662 | -0.25542 | 0 | 0
100 | 0.9712 | -0.55619 | 0.002063 | 0.00051705
101 | 0.97112 | -0.55766 | 0.0019659 | 0.00049269
102 | 0.9708 | -0.564 | 0.0014231 | 0.00035667
103 | 0.97073 | -0.56543 | 0 | 0
104 | 0.9876 | -0.23649 | 0.00095936 | 0.00024044
105 | 0.97067 | -0.56667 | 0.0010871 | 0.00027246
106 | 0.97188 | -0.54278 | 0.00094043 | 0.0002357
107 | 0.97184 | -0.54345 | 0.00084375 | 0.00021146
108 | 0.97183 | -0.5437 | 0.00084621 | 0.00021208
109 | 0.97183 | -0.54371 | 0.00048396 | 0.00012129
110 | 0.98484 | -0.28979 | 0.0011167 | 0.00027987
111 | 0.98612 | -0.26492 | 0 | 0
112 | 0.97188 | -0.54264 | 0.0026423 | 0.00066223
113 | 0.99031 | -0.18427 | 0.0065758 | 0.0016481
114 | 0.99192 | -0.1536 | 0.0072918 | 0.0018275
115 | 0.98478 | -0.29082 | 0.025468 | 0.0063828
116 | 0.97384 | -0.504 | 0.0018183 | 0.00045572
117 | 0.9925 | -0.14268 | 0 | 0
118 | 0.99245 | -0.14364 | 0.00044823 | 0.00011234
119 | 0.99244 | -0.14384 | 0.0016864 | 0.00042266
120 | 0.97059 | -0.5682 | 0.0010117 | 0.00025356
121 | 0.97059 | -0.5683 | 0.0021847 | 0.00054755
122 | 0.97196 | -0.54114 | 0.002416 | 0.0006055
123 | 0.97229 | -0.53472 | 0.00088839 | 0.00022265
124 | 0.97228 | -0.53488 | 0.00064092 | 0.00016063
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0015875 | -0.00039787 | 0.0015889 | 0.00039095 | 1.4001e-06 | -6.9231e-06 | 0.0024329 | 0.0024301 | 0.0024329 | 0.97099 | -0.56055 | 0.97192 | -0.54192 | 0.66837
1 | -0.0029182 | -0.0007241 | 0.0029183 | 0.00072401 | 8.7418e-08 | -8.8958e-08 | 0.0044652 | 0.0044651 | 0.0044652 | 0.97192 | -0.54192 | 0.97195 | -0.54128 | 1.2267
2 | -0.0034616 | -0.00086017 | 0.0034616 | 0.00086015 | 2.3514e-08 | -1.265e-08 | 0.0052968 | 0.0052968 | 0.0052968 | 0.97195 | -0.54128 | 0.97196 | -0.54114 | 1.4552
3 | 0.10423 | 0.026647 | -0.10421 | -0.026633 | 2.3178e-05 | 1.4702e-05 | 0.15595 | 0.15595 | 0.15595 | 0.99568 | -0.082001 | 0.99544 | -0.086599 | 21.4223
4 | -0.10516 | -0.026881 | 0.10516 | 0.026881 | 1.0989e-06 | 6.9712e-07 | 0.15735 | 0.15735 | 0.15735 | 0.99568 | -0.082001 | 0.99569 | -0.081785 | 21.6134
5 | 0.10095 | 0.025816 | -0.10094 | -0.025813 | 4.1024e-06 | 2.6006e-06 | 0.15108 | 0.15108 | 0.15108 | 0.99544 | -0.086599 | 0.9954 | -0.087438 | 20.7528
6 | -0.10592 | -0.027072 | 0.10603 | 0.027143 | 0.00011052 | 7.0123e-05 | 0.15848 | 0.15848 | 0.15848 | 0.99569 | -0.081785 | 0.99683 | -0.060237 | 21.7698
7 | 0.096673 | 0.024743 | -0.096443 | -0.024597 | 0.00023013 | 0.00014576 | 0.1447 | 0.1447 | 0.1447 | 0.9954 | -0.087438 | 0.99281 | -0.13673 | 19.8763
8 | -0.12713 | -0.03243 | 0.12721 | 0.032481 | 8.0708e-05 | 5.1342e-05 | 0.18998 | 0.18998 | 0.18998 | 0.99683 | -0.060237 | 0.99752 | -0.047101 | 26.0956
9 | 0.0050772 | 0.0012713 | -0.0050771 | -0.0012713 | 7.9361e-08 | 3.5282e-09 | 0.0076093 | 0.0076093 | 0.0076093 | 0.99281 | -0.13673 | 0.99279 | -0.13706 | 2.0905
10 | 0.091366 | 0.023326 | -0.091336 | -0.023308 | 2.9175e-05 | 1.8458e-05 | 0.13709 | 0.13709 | 0.13709 | 0.99281 | -0.13673 | 0.99246 | -0.14334 | 18.8311
11 | 0.034139 | 0.0085711 | -0.034115 | -0.0085561 | 2.3992e-05 | 1.5033e-05 | 0.050931 | 0.050931 | 0.050931 | 0.99752 | -0.047101 | 0.99676 | -0.061844 | 13.992
12 | -0.16135 | -0.041052 | 0.16165 | 0.041245 | 0.00030219 | 0.00019267 | 0.24091 | 0.24091 | 0.24091 | 0.99752 | -0.047101 | 0.99956 | -0.0083208 | 33.0916
13 | 0.0050771 | 0.0012713 | -0.0050764 | -0.0012713 | 7.0412e-07 | 3.1383e-08 | 0.0076093 | 0.0076095 | 0.0076095 | 0.99279 | -0.13706 | 0.99264 | -0.13997 | 2.0905
14 | 0.090611 | 0.023126 | -0.0905 | -0.023056 | 0.00011091 | 7.0159e-05 | 0.136 | 0.136 | 0.136 | 0.99246 | -0.14334 | 0.99114 | -0.16871 | 18.6817
15 | 0.027153 | 0.0068111 | -0.027136 | -0.0068008 | 1.6748e-05 | 1.0365e-05 | 0.040537 | 0.040537 | 0.040537 | 0.99676 | -0.061844 | 0.99608 | -0.074792 | 11.1366
16 | 0.0069622 | 0.001745 | -0.0069608 | -0.0017446 | 1.3586e-06 | 4.3247e-07 | 0.010394 | 0.010394 | 0.010394 | 0.99676 | -0.061844 | 0.99654 | -0.065941 | 2.8554
17 | -0.16495 | -0.042072 | 0.16502 | 0.042115 | 6.6309e-05 | 4.2284e-05 | 0.24582 | 0.24582 | 0.24582 | 0.99956 | -0.0083208 | 1 | 0 | 33.7665
18 | -0.089599 | -0.022825 | 0.089611 | 0.022833 | 1.1562e-05 | 7.312e-06 | 0.13467 | 0.13467 | 0.13467 | 0.991 | -0.17138 | 0.99114 | -0.16871 | 18.4983
19 | 0.087986 | 0.022421 | -0.087927 | -0.022384 | 5.9207e-05 | 3.7427e-05 | 0.13225 | 0.13225 | 0.13225 | 0.991 | -0.17138 | 0.99027 | -0.18534 | 18.1658
20 | 0.08575 | 0.021838 | -0.085675 | -0.021791 | 7.5115e-05 | 4.7455e-05 | 0.12898 | 0.12898 | 0.12898 | 0.99027 | -0.18534 | 0.98932 | -0.20351 | 17.7165
21 | 0.072776 | 0.018555 | -0.072739 | -0.018533 | 3.6029e-05 | 2.2648e-05 | 0.10957 | 0.10957 | 0.10957 | 0.98932 | -0.20351 | 0.98879 | -0.21378 | 15.0513
22 | 0.0129 | 0.0032353 | -0.012897 | -0.0032339 | 2.6765e-06 | 1.4696e-06 | 0.019403 | 0.019403 | 0.019403 | 0.98932 | -0.20351 | 0.9891 | -0.20787 | 5.3305
23 | 0.070536 | 0.01798 | -0.070508 | -0.017963 | 2.773e-05 | 1.7412e-05 | 0.10626 | 0.10626 | 0.10626 | 0.98879 | -0.21378 | 0.98836 | -0.22192 | 14.5958
24 | 0.010697 | 0.0026825 | -0.010694 | -0.0026812 | 2.6213e-06 | 1.3313e-06 | 0.016093 | 0.016094 | 0.016094 | 0.9891 | -0.20787 | 0.98883 | -0.21301 | 4.4213
25 | 0.066033 | 0.016841 | -0.065987 | -0.016812 | 4.6396e-05 | 2.9054e-05 | 0.09952 | 0.09952 | 0.09952 | 0.98836 | -0.22192 | 0.9876 | -0.23649 | 13.6703
26 | 0.0097086 | 0.0024341 | -0.0097058 | -0.0024328 | 2.7191e-06 | 1.3046e-06 | 0.01461 | 0.01461 | 0.01461 | 0.98883 | -0.21301 | 0.98853 | -0.21889 | 4.0138
27 | -0.00080437 | -0.00020159 | 0.00080438 | 0.00020122 | 1.7564e-08 | -3.7338e-07 | 0.00123 | 0.0012299 | 0.00123 | 0.97309 | -0.51885 | 0.97311 | -0.51839 | 0.33792
28 | -0.0017068 | -0.00042737 | 0.0017068 | 0.00042725 | 3.0577e-08 | -1.2917e-07 | 0.0026097 | 0.0026097 | 0.0026097 | 0.97311 | -0.51839 | 0.97313 | -0.51801 | 0.71695
29 | -0.0013102 | -0.00032836 | 0.0013102 | 0.00032793 | 5.1089e-08 | -4.2963e-07 | 0.0019579 | 0.0019578 | 0.0019579 | 0.99572 | -0.081824 | 0.99576 | -0.081005 | 0.53789
30 | 0.0018504 | 0.00046361 | -0.0018504 | -0.00046374 | 3.4873e-08 | -1.359e-07 | 0.0027651 | 0.0027651 | 0.0027651 | 0.99576 | -0.081005 | 0.99574 | -0.081401 | 0.75965
31 | -0.0031606 | -0.00079153 | 0.0031608 | 0.00079138 | 1.686e-07 | -1.5432e-07 | 0.0047228 | 0.0047227 | 0.0047228 | 0.99576 | -0.081005 | 0.99582 | -0.079885 | 1.2975
32 | 0.012307 | 0.0030856 | -0.012303 | -0.0030835 | 3.838e-06 | 2.0974e-06 | 0.018819 | 0.018819 | 0.018819 | 0.97313 | -0.51801 | 0.9728 | -0.52456 | 5.1701
33 | -0.014014 | -0.0035128 | 0.014018 | 0.0035154 | 4.5349e-06 | 2.575e-06 | 0.021429 | 0.021429 | 0.021429 | 0.97313 | -0.51801 | 0.97348 | -0.51122 | 5.887
34 | -0.0041225 | -0.0010324 | 0.0041229 | 0.0010323 | 4.5987e-07 | -1.2623e-07 | 0.0061598 | 0.0061596 | 0.0061598 | 0.99582 | -0.079885 | 0.99594 | -0.077542 | 1.6922
35 | 0.012303 | 0.0030835 | -0.012301 | -0.003082 | 2.6559e-06 | 1.4516e-06 | 0.018819 | 0.018819 | 0.018819 | 0.9728 | -0.52456 | 0.97257 | -0.52909 | 5.1702
36 | -0.015197 | -0.0038109 | 0.015198 | 0.0038115 | 1.0835e-06 | 6.2688e-07 | 0.023231 | 0.023231 | 0.023231 | 0.97348 | -0.51122 | 0.97355 | -0.50973 | 6.3821
37 | -0.010047 | -0.0025169 | 0.010047 | 0.002517 | 1.9146e-07 | 9.3045e-08 | 0.01501 | 0.01501 | 0.01501 | 0.99594 | -0.077542 | 0.99596 | -0.077141 | 4.1237
38 | 0.011477 | 0.0028756 | -0.011475 | -0.0028745 | 2.0771e-06 | 1.1065e-06 | 0.017559 | 0.017559 | 0.017559 | 0.97257 | -0.52909 | 0.97238 | -0.53289 | 4.824
39 | -0.016493 | -0.0041358 | 0.016497 | 0.0041385 | 4.499e-06 | 2.6445e-06 | 0.025209 | 0.025209 | 0.025209 | 0.97355 | -0.50973 | 0.97384 | -0.504 | 6.9255
40 | 0.0013211 | 0.00033085 | -0.0013211 | -0.0003311 | 3.2256e-08 | -2.5722e-07 | 0.0019903 | 0.0019904 | 0.0019904 | 0.98768 | -0.23546 | 0.98765 | -0.23597 | 0.54682
41 | -0.0072 | -0.0018042 | 0.0072012 | 0.0018046 | 1.2228e-06 | 4.2787e-07 | 0.010847 | 0.010847 | 0.010847 | 0.98768 | -0.23546 | 0.98786 | -0.23189 | 2.98
42 | -0.0072012 | -0.0018046 | 0.0072033 | 0.0018054 | 2.0581e-06 | 7.1982e-07 | 0.010847 | 0.010847 | 0.010847 | 0.98786 | -0.23189 | 0.98817 | -0.22589 | 2.98
43 | -0.0072033 | -0.0018054 | 0.0072057 | 0.0018062 | 2.4044e-06 | 8.404e-07 | 0.010847 | 0.010847 | 0.010847 | 0.98817 | -0.22589 | 0.98853 | -0.21889 | 2.9799
44 | 0.0014101 | 0.00035334 | -0.0014101 | -0.00035341 | 1.0456e-08 | -7.1105e-08 | 0.002133 | 0.0021331 | 0.0021331 | 0.9837 | -0.3115 | 0.98369 | -0.31166 | 0.58601
45 | -0.0024816 | -0.00062188 | 0.0024817 | 0.00062181 | 4.2147e-08 | -7.4283e-08 | 0.0037539 | 0.0037538 | 0.0037539 | 0.9837 | -0.3115 | 0.98372 | -0.31115 | 1.0313
46 | -0.0028097 | -0.00070402 | 0.0028097 | 0.00070401 | 2.2403e-09 | -2.7659e-09 | 0.00425 | 0.00425 | 0.00425 | 0.98372 | -0.31115 | 0.98372 | -0.31113 | 1.1676
47 | -0.003675 | -0.00092089 | 0.0036752 | 0.00092082 | 1.3854e-07 | -6.3121e-08 | 0.0055589 | 0.0055589 | 0.0055589 | 0.98372 | -0.31113 | 0.98376 | -0.31034 | 1.5272
48 | -0.088061 | -0.022368 | 0.088218 | 0.022468 | 0.00015676 | 0.00010002 | 0.13331 | 0.13331 | 0.13331 | 0.98376 | -0.31034 | 0.98567 | -0.27343 | 36.6226
49 | 0.084386 | 0.021447 | -0.084228 | -0.021347 | 0.00015762 | 0.00010055 | 0.12775 | 0.12775 | 0.12775 | 0.98376 | -0.31034 | 0.98175 | -0.34921 | 35.0955
50 | 0.026606 | 0.0066763 | -0.026586 | -0.0066634 | 2.0744e-05 | 1.284e-05 | 0.040169 | 0.040169 | 0.040169 | 0.98567 | -0.27343 | 0.98484 | -0.28979 | 11.0354
51 | -0.11482 | -0.029144 | 0.11487 | 0.029174 | 4.7036e-05 | 3.005e-05 | 0.17347 | 0.17347 | 0.17347 | 0.98567 | -0.27343 | 0.98612 | -0.26492 | 47.6579
52 | 0.082525 | 0.02092 | -0.082505 | -0.020907 | 1.9989e-05 | 1.275e-05 | 0.12517 | 0.12517 | 0.12517 | 0.98175 | -0.34921 | 0.9815 | -0.35425 | 34.3864
53 | -0.002994 | -0.0007501 | 0.002994 | 0.00075009 | 6.5046e-09 | -6.1576e-09 | 0.0045738 | 0.0045738 | 0.0045738 | 0.97404 | -0.49999 | 0.97405 | -0.49995 | 1.2565
54 | 0.0015656 | 0.00039208 | -0.0015655 | -0.00039235 | 5.1833e-08 | -2.6761e-07 | 0.0023916 | 0.0023917 | 0.0023917 | 0.97404 | -0.49999 | 0.97401 | -0.50069 | 0.65705
55 | -0.0054822 | -0.0013737 | 0.0054826 | 0.0013738 | 4.2714e-07 | 7.1209e-08 | 0.0083749 | 0.0083748 | 0.0083749 | 0.97405 | -0.49995 | 0.97413 | -0.49831 | 2.3008
56 | -0.04989 | -0.01253 | 0.049903 | 0.012539 | 1.2844e-05 | 8.1468e-06 | 0.076218 | 0.076218 | 0.076218 | 0.97413 | -0.49831 | 0.9744 | -0.49292 | 20.939
57 | 0.044407 | 0.011157 | -0.044383 | -0.011141 | 2.4095e-05 | 1.5247e-05 | 0.067843 | 0.067843 | 0.067843 | 0.97413 | -0.49831 | 0.97355 | -0.50969 | 18.6383
58 | -0.070017 | -0.017587 | 0.070069 | 0.01762 | 5.1949e-05 | 3.3096e-05 | 0.10694 | 0.10694 | 0.10694 | 0.9744 | -0.49292 | 0.97519 | -0.47738 | 29.3784
59 | 0.020114 | 0.0050487 | -0.020106 | -0.0050438 | 8.0314e-06 | 4.8575e-06 | 0.030719 | 0.030719 | 0.030719 | 0.9744 | -0.49292 | 0.97398 | -0.5013 | 8.4394
60 | 0.044383 | 0.011141 | -0.044374 | -0.011135 | 9.5668e-06 | 6.0539e-06 | 0.067843 | 0.067843 | 0.067843 | 0.97355 | -0.50969 | 0.97332 | -0.51421 | 18.6383
61 | -0.070069 | -0.01762 | 0.070192 | 0.017699 | 0.00012294 | 7.8323e-05 | 0.10694 | 0.10694 | 0.10694 | 0.97519 | -0.47738 | 0.97706 | -0.44072 | 29.3784
62 | 0.018318 | 0.0045956 | -0.018315 | -0.0045942 | 2.3645e-06 | 1.4131e-06 | 0.027987 | 0.027987 | 0.027987 | 0.97398 | -0.5013 | 0.97384 | -0.504 | 7.6887
63 | 0.043081 | 0.010812 | -0.043042 | -0.010787 | 3.9704e-05 | 2.5108e-05 | 0.065868 | 0.065868 | 0.065868 | 0.97332 | -0.51421 | 0.97234 | -0.53355 | 18.0957
64 | 0.017184 | 0.004309 | -0.017183 | -0.0043085 | 8.3418e-07 | 4.9405e-07 | 0.02631 | 0.02631 | 0.02631 | 0.97189 | -0.54242 | 0.97184 | -0.54344 | 7.228
65 | -0.017953 | -0.0045017 | 0.01796 | 0.0045062 | 7.5907e-06 | 4.5259e-06 | 0.027487 | 0.027487 | 0.027487 | 0.97189 | -0.54242 | 0.97234 | -0.53355 | 7.5515
66 | 0.015162 | 0.003802 | -0.015162 | -0.0038018 | 3.8573e-07 | 2.2322e-07 | 0.023216 | 0.023216 | 0.023216 | 0.97184 | -0.54344 | 0.97182 | -0.54397 | 6.378
67 | 0.015311 | 0.0038384 | -0.015308 | -0.0038368 | 2.8496e-06 | 1.6521e-06 | 0.023431 | 0.023431 | 0.023431 | 0.97234 | -0.53355 | 0.97215 | -0.53746 | 6.4371
68 | 0.0097707 | 0.0024419 | -0.0097696 | -0.0024413 | 1.1613e-06 | 5.7139e-07 | 0.01495 | 0.01495 | 0.01495 | 0.97234 | -0.53355 | 0.97222 | -0.53605 | 4.1072
69 | 0.015162 | 0.0038018 | -0.015157 | -0.0037993 | 4.3365e-06 | 2.5096e-06 | 0.023216 | 0.023216 | 0.023216 | 0.97182 | -0.54397 | 0.97151 | -0.54998 | 6.3781
70 | 0.013929 | 0.0034913 | -0.013929 | -0.003491 | 4.2531e-07 | 2.4127e-07 | 0.021321 | 0.021321 | 0.021321 | 0.97215 | -0.53746 | 0.97211 | -0.5381 | 5.8574
71 | 0.0081502 | 0.0020354 | -0.0081497 | -0.0020352 | 5.1664e-07 | 2.2082e-07 | 0.012472 | 0.012472 | 0.012472 | 0.97222 | -0.53605 | 0.97215 | -0.53739 | 3.4263
72 | 0.011655 | 0.0029216 | -0.011653 | -0.0029201 | 2.7646e-06 | 1.483e-06 | 0.017852 | 0.017852 | 0.017852 | 0.97151 | -0.54998 | 0.97126 | -0.55496 | 4.9044
73 | 0.011011 | 0.0027597 | -0.01101 | -0.0027594 | 5.0532e-07 | 2.646e-07 | 0.016854 | 0.016854 | 0.016854 | 0.97211 | -0.5381 | 0.97206 | -0.53906 | 4.6302
74 | 0.0071972 | 0.0017965 | -0.0071963 | -0.0017962 | 9.3132e-07 | 3.4224e-07 | 0.011014 | 0.011014 | 0.011014 | 0.97215 | -0.53739 | 0.97201 | -0.54011 | 3.0258
75 | 0.0097393 | 0.0024406 | -0.0097387 | -0.0024403 | 5.6986e-07 | 2.8024e-07 | 0.014921 | 0.014921 | 0.014921 | 0.97126 | -0.55496 | 0.9712 | -0.55619 | 4.0992
76 | 0.010232 | 0.0025645 | -0.010231 | -0.0025639 | 1.0228e-06 | 5.1678e-07 | 0.015663 | 0.015663 | 0.015663 | 0.97206 | -0.53906 | 0.97196 | -0.54116 | 4.3031
77 | 0.0058778 | 0.0014657 | -0.0058776 | -0.0014657 | 2.8574e-07 | 6.616e-08 | 0.0089955 | 0.0089955 | 0.0089955 | 0.97201 | -0.54011 | 0.97196 | -0.54114 | 2.4713
78 | 0.0030583 | 0.00076549 | -0.0030581 | -0.00076572 | 2.3369e-07 | -2.3373e-07 | 0.0045842 | 0.0045843 | 0.0045843 | 0.99264 | -0.13997 | 0.99256 | -0.14157 | 1.2594
79 | 0.0021349 | 0.00053435 | -0.0021348 | -0.00053466 | 1.1184e-07 | -3.0475e-07 | 0.0032003 | 0.0032005 | 0.0032005 | 0.99256 | -0.14157 | 0.9925 | -0.14268 | 0.87925
80 | -0.080794 | -0.020445 | 0.080878 | 0.020499 | 8.477e-05 | 5.4064e-05 | 0.1227 | 0.1227 | 0.1227 | 0.98037 | -0.37608 | 0.9815 | -0.35425 | 33.7088
81 | 0.078379 | 0.01984 | -0.078312 | -0.019797 | 6.7958e-05 | 4.3332e-05 | 0.11904 | 0.11904 | 0.11904 | 0.98037 | -0.37608 | 0.97944 | -0.39416 | 32.7021
82 | 0.075092 | 0.01899 | -0.075055 | -0.018966 | 3.7216e-05 | 2.3723e-05 | 0.11415 | 0.11415 | 0.11415 | 0.97944 | -0.39416 | 0.97891 | -0.4045 | 31.3585
83 | 0.073913 | 0.01868 | -0.073846 | -0.018637 | 6.7368e-05 | 4.2937e-05 | 0.11241 | 0.11241 | 0.11241 | 0.97891 | -0.4045 | 0.97794 | -0.42353 | 30.8816
84 | 0.071605 | 0.018076 | -0.071546 | -0.018038 | 5.8914e-05 | 3.7539e-05 | 0.109 | 0.109 | 0.109 | 0.97794 | -0.42353 | 0.97706 | -0.44072 | 29.9451
85 | 0.00088652 | 0.00022206 | -0.00088652 | -0.00022218 | 7.2885e-09 | -1.2625e-07 | 0.0013568 | 0.0013568 | 0.0013568 | 0.97223 | -0.53585 | 0.97222 | -0.53602 | 0.37276
86 | -0.0016868 | -0.00042264 | 0.0016869 | 0.00042248 | 3.63e-08 | -1.5687e-07 | 0.0025817 | 0.0025816 | 0.0025817 | 0.97223 | -0.53585 | 0.97225 | -0.5354 | 0.70926
87 | 0.0073292 | 0.0018362 | -0.0073275 | -0.0018356 | 1.6839e-06 | 6.3523e-07 | 0.011217 | 0.011217 | 0.011217 | 0.97225 | -0.5354 | 0.97201 | -0.54022 | 3.0816
88 | -0.0090161 | -0.0022587 | 0.0090171 | 0.0022592 | 1.0761e-06 | 5.0176e-07 | 0.013799 | 0.013799 | 0.013799 | 0.97225 | -0.5354 | 0.97238 | -0.53289 | 3.7908
89 | 0.0016893 | 0.00042305 | -0.0016892 | -0.00042323 | 4.0557e-08 | -1.7451e-07 | 0.0025859 | 0.002586 | 0.002586 | 0.97201 | -0.54022 | 0.97198 | -0.54072 | 0.71043
90 | 0.0056382 | 0.0014125 | -0.0056382 | -0.0014125 | 2.2474e-08 | 4.4122e-09 | 0.0086312 | 0.0086312 | 0.0086312 | 0.97201 | -0.54022 | 0.972 | -0.5403 | 2.3712
91 | 0.0024577 | 0.00061529 | -0.0024576 | -0.00061555 | 1.5357e-07 | -2.6086e-07 | 0.0037608 | 0.0037609 | 0.0037609 | 0.97238 | -0.53289 | 0.97231 | -0.5342 | 1.0332
92 | 0.00084937 | 0.00021275 | -0.00084937 | -0.00021287 | 6.6312e-09 | -1.2539e-07 | 0.0013003 | 0.0013003 | 0.0013003 | 0.97198 | -0.54072 | 0.97197 | -0.54089 | 0.35723
93 | 0.0043806 | 0.0010973 | -0.0043802 | -0.0010974 | 3.6095e-07 | -3.4269e-08 | 0.0067059 | 0.006706 | 0.006706 | 0.972 | -0.5403 | 0.97192 | -0.54203 | 1.8423
94 | 0.0015294 | 0.00038292 | -0.0015293 | -0.00038302 | 2.029e-08 | -1.0953e-07 | 0.0023404 | 0.0023404 | 0.0023404 | 0.97231 | -0.5342 | 0.9723 | -0.53448 | 0.64297
95 | 0.0031146 | 0.00078016 | -0.0031144 | -0.00078025 | 1.1096e-07 | -9.0255e-08 | 0.0047683 | 0.0047683 | 0.0047683 | 0.97192 | -0.54203 | 0.97188 | -0.54278 | 1.31
96 | 0.0015293 | 0.00038302 | -0.0015293 | -0.00038312 | 1.7645e-08 | -9.5242e-08 | 0.0023404 | 0.0023405 | 0.0023405 | 0.9723 | -0.53448 | 0.97229 | -0.53472 | 0.64298
97 | 0.0039616 | 0.00099264 | -0.0039615 | -0.00099267 | 1.1235e-07 | -2.904e-08 | 0.0060649 | 0.006065 | 0.006065 | 0.97196 | -0.54116 | 0.97193 | -0.54176 | 1.6662
98 | 0.0026424 | 0.00066208 | -0.0026423 | -0.00066223 | 1.1084e-07 | -1.5286e-07 | 0.0040455 | 0.0040456 | 0.0040456 | 0.97193 | -0.54176 | 0.97188 | -0.54264 | 1.1114
99 | 0.22197 | 0.05677 | -0.22113 | -0.056238 | 0.00083318 | 0.00053218 | 0.33069 | 0.33069 | 0.33069 | 1 | 0 | 0.9959 | -0.077883 | 45.4248
100 | 0.13382 | 0.034356 | -0.13351 | -0.034159 | 0.00030966 | 0.00019711 | 0.20024 | 0.20024 | 0.20024 | 0.9959 | -0.077883 | 0.99338 | -0.12567 | 27.5055
101 | 0.13351 | 0.034159 | -0.13341 | -0.034096 | 9.8891e-05 | 6.295e-05 | 0.20024 | 0.20024 | 0.20024 | 0.99338 | -0.12567 | 0.99258 | -0.14099 | 27.5055
102 | 0.020988 | 0.0052601 | -0.020986 | -0.0052586 | 2.3491e-06 | 1.4205e-06 | 0.031354 | 0.031354 | 0.031354 | 0.99608 | -0.074792 | 0.99596 | -0.077141 | 8.6137
103 | 0.12945 | 0.033102 | -0.12937 | -0.033052 | 7.8937e-05 | 5.0232e-05 | 0.19429 | 0.19429 | 0.19429 | 0.99258 | -0.14099 | 0.99192 | -0.1536 | 26.6887
104 | -0.030877 | -0.0077384 | 0.030951 | 0.007785 | 7.4494e-05 | 4.6561e-05 | 0.047167 | 0.047167 | 0.047167 | 0.97409 | -0.49979 | 0.97665 | -0.44928 | 12.958
105 | -0.04509 | -0.011328 | 0.045097 | 0.011333 | 7.791e-06 | 4.9311e-06 | 0.068708 | 0.068708 | 0.068708 | 0.97665 | -0.44928 | 0.97684 | -0.44566 | 18.8758
106 | -0.064378 | -0.016165 | 0.064857 | 0.016465 | 0.00047911 | 0.00029992 | 0.098078 | 0.098075 | 0.098078 | 0.97684 | -0.44566 | 0.98478 | -0.2909 | 13.4722
107 | -0.064857 | -0.016465 | 0.064968 | 0.016535 | 0.00011092 | 6.9424e-05 | 0.098075 | 0.098075 | 0.098075 | 0.98478 | -0.2909 | 0.98662 | -0.25542 | 13.4719
108 | -0.064968 | -0.016535 | 0.065027 | 0.016572 | 5.9363e-05 | 3.7151e-05 | 0.098075 | 0.098075 | 0.098075 | 0.98662 | -0.25542 | 0.9876 | -0.23649 | 13.4718
109 | 0.0076756 | 0.0019232 | -0.0076751 | -0.001923 | 5.4076e-07 | 2.1707e-07 | 0.01176 | 0.01176 | 0.01176 | 0.9712 | -0.55619 | 0.97112 | -0.55766 | 3.2308
110 | 0.0057092 | 0.0014303 | -0.0057075 | -0.00143 | 1.7228e-06 | 3.6008e-07 | 0.0087479 | 0.0087481 | 0.0087481 | 0.97112 | -0.55766 | 0.9708 | -0.564 | 2.4033
111 | 0.0042844 | 0.0010733 | -0.0042841 | -0.0010733 | 2.9207e-07 | -3.6374e-08 | 0.0065668 | 0.0065669 | 0.0065669 | 0.9708 | -0.564 | 0.97073 | -0.56543 | 1.8041
112 | 0.0042841 | 0.0010733 | -0.0042838 | -0.0010734 | 2.5167e-07 | -3.1311e-08 | 0.0065669 | 0.0065669 | 0.0065669 | 0.97073 | -0.56543 | 0.97067 | -0.56667 | 1.8041
113 | 0.0031967 | 0.00080091 | -0.0031965 | -0.00080108 | 2.3332e-07 | -1.7091e-07 | 0.0049004 | 0.0049005 | 0.0049005 | 0.97067 | -0.56667 | 0.97059 | -0.5682 | 1.3463
114 | 0.002174 | 0.00054455 | -0.0021739 | -0.00054471 | 6.8773e-08 | -1.6111e-07 | 0.0033285 | 0.0033285 | 0.0033285 | 0.97188 | -0.54278 | 0.97184 | -0.54345 | 0.91443
115 | 0.0013302 | 0.00033325 | -0.0013302 | -0.00033337 | 1.6302e-08 | -1.1942e-07 | 0.0020366 | 0.0020367 | 0.0020367 | 0.97184 | -0.54345 | 0.97183 | -0.5437 | 0.55953
116 | 0.00048396 | 0.00012129 | -0.00048396 | -0.00012129 | 6.6745e-11 | -3.9882e-09 | 0.00074101 | 0.00074101 | 0.00074101 | 0.97183 | -0.5437 | 0.97183 | -0.54371 | 0.20357
117 | 0.025469 | 0.0063835 | -0.025468 | -0.0063828 | 1.2479e-06 | 7.7006e-07 | 0.038482 | 0.038482 | 0.038482 | 0.98484 | -0.28979 | 0.98478 | -0.29082 | 10.5719
118 | -0.11487 | -0.029174 | 0.11532 | 0.029461 | 0.00044778 | 0.00028607 | 0.17347 | 0.17347 | 0.17347 | 0.98612 | -0.26492 | 0.99031 | -0.18427 | 47.6579
119 | -0.12189 | -0.031109 | 0.12208 | 0.031224 | 0.0001809 | 0.00011559 | 0.18336 | 0.18336 | 0.18336 | 0.99031 | -0.18427 | 0.99192 | -0.1536 | 50.3723
120 | 0.0021348 | 0.00053466 | -0.0021347 | -0.00053492 | 9.8073e-08 | -2.6717e-07 | 0.0032005 | 0.0032006 | 0.0032006 | 0.9925 | -0.14268 | 0.99245 | -0.14364 | 0.87928
121 | 0.0016865 | 0.00042259 | -0.0016864 | -0.00042266 | 1.5736e-08 | -7.474e-08 | 0.0025285 | 0.0025286 | 0.0025286 | 0.99245 | -0.14364 | 0.99244 | -0.14384 | 0.69466
122 | 0.0021848 | 0.00054753 | -0.0021847 | -0.00054755 | 1.0005e-08 | -2.2989e-08 | 0.0033494 | 0.0033495 | 0.0033495 | 0.97059 | -0.5682 | 0.97059 | -0.5683 | 0.92018
123 | 0.00064092 | 0.00016047 | -0.00064092 | -0.00016063 | 4.7922e-09 | -1.6167e-07 | 0.00098083 | 0.00098089 | 0.00098089 | 0.97229 | -0.53472 | 0.97228 | -0.53488 | 0.26948

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.391 | 0.099477

## res_load
| p_mw | q_mvar
0 | 0.0015875 | 0.00039787
1 | 0.0013293 | 0.00033315
2 | 0.00054328 | 0.00013616
3 | 0.00093115 | 0.00023337
4 | 0.0032607 | 0.0008172
5 | 0.00076182 | 0.00019093
6 | 0.0042686 | 0.0010698
7 | 0.021097 | 0.0052874
8 | 0.00072576 | 0.00018189
9 | 0.0033008 | 0.00082725
10 | 0.0016125 | 0.00040414
11 | 0.00088914 | 0.00022284
12 | 0.002177 | 0.0005456
13 | 0.0022036 | 0.00055228
14 | 0.0021999 | 0.00055134
15 | 0.0044752 | 0.0011216
16 | 0.00098587 | 0.00024708
17 | 0.00080437 | 0.00020159
18 | 0.00090237 | 0.00022615
19 | 0.0013102 | 0.00032836
20 | 0.0018504 | 0.00046374
21 | 0.0009617 | 0.00024102
22 | 0.0011789 | 0.00029547
23 | 0.0059239 | 0.0014847
24 | 0.00082364 | 0.00020642
25 | 0.0012941 | 0.00032433
26 | 0.0058788 | 0.0014734
27 | 0.0013211 | 0.0003311
28 | 0.0025002 | 0.0006266
29 | 0.0010715 | 0.00026854
30 | 0.0014101 | 0.00035341
31 | 0.00032801 | 8.2207e-05
32 | 0.00086534 | 0.00021687
33 | 0.0017031 | 0.00042683
34 | 0.0014285 | 0.00035801
35 | 0.0024882 | 0.00062359
36 | 0.0015655 | 0.00039235
37 | 0.0017885 | 0.00044824
38 | 0.001292 | 0.00032381
39 | 0.00076899 | 0.00019273
40 | 0.0020208 | 0.00050645
41 | 0.0013786 | 0.0003455
42 | 0.0016193 | 0.00040585
43 | 0.0035021 | 0.00087772
44 | 0.0029183 | 0.00073139
45 | 0.00095249 | 0.00023872
46 | 0.0019133 | 0.00047952
47 | 0.00077779 | 0.00019493
48 | 0.0013185 | 0.00033044
49 | 0.0020181 | 0.00050579
50 | 0.00092317 | 0.00023137
51 | 0.0024142 | 0.00060506
52 | 0.0016269 | 0.00040773
53 | 0.0032191 | 0.00080679
54 | 0.0011422 | 0.00028627
55 | 0.0022403 | 0.00056148
56 | 0.0013545 | 0.00033948
57 | 0.00080033 | 0.00020058
58 | 0.00088652 | 0.00022218
59 | 0.00083984 | 0.00021048
60 | 0.0012576 | 0.00031519
61 | 0.00092821 | 0.00023263
62 | 0.00084937 | 0.00021287
63 | 0.0012657 | 0.00031721
64 | 0.0062696 | 0.0015713
65 | 0.0013191 | 0.00033059
66 | 0.0023623 | 0.00059204
67 | 0.087311 | 0.021882
68 | 0.0061474 | 0.0015407
69 | 0.0069608 | 0.0017446
70 | 0.0039668 | 0.00099418
71 | 0.010939 | 0.0027416
72 | 0.030877 | 0.0077384
73 | 0.014139 | 0.0035434
74 | 0.01928 | 0.0048321
75 | 0.002063 | 0.00051705
76 | 0.0019659 | 0.00049269
77 | 0.0014231 | 0.00035667
78 | 0.00095936 | 0.00024044
79 | 0.0010871 | 0.00027246
80 | 0.00094043 | 0.0002357
81 | 0.00084375 | 0.00021146
82 | 0.00084621 | 0.00021208
83 | 0.00048396 | 0.00012129
84 | 0.0011167 | 0.00027987
85 | 0.0026423 | 0.00066223
86 | 0.0065758 | 0.0016481
87 | 0.0072918 | 0.0018275
88 | 0.025468 | 0.0063828
89 | 0.0018183 | 0.00045572
90 | 0.00044823 | 0.00011234
91 | 0.0016864 | 0.00042266
92 | 0.0010117 | 0.00025356
93 | 0.0021847 | 0.00054755
94 | 0.002416 | 0.0006055
95 | 0.00088839 | 0.00022265
96 | 0.00064092 | 0.00016063

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1