## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2516-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2516-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2516-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2516-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2516-5_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2516-5_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2516-5_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2516-5_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2516-5_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2516-5_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_2516-5_0_4_node_78 | 0.4 | n |  | TRUE
11 | bus_LV_2516-5_0_4_node_135 | 0.4 | n |  | TRUE
12 | bus_LV_2516-5_0_4_node_57 | 0.4 | n |  | TRUE
13 | bus_LV_2516-5_0_4_node_180 | 0.4 | n |  | TRUE
14 | bus_LV_2516-5_0_4_node_134 | 0.4 | n |  | TRUE
15 | bus_LV_2516-5_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2516-5_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2516-5_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2516-5_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_2516-5_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2516-5_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2516-5_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_2516-5_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_2516-5_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_2516-5_0_4_node_109 | 0.4 | n |  | TRUE
25 | bus_LV_2516-5_0_4_node_106 | 0.4 | n |  | TRUE
26 | bus_LV_2516-5_0_4_node_195 | 0.4 | n |  | TRUE
27 | bus_LV_2516-5_0_4_node_243 | 0.4 | n |  | TRUE
28 | bus_LV_2516-5_0_4_node_191 | 0.4 | n |  | TRUE
29 | bus_LV_2516-5_0_4_node_104 | 0.4 | n |  | TRUE
30 | bus_LV_2516-5_0_4_node_242 | 0.4 | n |  | TRUE
31 | bus_LV_2516-5_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_2516-5_0_4_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_2516-5_0_4_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_2516-5_0_4_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_2516-5_0_4_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_2516-5_0_4_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_2516-5_0_4_node_36 | 0.4 | n |  | TRUE
38 | bus_LV_2516-5_0_4_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_2516-5_0_4_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_2516-5_0_4_node_75 | 0.4 | n |  | TRUE
41 | bus_LV_2516-5_0_4_node_199 | 0.4 | n |  | TRUE
42 | bus_LV_2516-5_0_4_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_2516-5_0_4_node_190 | 0.4 | n |  | TRUE
44 | bus_LV_2516-5_0_4_node_176 | 0.4 | n |  | TRUE
45 | bus_LV_2516-5_0_4_node_49 | 0.4 | n |  | TRUE
46 | bus_LV_2516-5_0_4_node_253 | 0.4 | n |  | TRUE
47 | bus_LV_2516-5_0_4_node_177 | 0.4 | n |  | TRUE
48 | bus_LV_2516-5_0_4_node_174 | 0.4 | n |  | TRUE
49 | bus_LV_2516-5_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_2516-5_0_4_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_2516-5_0_4_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_2516-5_0_4_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_2516-5_0_4_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_2516-5_0_4_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_2516-5_0_4_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_2516-5_0_4_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_2516-5_0_4_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_2516-5_0_4_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_2516-5_0_4_node_72 | 0.4 | n |  | TRUE
60 | bus_LV_2516-5_0_4_node_206 | 0.4 | n |  | TRUE
61 | bus_LV_2516-5_0_4_node_223 | 0.4 | n |  | TRUE
62 | bus_LV_2516-5_0_4_node_73 | 0.4 | n |  | TRUE
63 | bus_LV_2516-5_0_4_node_74 | 0.4 | n |  | TRUE
64 | bus_LV_2516-5_0_4_node_179 | 0.4 | n |  | TRUE
65 | bus_LV_2516-5_0_4_node_224 | 0.4 | n |  | TRUE
66 | bus_LV_2516-5_0_4_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_2516-5_0_4_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_2516-5_0_4_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_2516-5_0_4_node_54 | 0.4 | n |  | TRUE
70 | bus_LV_2516-5_0_4_node_55 | 0.4 | n |  | TRUE
71 | bus_LV_2516-5_0_4_node_56 | 0.4 | n |  | TRUE
72 | bus_LV_2516-5_0_4_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_2516-5_0_4_node_76 | 0.4 | n |  | TRUE
74 | bus_LV_2516-5_0_4_node_77 | 0.4 | n |  | TRUE
75 | bus_LV_2516-5_0_4_node_130 | 0.4 | n |  | TRUE
76 | bus_LV_2516-5_0_4_node_115 | 0.4 | n |  | TRUE
77 | bus_LV_2516-5_0_4_node_129 | 0.4 | n |  | TRUE
78 | bus_LV_2516-5_0_4_node_194 | 0.4 | n |  | TRUE
79 | bus_LV_2516-5_0_4_node_127 | 0.4 | n |  | TRUE
80 | bus_LV_2516-5_0_4_node_210 | 0.4 | n |  | TRUE
81 | bus_LV_2516-5_0_4_node_128 | 0.4 | n |  | TRUE
82 | bus_LV_2516-5_0_4_node_117 | 0.4 | n |  | TRUE
83 | bus_LV_2516-5_0_4_node_118 | 0.4 | n |  | TRUE
84 | bus_LV_2516-5_0_4_node_113 | 0.4 | n |  | TRUE
85 | bus_LV_2516-5_0_4_node_105 | 0.4 | n |  | TRUE
86 | bus_LV_2516-5_0_4_node_107 | 0.4 | n |  | TRUE
87 | bus_LV_2516-5_0_4_node_108 | 0.4 | n |  | TRUE
88 | bus_LV_2516-5_0_4_node_136 | 0.4 | n |  | TRUE
89 | bus_LV_2516-5_0_4_node_137 | 0.4 | n |  | TRUE
90 | bus_LV_2516-5_0_4_node_248 | 0.4 | n |  | TRUE
91 | bus_LV_2516-5_0_4_node_114 | 0.4 | n |  | TRUE
92 | bus_LV_2516-5_0_4_node_116 | 0.4 | n |  | TRUE
93 | bus_LV_2516-5_0_4_node_119 | 0.4 | n |  | TRUE
94 | bus_LV_2516-5_0_4_node_120 | 0.4 | n |  | TRUE
95 | bus_LV_2516-5_0_4_node_152 | 0.4 | n |  | TRUE
96 | bus_LV_2516-5_0_4_node_168 | 0.4 | n |  | TRUE
97 | bus_LV_2516-5_0_4_node_165 | 0.4 | n |  | TRUE
98 | bus_LV_2516-5_0_4_node_153 | 0.4 | n |  | TRUE
99 | bus_LV_2516-5_0_4_node_164 | 0.4 | n |  | TRUE
100 | bus_LV_2516-5_0_4_node_131 | 0.4 | n |  | TRUE
101 | bus_LV_2516-5_0_4_node_132 | 0.4 | n |  | TRUE
102 | bus_LV_2516-5_0_4_node_133 | 0.4 | n |  | TRUE
103 | bus_LV_2516-5_0_4_node_246 | 0.4 | n |  | TRUE
104 | bus_LV_2516-5_0_4_node_138 | 0.4 | n |  | TRUE
105 | bus_LV_2516-5_0_4_node_139 | 0.4 | n |  | TRUE
106 | bus_LV_2516-5_0_4_node_181 | 0.4 | n |  | TRUE
107 | bus_LV_2516-5_0_4_node_182 | 0.4 | n |  | TRUE
108 | bus_LV_2516-5_0_4_node_183 | 0.4 | n |  | TRUE
109 | bus_LV_2516-5_0_4_node_154 | 0.4 | n |  | TRUE
110 | bus_LV_2516-5_0_4_node_156 | 0.4 | n |  | TRUE
111 | bus_LV_2516-5_0_4_node_155 | 0.4 | n |  | TRUE
112 | bus_LV_2516-5_0_4_node_188 | 0.4 | n |  | TRUE
113 | bus_LV_2516-5_0_4_node_214 | 0.4 | n |  | TRUE
114 | bus_LV_2516-5_0_4_node_189 | 0.4 | n |  | TRUE
115 | bus_LV_2516-5_0_4_node_215 | 0.4 | n |  | TRUE
116 | bus_LV_2516-5_0_4_node_166 | 0.4 | n |  | TRUE
117 | bus_LV_2516-5_0_4_node_167 | 0.4 | n |  | TRUE
118 | bus_LV_2516-5_0_4_node_172 | 0.4 | n |  | TRUE
119 | bus_LV_2516-5_0_4_node_173 | 0.4 | n |  | TRUE
120 | bus_LV_2516-5_0_4_node_175 | 0.4 | n |  | TRUE
121 | bus_LV_2516-5_0_4_node_178 | 0.4 | n |  | TRUE
122 | bus_LV_2516-5_0_4_node_207 | 0.4 | n |  | TRUE
123 | bus_LV_2516-5_0_4_node_217 | 0.4 | n |  | TRUE
124 | bus_LV_2516-5_0_4_node_245 | 0.4 | n |  | TRUE
125 | bus_LV_2516-5_0_4_node_201 | 0.4 | n |  | TRUE
126 | bus_LV_2516-5_0_4_node_202 | 0.4 | n |  | TRUE
127 | bus_LV_2516-5_0_4_node_226 | 0.4 | n |  | TRUE
128 | bus_LV_2516-5_0_4_node_213 | 0.4 | n |  | TRUE
129 | bus_LV_2516-5_0_4_node_211 | 0.4 | n |  | TRUE
130 | bus_LV_2516-5_0_4_node_208 | 0.4 | n |  | TRUE
131 | bus_LV_2516-5_0_4_node_227 | 0.4 | n |  | TRUE
132 | bus_LV_2516-5_0_4_node_209 | 0.4 | n |  | TRUE
133 | bus_LV_2516-5_0_4_node_212 | 0.4 | n |  | TRUE
134 | bus_LV_2516-5_0_4_node_216 | 0.4 | n |  | TRUE
135 | bus_LV_2516-5_0_4_node_225 | 0.4 | n |  | TRUE
136 | bus_LV_2516-5_0_4_node_234 | 0.4 | n |  | TRUE
137 | bus_LV_2516-5_0_4_node_231 | 0.4 | n |  | TRUE
138 | bus_LV_2516-5_0_4_node_236 | 0.4 | n |  | TRUE
139 | bus_LV_2516-5_0_4_node_232 | 0.4 | n |  | TRUE
140 | bus_LV_2516-5_0_4_node_233 | 0.4 | n |  | TRUE
141 | bus_LV_2516-5_0_4_node_249 | 0.4 | n |  | TRUE
142 | bus_LV_2516-5_0_4_node_244 | 0.4 | n |  | TRUE
143 | bus_LV_2516-5_0_4_node_247 | 0.4 | n |  | TRUE
144 | bus_MV_392_0_node_15 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2516-5_0_4_load_0 | 0 | 0.004677 | 0.0011722 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2516-5_0_4_load_1 | 1 | 0.001432 | 0.00035888 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2516-5_0_4_load_4 | 4 | 0.00078649 | 0.00019711 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2516-5_0_4_load_5 | 5 | 0.0015128 | 0.00037915 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2516-5_0_4_load_6 | 6 | 0.0032299 | 0.00080948 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2516-5_0_4_load_7 | 7 | 0.0062826 | 0.0015746 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2516-5_0_4_load_8 | 8 | 0.0022737 | 0.00056985 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2516-5_0_4_load_9 | 9 | 0.0050684 | 0.0012703 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2516-5_0_4_load_78 | 10 | 0.0063224 | 0.0015845 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2516-5_0_4_load_57 | 12 | 0.001631 | 0.00040876 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2516-5_0_4_load_180 | 13 | 0.0055887 | 0.0014006 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2516-5_0_4_load_134 | 14 | 0.0034981 | 0.0008767 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2516-5_0_4_load_10 | 15 | 0.0013694 | 0.0003432 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2516-5_0_4_load_13 | 18 | 0.0013023 | 0.00032639 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2516-5_0_4_load_14 | 19 | 0.0019888 | 0.00049843 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2516-5_0_4_load_15 | 20 | 0.001779 | 0.00044587 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2516-5_0_4_load_18 | 22 | 0.0072242 | 0.0018106 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2516-5_0_4_load_19 | 23 | 0.0014093 | 0.00035321 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2516-5_0_4_load_109 | 24 | 0.0090726 | 0.0022738 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2516-5_0_4_load_106 | 25 | 0.00064807 | 0.00016242 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2516-5_0_4_load_195 | 26 | 0.00017867 | 4.4778e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2516-5_0_4_load_243 | 27 | 0.0019614 | 0.00049158 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2516-5_0_4_load_104 | 29 | 0.00060719 | 0.00015218 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2516-5_0_4_load_242 | 30 | 0.0037298 | 0.00093478 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2516-5_0_4_load_30 | 31 | 0.0048246 | 0.0012092 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2516-5_0_4_load_31 | 32 | 0.00083589 | 0.00020949 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2516-5_0_4_load_33 | 34 | 0.0027729 | 0.00069495 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2516-5_0_4_load_35 | 36 | 0.010141 | 0.0025415 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2516-5_0_4_load_36 | 37 | 0.0079733 | 0.0019983 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2516-5_0_4_load_38 | 39 | 0.0034187 | 0.0008568 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2516-5_0_4_load_75 | 40 | 0.0049452 | 0.0012394 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2516-5_0_4_load_199 | 41 | 0.0071027 | 0.0017801 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2516-5_0_4_load_49 | 45 | 0.010108 | 0.0025334 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2516-5_0_4_load_253 | 46 | 0.012278 | 0.0030771 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2516-5_0_4_load_40 | 49 | 0.0089429 | 0.0022413 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2516-5_0_4_load_43 | 52 | 0.0010112 | 0.00025343 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2516-5_0_4_load_44 | 53 | 0.0012481 | 0.0003128 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2516-5_0_4_load_45 | 54 | 0.001582 | 0.00039647 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2516-5_0_4_load_46 | 55 | 0.0012094 | 0.0003031 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2516-5_0_4_load_47 | 56 | 0.00080022 | 0.00020055 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2516-5_0_4_load_48 | 57 | 0.0016333 | 0.00040934 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2516-5_0_4_load_50 | 58 | 0.0014715 | 0.00036878 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2516-5_0_4_load_206 | 60 | 0.0036335 | 0.00091063 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2516-5_0_4_load_223 | 61 | 0.0014509 | 0.00036363 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2516-5_0_4_load_73 | 62 | 0.0014486 | 0.00036305 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2516-5_0_4_load_74 | 63 | 0.0011673 | 0.00029256 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2516-5_0_4_load_179 | 64 | 0.0069642 | 0.0017454 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2516-5_0_4_load_224 | 65 | 0.0065684 | 0.0016462 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2516-5_0_4_load_51 | 66 | 0.0028607 | 0.00071696 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2516-5_0_4_load_52 | 67 | 0.00055867 | 0.00014002 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2516-5_0_4_load_53 | 68 | 0.0033736 | 0.00084551 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2516-5_0_4_load_55 | 70 | 0.0067788 | 0.0016989 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2516-5_0_4_load_58 | 72 | 0.0008245 | 0.00020664 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2516-5_0_4_load_76 | 73 | 0.0018316 | 0.00045905 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2516-5_0_4_load_77 | 74 | 0.0019788 | 0.00049594 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2516-5_0_4_load_129 | 77 | 0.00083912 | 0.0002103 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2516-5_0_4_load_127 | 79 | 0.00075304 | 0.00018873 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2516-5_0_4_load_210 | 80 | 0.0031647 | 0.00079315 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2516-5_0_4_load_128 | 81 | 0.0018182 | 0.00045568 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2516-5_0_4_load_117 | 82 | 0.00067291 | 0.00016865 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2516-5_0_4_load_118 | 83 | 0.003096 | 0.00077592 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2516-5_0_4_load_113 | 84 | 0.0013168 | 0.00033002 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2516-5_0_4_load_105 | 85 | 0.00011234 | 2.8155e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2516-5_0_4_load_107 | 86 | 0.00088437 | 0.00022164 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2516-5_0_4_load_108 | 87 | 0.00038068 | 9.5407e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2516-5_0_4_load_136 | 88 | 0.0020193 | 0.00050609 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2516-5_0_4_load_137 | 89 | 0.0007793 | 0.00019531 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2516-5_0_4_load_248 | 90 | 0.0070701 | 0.0017719 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2516-5_0_4_load_114 | 91 | 0.0022541 | 0.00056494 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2516-5_0_4_load_116 | 92 | 0.0010292 | 0.00025795 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2516-5_0_4_load_152 | 95 | 0.0033869 | 0.00084883 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2516-5_0_4_load_168 | 96 | 0.00092452 | 0.00023171 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2516-5_0_4_load_165 | 97 | 0.00072015 | 0.00018049 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2516-5_0_4_load_153 | 98 | 0.0034828 | 0.00087286 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2516-5_0_4_load_164 | 99 | 0.001847 | 0.00046291 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2516-5_0_4_load_131 | 100 | 0.0011322 | 0.00028376 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2516-5_0_4_load_132 | 101 | 0.0028369 | 0.00071098 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2516-5_0_4_load_133 | 102 | 0.0013976 | 0.00035028 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2516-5_0_4_load_138 | 104 | 0.0013364 | 0.00033494 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2516-5_0_4_load_139 | 105 | 0.0017352 | 0.00043488 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2516-5_0_4_load_183 | 108 | 0.0027181 | 0.00068122 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2516-5_0_4_load_156 | 110 | 0.00076421 | 0.00019153 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2516-5_0_4_load_155 | 111 | 0.0053261 | 0.0013348 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2516-5_0_4_load_188 | 112 | 0.0040868 | 0.0010242 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2516-5_0_4_load_214 | 113 | 0.00040217 | 0.00010079 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2516-5_0_4_load_189 | 114 | 0.0008688 | 0.00021774 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2516-5_0_4_load_215 | 115 | 0.00063972 | 0.00016033 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2516-5_0_4_load_166 | 116 | 0.00074737 | 0.00018731 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2516-5_0_4_load_167 | 117 | 0.0017 | 0.00042605 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2516-5_0_4_load_172 | 118 | 0.0022267 | 0.00055807 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2516-5_0_4_load_173 | 119 | 0.0018232 | 0.00045693 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2516-5_0_4_load_207 | 122 | 0.0041324 | 0.0010357 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2516-5_0_4_load_217 | 123 | 0.00072967 | 0.00018287 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2516-5_0_4_load_245 | 124 | 0.0050293 | 0.0012605 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2516-5_0_4_load_201 | 125 | 0.0026054 | 0.00065298 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2516-5_0_4_load_202 | 126 | 0.0024152 | 0.00060532 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2516-5_0_4_load_226 | 127 | 0.0010856 | 0.00027209 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2516-5_0_4_load_213 | 128 | 0.0015266 | 0.00038261 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2516-5_0_4_load_208 | 130 | 0.0022649 | 0.00056763 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2516-5_0_4_load_227 | 131 | 0.0018526 | 0.0004643 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2516-5_0_4_load_209 | 132 | 0.0056179 | 0.001408 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2516-5_0_4_load_212 | 133 | 0.0080943 | 0.0020286 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2516-5_0_4_load_216 | 134 | 0.0011585 | 0.00029036 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2516-5_0_4_load_231 | 137 | 0.0013795 | 0.00034573 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2516-5_0_4_load_236 | 138 | 0.0027032 | 0.00067749 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2516-5_0_4_load_232 | 139 | 0.0089822 | 0.0022512 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2516-5_0_4_load_233 | 140 | 0.0022883 | 0.00057349 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2516-5_0_4_load_249 | 141 | 0.0011825 | 0.00029637 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2516-5_0_4_load_244 | 142 | 0.0019988 | 0.00050094 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2516-5_0_4_load_247 | 143 | 0.0078758 | 0.0019739 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 80 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2516-5_0_4_line_0 |  | 0 | 1 | 0.00032374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2516-5_0_4_line_1 |  | 0 | 2 | 0.0429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2516-5_0_4_line_2 |  | 1 | 3 | 0.020831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2516-5_0_4_line_3 |  | 2 | 4 | 0.010851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2516-5_0_4_line_4 |  | 2 | 5 | 0.0060372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2516-5_0_4_line_5 |  | 3 | 6 | 0.025281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2516-5_0_4_line_6 |  | 3 | 7 | 0.011198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2516-5_0_4_line_7 |  | 4 | 8 | 0.0070322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2516-5_0_4_line_8 |  | 5 | 9 | 0.0086237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2516-5_0_4_line_9 |  | 7 | 10 | 0.02032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2516-5_0_4_line_10 |  | 9 | 11 | 0.0085072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2516-5_0_4_line_11 |  | 10 | 12 | 0.020327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2516-5_0_4_line_12 |  | 11 | 13 | 0.026908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2516-5_0_4_line_13 |  | 11 | 14 | 0.024896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2516-5_0_4_line_14 |  | 12 | 69 | 0.028575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_2516-5_0_4_line_15 |  | 13 | 103 | 0.021668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2516-5_0_4_line_16 |  | 14 | 101 | 0.025652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2516-5_0_4_line_17 |  | 15 | 16 | 0.013369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2516-5_0_4_line_18 |  | 15 | 17 | 0.01411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2516-5_0_4_line_19 |  | 16 | 18 | 0.038703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2516-5_0_4_line_20 |  | 16 | 19 | 0.024817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2516-5_0_4_line_21 |  | 17 | 20 | 0.012488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2516-5_0_4_line_22 |  | 18 | 21 | 0.011923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2516-5_0_4_line_23 |  | 19 | 22 | 0.00057619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2516-5_0_4_line_24 |  | 20 | 23 | 0.015547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2516-5_0_4_line_25 |  | 21 | 24 | 0.031927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2516-5_0_4_line_26 |  | 21 | 25 | 0.034095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2516-5_0_4_line_27 |  | 22 | 26 | 0.032052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2516-5_0_4_line_28 |  | 23 | 27 | 0.023698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2516-5_0_4_line_29 |  | 24 | 28 | 0.0038293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2516-5_0_4_line_30 |  | 25 | 29 | 0.03426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2516-5_0_4_line_31 |  | 27 | 30 | 0.011827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2516-5_0_4_line_32 |  | 28 | 90 | 0.034558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2516-5_0_4_line_33 |  | 29 | 85 | 0.030393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2516-5_0_4_line_34 |  | 30 | 142 | 0.012725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2516-5_0_4_line_35 |  | 31 | 32 | 0.029221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2516-5_0_4_line_36 |  | 31 | 33 | 0.0032607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2516-5_0_4_line_37 |  | 32 | 34 | 0.0019613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2516-5_0_4_line_38 |  | 33 | 35 | 0.037175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2516-5_0_4_line_39 |  | 33 | 36 | 0.030415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2516-5_0_4_line_40 |  | 34 | 37 | 0.014386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2516-5_0_4_line_41 |  | 35 | 38 | 0.011536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2516-5_0_4_line_42 |  | 35 | 39 | 0.016888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2516-5_0_4_line_43 |  | 38 | 40 | 0.032542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2516-5_0_4_line_44 |  | 38 | 41 | 0.017744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2516-5_0_4_line_45 |  | 40 | 45 | 0.005261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2516-5_0_4_line_46 |  | 42 | 43 | 0.026145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2516-5_0_4_line_47 |  | 42 | 44 | 0.033229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2516-5_0_4_line_48 |  | 43 | 46 | 0.026775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2516-5_0_4_line_49 |  | 43 | 47 | 0.040213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2516-5_0_4_line_50 |  | 44 | 48 | 0.003558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2516-5_0_4_line_51 |  | 45 | 54 | 0.014505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2516-5_0_4_line_52 |  | 47 | 114 | 0.021395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2516-5_0_4_line_53 |  | 48 | 118 | 0.014679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2516-5_0_4_line_54 |  | 49 | 50 | 0.008013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2516-5_0_4_line_55 |  | 49 | 51 | 0.030702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2516-5_0_4_line_56 |  | 50 | 52 | 0.020249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2516-5_0_4_line_57 |  | 50 | 53 | 0.018747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2516-5_0_4_line_58 |  | 51 | 54 | 0.0126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2516-5_0_4_line_59 |  | 51 | 55 | 0.045134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2516-5_0_4_line_60 |  | 52 | 56 | 0.0099559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2516-5_0_4_line_61 |  | 53 | 57 | 0.0043216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2516-5_0_4_line_62 |  | 55 | 58 | 0.025001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2516-5_0_4_line_63 |  | 56 | 59 | 0.0042849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2516-5_0_4_line_64 |  | 57 | 60 | 0.027261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2516-5_0_4_line_65 |  | 58 | 61 | 0.0086195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2516-5_0_4_line_66 |  | 59 | 62 | 0.0023487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_2516-5_0_4_line_67 |  | 59 | 63 | 0.021073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2516-5_0_4_line_68 |  | 60 | 64 | 0.0029963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2516-5_0_4_line_69 |  | 61 | 65 | 0.019793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2516-5_0_4_line_70 |  | 62 | 78 | 0.018575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_2516-5_0_4_line_71 |  | 63 | 79 | 0.0091716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_2516-5_0_4_line_72 |  | 64 | 120 | 0.02022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2516-5_0_4_line_73 |  | 65 | 135 | 0.011752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2516-5_0_4_line_74 |  | 66 | 67 | 0.019979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_2516-5_0_4_line_75 |  | 66 | 68 | 0.0044583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_2516-5_0_4_line_76 |  | 67 | 69 | 0.014865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_2516-5_0_4_line_77 |  | 68 | 70 | 0.019397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_2516-5_0_4_line_78 |  | 69 | 71 | 0.010916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2516-5_0_4_line_79 |  | 70 | 72 | 0.0028428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2516-5_0_4_line_80 |  | 71 | 73 | 0.0018961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2516-5_0_4_line_81 |  | 71 | 74 | 0.016023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2516-5_0_4_line_82 |  | 72 | 75 | 0.034704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_2516-5_0_4_line_83 |  | 74 | 76 | 0.037288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2516-5_0_4_line_84 |  | 75 | 77 | 0.012695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_2516-5_0_4_line_85 |  | 76 | 82 | 0.015106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2516-5_0_4_line_86 |  | 76 | 83 | 0.038615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2516-5_0_4_line_87 |  | 76 | 84 | 0.01545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2516-5_0_4_line_88 |  | 77 | 81 | 0.0094021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2516-5_0_4_line_89 |  | 78 | 80 | 0.0058414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_2516-5_0_4_line_90 |  | 79 | 81 | 0.0045661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_2516-5_0_4_line_91 |  | 80 | 130 | 0.019986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2516-5_0_4_line_92 |  | 83 | 94 | 0.0067827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2516-5_0_4_line_93 |  | 84 | 91 | 0.015913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2516-5_0_4_line_94 |  | 85 | 86 | 0.018893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2516-5_0_4_line_95 |  | 86 | 87 | 0.026554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2516-5_0_4_line_96 |  | 87 | 88 | 0.013615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2516-5_0_4_line_97 |  | 88 | 89 | 0.0085733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2516-5_0_4_line_98 |  | 89 | 104 | 0.018401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2516-5_0_4_line_99 |  | 90 | 103 | 0.0076259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2516-5_0_4_line_100 |  | 91 | 92 | 0.039549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2516-5_0_4_line_101 |  | 92 | 93 | 0.032871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2516-5_0_4_line_102 |  | 93 | 95 | 0.042532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2516-5_0_4_line_103 |  | 94 | 96 | 0.028019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2516-5_0_4_line_104 |  | 94 | 97 | 0.011785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2516-5_0_4_line_105 |  | 95 | 98 | 0.037375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2516-5_0_4_line_106 |  | 97 | 99 | 0.025206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2516-5_0_4_line_107 |  | 98 | 109 | 0.031443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2516-5_0_4_line_108 |  | 99 | 116 | 0.002142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2516-5_0_4_line_109 |  | 100 | 101 | 0.00037639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2516-5_0_4_line_110 |  | 100 | 102 | 0.010986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2516-5_0_4_line_111 |  | 103 | 124 | 0.01571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2516-5_0_4_line_112 |  | 104 | 105 | 0.029895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2516-5_0_4_line_113 |  | 105 | 106 | 0.019976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2516-5_0_4_line_114 |  | 106 | 107 | 0.00968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2516-5_0_4_line_115 |  | 106 | 108 | 0.015506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2516-5_0_4_line_116 |  | 107 | 125 | 0.023594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2516-5_0_4_line_117 |  | 108 | 126 | 0.022233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2516-5_0_4_line_118 |  | 109 | 110 | 0.014154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2516-5_0_4_line_119 |  | 110 | 113 | 0.0074028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2516-5_0_4_line_120 |  | 111 | 112 | 1.2811e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2516-5_0_4_line_121 |  | 112 | 114 | 0.0469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2516-5_0_4_line_122 |  | 113 | 115 | 0.026793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2516-5_0_4_line_123 |  | 115 | 134 | 0.017106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2516-5_0_4_line_124 |  | 116 | 117 | 0.015442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2516-5_0_4_line_125 |  | 118 | 119 | 0.030642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2516-5_0_4_line_126 |  | 119 | 120 | 0.036191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2516-5_0_4_line_127 |  | 120 | 121 | 0.008989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2516-5_0_4_line_128 |  | 121 | 122 | 0.012814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2516-5_0_4_line_129 |  | 122 | 123 | 0.013754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2516-5_0_4_line_130 |  | 124 | 143 | 0.031135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2516-5_0_4_line_131 |  | 125 | 127 | 0.037571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2516-5_0_4_line_132 |  | 127 | 131 | 0.030521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2516-5_0_4_line_133 |  | 128 | 129 | 0.0052081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2516-5_0_4_line_134 |  | 129 | 133 | 0.035633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2516-5_0_4_line_135 |  | 129 | 132 | 0.021761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2516-5_0_4_line_136 |  | 130 | 132 | 0.0092468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2516-5_0_4_line_137 |  | 135 | 136 | 0.020445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2516-5_0_4_line_138 |  | 135 | 137 | 0.012941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2516-5_0_4_line_139 |  | 136 | 138 | 0.024872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2516-5_0_4_line_140 |  | 137 | 139 | 0.017422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2516-5_0_4_line_141 |  | 138 | 141 | 0.014391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2516-5_0_4_line_142 |  | 139 | 140 | 0.0014344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2516-5_0_4_trafo_210 | 0.63 MVA 20/0.4 kV | 144 | 80 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2613874.3137 | 1229402.6688 | 2613874.0038 | 1229402.5752
1 | 2613915.3787 | 1229415.0813 | 2613912.7974 | 1229414.2971 | 2613874.3137 | 1229402.6688
2 | 2613854.0633 | 1229396.55 | 2613874.0038 | 1229402.5752
3 | 2613915.3787 | 1229415.0813 | 2613912.8086 | 1229425.6238
4 | 2613915.3787 | 1229415.0813 | 2613916.8176 | 1229409.2181
5 | 2613854.0633 | 1229396.55 | 2613850.0728 | 1229421.5145
6 | 2613854.0633 | 1229396.55 | 2613843.4469 | 1229392.987
7 | 2613912.8086 | 1229425.6238 | 2613911.143 | 1229432.4559
8 | 2613918.8729 | 1229400.8428 | 2613916.8176 | 1229409.2181
9 | 2613824.183 | 1229386.5219 | 2613843.4469 | 1229392.987
10 | 2613920.9004 | 1229392.5808 | 2613918.8729 | 1229400.8428
11 | 2613824.183 | 1229386.5219 | 2613812.8335 | 1229382.7129 | 2613804.5284 | 1229381.7957
12 | 2613920.9004 | 1229392.5808 | 2613927.8637 | 1229366.5897
13 | 2613920.9004 | 1229392.5808 | 2613938.9605 | 1229398.6821 | 2613944.1128 | 1229401.418 | 2613944.1128 | 1229401.418
14 | 2613776.126 | 1229378.6591 | 2613804.5284 | 1229381.7957
15 | 2613933.4711 | 1229345.6599 | 2613927.8637 | 1229366.5897
16 | 2613944.1128 | 1229401.418 | 2613962.8083 | 1229418.9827
17 | 2614022.0453 | 1229295.2149 | 2614020.9582 | 1229283.9167 | 2614020.8805 | 1229281.8997
18 | 2614023.9642 | 1229268.3812 | 2614021.7488 | 1229273.0899 | 2614021.0295 | 1229276.1678 | 2614020.7726 | 1229279.1023 | 2614020.8805 | 1229281.8997
19 | 2614022.0453 | 1229295.2149 | 2614012.947 | 1229295.3603 | 2613989.3889 | 1229294.9493 | 2613983.395 | 1229295.7135
20 | 2614022.0453 | 1229295.2149 | 2614046.8623 | 1229295.2086
21 | 2614023.9642 | 1229268.3812 | 2614013.3582 | 1229261.7889
22 | 2613976.4441 | 1229304.0577 | 2613976.9209 | 1229301.0348 | 2613977.546 | 1229299.3464 | 2613979.0044 | 1229297.6599 | 2613980.9919 | 1229296.4861 | 2613983.395 | 1229295.7135
23 | 2614047.4385 | 1229295.2084 | 2614046.8623 | 1229295.2086
24 | 2614013.3582 | 1229261.7889 | 2614000.1538 | 1229253.5816
25 | 2613976.4441 | 1229304.0577 | 2613944.5178 | 1229304.2213
26 | 2613976.4441 | 1229304.0577 | 2613992.0147 | 1229305.8286 | 2614009.3956 | 1229311.9394
27 | 2614047.4385 | 1229295.2084 | 2614079.4904 | 1229295.2003
28 | 2614000.1538 | 1229253.5816 | 2613983.6919 | 1229243.3496 | 2613979.3811 | 1229243.5396
29 | 2613940.6885 | 1229304.2409 | 2613944.5178 | 1229304.2213
30 | 2614009.3956 | 1229311.9394 | 2614011.6563 | 1229312.7343 | 2614029.4521 | 1229324.9722 | 2614037.3101 | 1229331.579
31 | 2613970.0999 | 1229250.6333 | 2613974.9616 | 1229248.0765 | 2613979.3811 | 1229243.5396 | 2613979.3811 | 1229243.5396
32 | 2613940.6885 | 1229304.2409 | 2613940.473 | 1229308.9099 | 2613940.2737 | 1229313.1898 | 2613939.6678 | 1229319.5922 | 2613935.2347 | 1229338.2407
33 | 2614058.5006 | 1229353.2217 | 2614047.1281 | 1229339.8337 | 2614037.3101 | 1229331.579
34 | 2613957.9579 | 1229246.8248 | 2613970.0999 | 1229250.6333 | 2613970.0999 | 1229250.6333
35 | 2613724.127 | 1229061.7998 | 2613744.0292 | 1229083.1949
36 | 2613746.2501 | 1229085.5824 | 2613744.0292 | 1229083.1949
37 | 2613724.127 | 1229061.7998 | 2613722.7911 | 1229060.3638
38 | 2613746.2501 | 1229085.5824 | 2613766.797 | 1229107.6762 | 2613770.7 | 1229113.5442
39 | 2613746.2501 | 1229085.5824 | 2613727.6284 | 1229102.5052 | 2613722.5547 | 1229103.8638
40 | 2613722.7911 | 1229060.3638 | 2613712.9931 | 1229049.8308
41 | 2613776.8591 | 1229123.3087 | 2613770.7 | 1229113.5442
42 | 2613770.7 | 1229113.5442 | 2613764.318 | 1229115.0304 | 2613756.3289 | 1229121.587
43 | 2613776.8591 | 1229123.3087 | 2613782.345 | 1229139.1752 | 2613786.1887 | 1229154.4532
44 | 2613776.8591 | 1229123.3087 | 2613793.9617 | 1229118.5794
45 | 2613787.4722 | 1229159.5553 | 2613786.1887 | 1229154.4532
46 | 2613689.7198 | 1229122.6413 | 2613683.7846 | 1229124.1842 | 2613664.785 | 1229117.6813
47 | 2613703.0591 | 1229152.8343 | 2613700.0778 | 1229141.4318 | 2613689.7198 | 1229122.6413
48 | 2613664.785 | 1229117.6813 | 2613672.1558 | 1229091.9403
49 | 2613645.9385 | 1229140.3184 | 2613657.0035 | 1229144.8463 | 2613664.785 | 1229117.6813
50 | 2613700.2511 | 1229155.0292 | 2613703.0591 | 1229152.8343
51 | 2613791.0111 | 1229173.6217 | 2613787.4722 | 1229159.5553
52 | 2613645.9385 | 1229140.3184 | 2613637.3185 | 1229159.9003
53 | 2613700.2511 | 1229155.0292 | 2613704.7527 | 1229157.5632 | 2613707.8454 | 1229166.5601
54 | 2613802.8537 | 1229223.5506 | 2613801.039 | 1229215.7458
55 | 2613794.0853 | 1229185.8412 | 2613799.2533 | 1229208.0664 | 2613801.039 | 1229215.7458
56 | 2613802.8537 | 1229223.5506 | 2613807.6751 | 1229235.1687 | 2613811.0641 | 1229242.0496
57 | 2613802.8537 | 1229223.5506 | 2613798.9896 | 1229223.8752 | 2613793.0796 | 1229224.3841 | 2613784.1742 | 1229225.1384
58 | 2613794.0853 | 1229185.8412 | 2613791.0111 | 1229173.6217
59 | 2613794.0853 | 1229185.8412 | 2613797.995 | 1229185.4945 | 2613824.484 | 1229183.1655 | 2613839.089 | 1229182.5494
60 | 2613811.0641 | 1229242.0496 | 2613815.4631 | 1229250.981
61 | 2613779.8681 | 1229225.5031 | 2613784.1742 | 1229225.1384
62 | 2613864.0679 | 1229181.4957 | 2613839.089 | 1229182.5494
63 | 2613817.3564 | 1229254.825 | 2613815.4631 | 1229250.981
64 | 2613752.7045 | 1229227.8038 | 2613779.8681 | 1229225.5031
65 | 2613872.6744 | 1229181.5885 | 2613871.4708 | 1229181.4178 | 2613864.9558 | 1229181.4582 | 2613864.0679 | 1229181.4957
66 | 2613817.3564 | 1229254.825 | 2613818.6382 | 1229256.793
67 | 2613817.3564 | 1229254.825 | 2613801.2162 | 1229268.3741
68 | 2613752.7045 | 1229227.8038 | 2613749.7188 | 1229228.0567
69 | 2613872.6744 | 1229181.5885 | 2613879.5965 | 1229182.5707 | 2613886.649 | 1229185.9446 | 2613889.3141 | 1229189.7976 | 2613889.4014 | 1229190.0833
70 | 2613829.6271 | 1229271.7301 | 2613823.8254 | 1229264.757 | 2613818.6382 | 1229256.793
71 | 2613797.5676 | 1229275.5552 | 2613797.0302 | 1229271.8882 | 2613801.2162 | 1229268.3741
72 | 2613729.5705 | 1229229.7632 | 2613749.7188 | 1229228.0567
73 | 2613892.8326 | 1229201.3237 | 2613889.4014 | 1229190.0833
74 | 2613779.5397 | 1229364.1916 | 2613784.1279 | 1229344.7462
75 | 2613786.4858 | 1229340.9625 | 2613784.1279 | 1229344.7462 | 2613784.1279 | 1229344.7462
76 | 2613776.126 | 1229378.6591 | 2613779.5397 | 1229364.1916
77 | 2613786.4858 | 1229340.9625 | 2613796.7443 | 1229324.5007
78 | 2613773.8137 | 1229389.3268 | 2613776.126 | 1229378.6591
79 | 2613796.7443 | 1229324.5007 | 2613798.2478 | 1229322.088
80 | 2613773.8137 | 1229389.3268 | 2613773.5218 | 1229391.2003
81 | 2613773.8137 | 1229389.3268 | 2613758.3044 | 1229385.3013
82 | 2613816.6022 | 1229292.6346 | 2613798.2478 | 1229322.088
83 | 2613722.2122 | 1229375.9334 | 2613758.3044 | 1229385.3013
84 | 2613816.6022 | 1229292.6346 | 2613806.2418 | 1229285.2984
85 | 2613722.2122 | 1229375.9334 | 2613720.0634 | 1229390.8859
86 | 2613722.2122 | 1229375.9334 | 2613723.9024 | 1229365.6422 | 2613723.5459 | 1229337.4581
87 | 2613722.2122 | 1229375.9334 | 2613717.7987 | 1229378.0356 | 2613707.2788 | 1229377.1001
88 | 2613798.5686 | 1229279.8651 | 2613806.2418 | 1229285.2984
89 | 2613829.6271 | 1229271.7301 | 2613834.0507 | 1229275.5451
90 | 2613797.5676 | 1229275.5552 | 2613798.1563 | 1229279.5731 | 2613798.5686 | 1229279.8651
91 | 2613834.0507 | 1229275.5451 | 2613841.8292 | 1229282.2535 | 2613847.3425 | 1229286.2131 | 2613849.9273 | 1229287.5862
92 | 2613723.4601 | 1229330.676 | 2613723.5459 | 1229337.4581
93 | 2613707.2788 | 1229377.1001 | 2613691.4282 | 1229375.6906
94 | 2614058.5006 | 1229353.2217 | 2614065.7795 | 1229361.7907 | 2614069.7971 | 1229368.301
95 | 2614082.5298 | 1229391.5495 | 2614077.7556 | 1229381.1971 | 2614069.7971 | 1229368.301
96 | 2614082.5298 | 1229391.5495 | 2614088.2315 | 1229403.9132 | 2614088.2315 | 1229403.9132
97 | 2614090.9394 | 1229412.0475 | 2614088.2315 | 1229403.9132
98 | 2614090.9394 | 1229412.0475 | 2614096.7516 | 1229429.5066
99 | 2613933.4711 | 1229345.6599 | 2613935.2347 | 1229338.2407
100 | 2613691.4282 | 1229375.6906 | 2613668.9033 | 1229373.6876 | 2613652.0203 | 1229372.3638
101 | 2613619.2494 | 1229369.7941 | 2613652.0203 | 1229372.3638
102 | 2613619.2494 | 1229369.7941 | 2613612.8261 | 1229336.3484 | 2613612.18 | 1229327.8981
103 | 2613723.4601 | 1229330.676 | 2613724.3995 | 1229302.6729
104 | 2613723.4601 | 1229330.676 | 2613711.7307 | 1229329.5327
105 | 2613613.5364 | 1229290.6228 | 2613613.5364 | 1229290.6228 | 2613611.4947 | 1229318.935 | 2613612.18 | 1229327.8981
106 | 2613686.644 | 1229327.0875 | 2613711.7307 | 1229329.5327
107 | 2613620.9011 | 1229260.0547 | 2613613.5364 | 1229290.6228
108 | 2613684.5121 | 1229326.8797 | 2613686.644 | 1229327.0875
109 | 2613963.0826 | 1229419.2404 | 2613962.8083 | 1229418.9827
110 | 2613971.0891 | 1229426.7628 | 2613963.0826 | 1229419.2404
111 | 2613933.4711 | 1229345.6599 | 2613948.5357 | 1229350.1171
112 | 2614096.7516 | 1229429.5066 | 2614106.1944 | 1229457.8715
113 | 2614112.5041 | 1229476.825 | 2614106.1944 | 1229457.8715
114 | 2614115.5806 | 1229486.0044 | 2614112.5041 | 1229476.825
115 | 2614112.5041 | 1229476.825 | 2614098.8741 | 1229484.2176
116 | 2614115.5806 | 1229486.0044 | 2614138.9374 | 1229482.6647
117 | 2614079.3303 | 1229494.8177 | 2614098.8741 | 1229484.2176
118 | 2613620.9011 | 1229260.0547 | 2613617.795 | 1229260.1811 | 2613606.7593 | 1229260.6341
119 | 2613599.3627 | 1229260.9377 | 2613606.7593 | 1229260.6341
120 | 2613627.2076 | 1229205.0558 | 2613627.2073 | 1229205.0686
121 | 2613637.3185 | 1229159.9003 | 2613633.5642 | 1229168.4291 | 2613627.5601 | 1229186.893 | 2613627.2076 | 1229205.0558
122 | 2613599.3627 | 1229260.9377 | 2613572.592 | 1229262.0367
123 | 2613572.592 | 1229262.0367 | 2613555.5004 | 1229262.7383
124 | 2613669.1427 | 1229325.3816 | 2613684.5121 | 1229326.8797
125 | 2613717.8066 | 1229195.5377 | 2613707.8454 | 1229166.5601
126 | 2613729.5705 | 1229229.7632 | 2613728.5697 | 1229226.8481 | 2613717.8066 | 1229195.5377
127 | 2613720.7336 | 1229231.544 | 2613729.5705 | 1229229.7632
128 | 2613720.7336 | 1229231.544 | 2613708.179 | 1229234.1109
129 | 2613708.179 | 1229234.1109 | 2613695.7838 | 1229236.6453 | 2613694.7387 | 1229236.9952
130 | 2613978.3912 | 1229358.9505 | 2613948.5357 | 1229350.1171
131 | 2614175.9502 | 1229476.3861 | 2614174.7332 | 1229476.7612 | 2614168.2531 | 1229478.2023 | 2614162.8497 | 1229479.2456 | 2614138.9374 | 1229482.6647
132 | 2614175.9502 | 1229476.3861 | 2614180.1382 | 1229475.0953 | 2614187.5761 | 1229472.2223 | 2614203.7249 | 1229463.9047
133 | 2613879.0789 | 1229297.6936 | 2613884.2371 | 1229298.4126
134 | 2613879.0789 | 1229297.6936 | 2613872.4298 | 1229332.699
135 | 2613879.0789 | 1229297.6936 | 2613865.118 | 1229294.3147 | 2613858.8206 | 1229292.0432 | 2613858.1894 | 1229291.7357
136 | 2613849.9273 | 1229287.5862 | 2613852.7445 | 1229289.0829 | 2613858.1894 | 1229291.7357
137 | 2613892.8326 | 1229201.3237 | 2613901.6473 | 1229202.6339 | 2613909.0863 | 1229202.6512 | 2613912.893 | 1229200.9924
138 | 2613892.8326 | 1229201.3237 | 2613895.2499 | 1229214.0369
139 | 2613912.893 | 1229200.9924 | 2613935.6652 | 1229210.9945
140 | 2613906.3963 | 1229227.4268 | 2613895.2499 | 1229214.0369
141 | 2613948.8411 | 1229216.7817 | 2613935.6652 | 1229210.9945
142 | 2613907.314 | 1229228.5292 | 2613906.3963 | 1229227.4268

## bus_geodata
| x | y | coords
0 | 2613874.3137 | 1229402.6688
1 | 2613874.0038 | 1229402.5752
2 | 2613915.3787 | 1229415.0813
3 | 2613854.0633 | 1229396.55
4 | 2613912.8086 | 1229425.6238
5 | 2613916.8176 | 1229409.2181
6 | 2613850.0728 | 1229421.5145
7 | 2613843.4469 | 1229392.987
8 | 2613911.143 | 1229432.4559
9 | 2613918.8729 | 1229400.8428
10 | 2613824.183 | 1229386.5219
11 | 2613920.9004 | 1229392.5808
12 | 2613804.5284 | 1229381.7957
13 | 2613927.8637 | 1229366.5897
14 | 2613944.1128 | 1229401.418
15 | 2614020.8805 | 1229281.8997
16 | 2614022.0453 | 1229295.2149
17 | 2614023.9642 | 1229268.3812
18 | 2613983.395 | 1229295.7135
19 | 2614046.8623 | 1229295.2086
20 | 2614013.3582 | 1229261.7889
21 | 2613976.4441 | 1229304.0577
22 | 2614047.4385 | 1229295.2084
23 | 2614000.1538 | 1229253.5816
24 | 2613944.5178 | 1229304.2213
25 | 2614009.3956 | 1229311.9394
26 | 2614079.4904 | 1229295.2003
27 | 2613979.3811 | 1229243.5396
28 | 2613940.6885 | 1229304.2409
29 | 2614037.3101 | 1229331.579
30 | 2613970.0999 | 1229250.6333
31 | 2613744.0292 | 1229083.1949
32 | 2613724.127 | 1229061.7998
33 | 2613746.2501 | 1229085.5824
34 | 2613722.7911 | 1229060.3638
35 | 2613770.7 | 1229113.5442
36 | 2613722.5547 | 1229103.8638
37 | 2613712.9931 | 1229049.8308
38 | 2613776.8591 | 1229123.3087
39 | 2613756.3289 | 1229121.587
40 | 2613786.1887 | 1229154.4532
41 | 2613793.9617 | 1229118.5794
42 | 2613689.7198 | 1229122.6413
43 | 2613664.785 | 1229117.6813
44 | 2613703.0591 | 1229152.8343
45 | 2613787.4722 | 1229159.5553
46 | 2613672.1558 | 1229091.9403
47 | 2613645.9385 | 1229140.3184
48 | 2613700.2511 | 1229155.0292
49 | 2613801.039 | 1229215.7458
50 | 2613802.8537 | 1229223.5506
51 | 2613794.0853 | 1229185.8412
52 | 2613811.0641 | 1229242.0496
53 | 2613784.1742 | 1229225.1384
54 | 2613791.0111 | 1229173.6217
55 | 2613839.089 | 1229182.5494
56 | 2613815.4631 | 1229250.981
57 | 2613779.8681 | 1229225.5031
58 | 2613864.0679 | 1229181.4957
59 | 2613817.3564 | 1229254.825
60 | 2613752.7045 | 1229227.8038
61 | 2613872.6744 | 1229181.5885
62 | 2613818.6382 | 1229256.793
63 | 2613801.2162 | 1229268.3741
64 | 2613749.7188 | 1229228.0567
65 | 2613889.4014 | 1229190.0833
66 | 2613784.1279 | 1229344.7462
67 | 2613779.5397 | 1229364.1916
68 | 2613786.4858 | 1229340.9625
69 | 2613776.126 | 1229378.6591
70 | 2613796.7443 | 1229324.5007
71 | 2613773.8137 | 1229389.3268
72 | 2613798.2478 | 1229322.088
73 | 2613773.5218 | 1229391.2003
74 | 2613758.3044 | 1229385.3013
75 | 2613816.6022 | 1229292.6346
76 | 2613722.2122 | 1229375.9334
77 | 2613806.2418 | 1229285.2984
78 | 2613829.6271 | 1229271.7301
79 | 2613797.5676 | 1229275.5552
80 | 2613834.0507 | 1229275.5451
81 | 2613798.5686 | 1229279.8651
82 | 2613720.0634 | 1229390.8859
83 | 2613723.5459 | 1229337.4581
84 | 2613707.2788 | 1229377.1001
85 | 2614058.5006 | 1229353.2217
86 | 2614069.7971 | 1229368.301
87 | 2614082.5298 | 1229391.5495
88 | 2614088.2315 | 1229403.9132
89 | 2614090.9394 | 1229412.0475
90 | 2613935.2347 | 1229338.2407
91 | 2613691.4282 | 1229375.6906
92 | 2613652.0203 | 1229372.3638
93 | 2613619.2494 | 1229369.7941
94 | 2613723.4601 | 1229330.676
95 | 2613612.18 | 1229327.8981
96 | 2613724.3995 | 1229302.6729
97 | 2613711.7307 | 1229329.5327
98 | 2613613.5364 | 1229290.6228
99 | 2613686.644 | 1229327.0875
100 | 2613963.0826 | 1229419.2404
101 | 2613962.8083 | 1229418.9827
102 | 2613971.0891 | 1229426.7628
103 | 2613933.4711 | 1229345.6599
104 | 2614096.7516 | 1229429.5066
105 | 2614106.1944 | 1229457.8715
106 | 2614112.5041 | 1229476.825
107 | 2614115.5806 | 1229486.0044
108 | 2614098.8741 | 1229484.2176
109 | 2613620.9011 | 1229260.0547
110 | 2613606.7593 | 1229260.6341
111 | 2613627.2073 | 1229205.0686
112 | 2613627.2076 | 1229205.0558
113 | 2613599.3627 | 1229260.9377
114 | 2613637.3185 | 1229159.9003
115 | 2613572.592 | 1229262.0367
116 | 2613684.5121 | 1229326.8797
117 | 2613669.1427 | 1229325.3816
118 | 2613707.8454 | 1229166.5601
119 | 2613717.8066 | 1229195.5377
120 | 2613729.5705 | 1229229.7632
121 | 2613720.7336 | 1229231.544
122 | 2613708.179 | 1229234.1109
123 | 2613694.7387 | 1229236.9952
124 | 2613948.5357 | 1229350.1171
125 | 2614138.9374 | 1229482.6647
126 | 2614079.3303 | 1229494.8177
127 | 2614175.9502 | 1229476.3861
128 | 2613884.2371 | 1229298.4126
129 | 2613879.0789 | 1229297.6936
130 | 2613849.9273 | 1229287.5862
131 | 2614203.7249 | 1229463.9047
132 | 2613858.1894 | 1229291.7357
133 | 2613872.4298 | 1229332.699
134 | 2613555.5004 | 1229262.7383
135 | 2613892.8326 | 1229201.3237
136 | 2613912.893 | 1229200.9924
137 | 2613895.2499 | 1229214.0369
138 | 2613935.6652 | 1229210.9945
139 | 2613906.3963 | 1229227.4268
140 | 2613907.314 | 1229228.5292
141 | 2613948.8411 | 1229216.7817
142 | 2613957.9579 | 1229246.8248
143 | 2613978.3912 | 1229358.9505
144 | 2613829.6271 | 1229271.7301

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98655 | -0.25698 | 0.004677 | 0.0011722
1 | 0.98656 | -0.25679 | 0.001432 | 0.00035888
2 | 0.98466 | -0.29365 | 0 | 0
3 | 0.98722 | -0.24419 | 0 | 0
4 | 0.98463 | -0.29425 | 0.00078649 | 0.00019711
5 | 0.98414 | -0.30367 | 0.0015128 | 0.00037915
6 | 0.98714 | -0.24565 | 0.0032299 | 0.00080948
7 | 0.98758 | -0.2372 | 0.0062826 | 0.0015746
8 | 0.98461 | -0.29454 | 0.0022737 | 0.00056985
9 | 0.98341 | -0.31776 | 0.0050684 | 0.0012703
10 | 0.98828 | -0.22379 | 0.0063224 | 0.0015845
11 | 0.98274 | -0.3309 | 0 | 0
12 | 0.98901 | -0.20962 | 0.001631 | 0.00040876
13 | 0.98082 | -0.36826 | 0.0055887 | 0.0014006
14 | 0.98253 | -0.33488 | 0.0034981 | 0.0008767
15 | 0.9747 | -0.4881 | 0.0013694 | 0.0003432
16 | 0.97486 | -0.4851 | 0 | 0
17 | 0.97456 | -0.49092 | 0 | 0
18 | 0.97564 | -0.46975 | 0.0013023 | 0.00032639
19 | 0.97464 | -0.48938 | 0.0019888 | 0.00049843
20 | 0.97443 | -0.49341 | 0.001779 | 0.00044587
21 | 0.97589 | -0.46474 | 0 | 0
22 | 0.97464 | -0.48945 | 0.0072242 | 0.0018106
23 | 0.9743 | -0.49601 | 0.0014093 | 0.00035321
24 | 0.97714 | -0.44015 | 0.0090726 | 0.0022738
25 | 0.97528 | -0.47672 | 0.00064807 | 0.00016242
26 | 0.97463 | -0.48956 | 0.00017867 | 4.4778e-05
27 | 0.97413 | -0.49936 | 0.0019614 | 0.00049158
28 | 0.97732 | -0.43657 | 0 | 0
29 | 0.97469 | -0.48837 | 0.00060719 | 0.00015218
30 | 0.97407 | -0.5006 | 0.0037298 | 0.00093478
31 | 0.98637 | -0.2621 | 0.0048246 | 0.0012092
32 | 0.98606 | -0.26816 | 0.00083589 | 0.00020949
33 | 0.98642 | -0.26114 | 0 | 0
34 | 0.98604 | -0.26854 | 0.0027729 | 0.00069495
35 | 0.98733 | -0.24347 | 0 | 0
36 | 0.98614 | -0.26666 | 0.010141 | 0.0025415
37 | 0.98593 | -0.2706 | 0.0079733 | 0.0019983
38 | 0.98765 | -0.23729 | 0 | 0
39 | 0.98727 | -0.24451 | 0.0034187 | 0.0008568
40 | 0.98875 | -0.21576 | 0.0049452 | 0.0012394
41 | 0.98753 | -0.23955 | 0.0071027 | 0.0017801
42 | 0.98788 | -0.23281 | 0 | 0
43 | 0.98734 | -0.24335 | 0 | 0
44 | 0.98857 | -0.21942 | 0 | 0
45 | 0.98896 | -0.21182 | 0.010108 | 0.0025334
46 | 0.98704 | -0.24923 | 0.012278 | 0.0030771
47 | 0.98696 | -0.25075 | 0 | 0
48 | 0.98864 | -0.21799 | 0 | 0
49 | 0.99256 | -0.14224 | 0.0089429 | 0.0022413
50 | 0.99322 | -0.12951 | 0 | 0
51 | 0.99027 | -0.18632 | 0 | 0
52 | 0.99572 | -0.08138 | 0.0010112 | 0.00025343
53 | 0.99244 | -0.14441 | 0.0012481 | 0.0003128
54 | 0.98965 | -0.19835 | 0.001582 | 0.00039647
55 | 0.98914 | -0.2082 | 0.0012094 | 0.0003031
56 | 0.99696 | -0.057629 | 0.00080022 | 0.00020055
57 | 0.99227 | -0.14776 | 0.0016333 | 0.00040934
58 | 0.98855 | -0.2198 | 0.0014715 | 0.00036878
59 | 0.9975 | -0.047365 | 0 | 0
60 | 0.99122 | -0.16808 | 0.0036335 | 0.00091063
61 | 0.98835 | -0.22357 | 0.0014509 | 0.00036363
62 | 0.99772 | -0.043218 | 0.0014486 | 0.00036305
63 | 0.99643 | -0.067793 | 0.0011673 | 0.00029256
64 | 0.99111 | -0.17013 | 0.0069642 | 0.0017454
65 | 0.98793 | -0.23174 | 0.0065684 | 0.0016462
66 | 0.99164 | -0.15912 | 0.0028607 | 0.00071696
67 | 0.99073 | -0.17654 | 0.00055867 | 0.00014002
68 | 0.99185 | -0.15516 | 0.0033736 | 0.00084551
69 | 0.99006 | -0.18947 | 0 | 0
70 | 0.99277 | -0.13758 | 0.0067788 | 0.0016989
71 | 0.98978 | -0.1949 | 0 | 0
72 | 0.99291 | -0.13489 | 0.0008245 | 0.00020664
73 | 0.98978 | -0.19496 | 0.0018316 | 0.00045905
74 | 0.9894 | -0.20235 | 0.0019788 | 0.00049594
75 | 0.99463 | -0.10197 | 0 | 0
76 | 0.98857 | -0.2184 | 0 | 0
77 | 0.99526 | -0.089954 | 0.00083912 | 0.0002103
78 | 0.99945 | -0.010321 | 0 | 0
79 | 0.99596 | -0.076635 | 0.00075304 | 0.00018873
80 | 1 | 0 | -0.32723 | -0.083197
81 | 0.99573 | -0.081019 | 0.0018182 | 0.00045568
82 | 0.98856 | -0.21858 | 0.00067291 | 0.00016865
83 | 0.98825 | -0.22463 | 0.003096 | 0.00077592
84 | 0.98837 | -0.22238 | 0.0013168 | 0.00033002
85 | 0.97418 | -0.49837 | 0.00011234 | 2.8155e-05
86 | 0.97387 | -0.50456 | 0.00088437 | 0.00022164
87 | 0.97345 | -0.51283 | 0.00038068 | 9.5407e-05
88 | 0.97324 | -0.51697 | 0.0020193 | 0.00050609
89 | 0.97312 | -0.51927 | 0.0007793 | 0.00019531
90 | 0.97897 | -0.40433 | 0.0070701 | 0.0017719
91 | 0.98817 | -0.22611 | 0.0022541 | 0.00056494
92 | 0.98778 | -0.23379 | 0.0010292 | 0.00025795
93 | 0.98748 | -0.23957 | 0 | 0
94 | 0.98821 | -0.22535 | 0 | 0
95 | 0.9871 | -0.24705 | 0.0033869 | 0.00084883
96 | 0.98819 | -0.22581 | 0.00092452 | 0.00023171
97 | 0.98816 | -0.2264 | 0.00072015 | 0.00018049
98 | 0.98688 | -0.25136 | 0.0034828 | 0.00087286
99 | 0.98806 | -0.22833 | 0.001847 | 0.00046291
100 | 0.98241 | -0.33739 | 0.0011322 | 0.00028376
101 | 0.98241 | -0.33737 | 0.0028369 | 0.00071098
102 | 0.98239 | -0.33766 | 0.0013976 | 0.00035028
103 | 0.97939 | -0.39625 | 0 | 0
104 | 0.97289 | -0.52393 | 0.0013364 | 0.00033494
105 | 0.97254 | -0.53076 | 0.0017352 | 0.00043488
106 | 0.97234 | -0.5347 | 0 | 0
107 | 0.97229 | -0.53569 | 0 | 0
108 | 0.97227 | -0.53617 | 0.0027181 | 0.00068122
109 | 0.98679 | -0.25303 | 0 | 0
110 | 0.98675 | -0.25378 | 0.00076421 | 0.00019153
111 | 0.98635 | -0.26259 | 0.0053261 | 0.0013348
112 | 0.98635 | -0.26259 | 0.0040868 | 0.0010242
113 | 0.98674 | -0.25408 | 0.00040217 | 0.00010079
114 | 0.98676 | -0.25468 | 0.0008688 | 0.00021774
115 | 0.98669 | -0.25494 | 0.00063972 | 0.00016033
116 | 0.98806 | -0.22843 | 0.00074737 | 0.00018731
117 | 0.98803 | -0.2289 | 0.0017 | 0.00042605
118 | 0.98895 | -0.21209 | 0.0022267 | 0.00055807
119 | 0.98964 | -0.19856 | 0.0018232 | 0.00045693
120 | 0.99053 | -0.18143 | 0 | 0
121 | 0.99049 | -0.18221 | 0 | 0
122 | 0.99043 | -0.18331 | 0.0041324 | 0.0010357
123 | 0.99042 | -0.18349 | 0.00072967 | 0.00018287
124 | 0.9792 | -0.39993 | 0.0050293 | 0.0012605
125 | 0.97217 | -0.5381 | 0.0026054 | 0.00065298
126 | 0.97222 | -0.53716 | 0.0024152 | 0.00060532
127 | 0.97207 | -0.54014 | 0.0010856 | 0.00027209
128 | 0.99936 | -0.012351 | 0.0015266 | 0.00038261
129 | 0.99936 | -0.012212 | 0 | 0
130 | 0.99968 | -0.0061003 | 0.0022649 | 0.00056763
131 | 0.97201 | -0.54118 | 0.0018526 | 0.0004643
132 | 0.99955 | -0.0085585 | 0.0056179 | 0.001408
133 | 0.9991 | -0.017247 | 0.0080943 | 0.0020286
134 | 0.98668 | -0.25529 | 0.0011585 | 0.00029036
135 | 0.98775 | -0.23521 | 0 | 0
136 | 0.98768 | -0.23663 | 0 | 0
137 | 0.9876 | -0.23813 | 0.0013795 | 0.00034573
138 | 0.98759 | -0.23836 | 0.0027032 | 0.00067749
139 | 0.98742 | -0.24164 | 0.0089822 | 0.0022512
140 | 0.98742 | -0.2417 | 0.0022883 | 0.00057349
141 | 0.98758 | -0.23866 | 0.0011825 | 0.00029637
142 | 0.97405 | -0.50107 | 0.0019988 | 0.00050094
143 | 0.97897 | -0.40439 | 0.0078758 | 0.0019739
144 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.10076 | -0.02556 | 0.10076 | 0.02556 | 9.3601e-07 | 5.8664e-07 | 0.15209 | 0.15209 | 0.15209 | 0.98655 | -0.25698 | 0.98656 | -0.25679 | 13.9272
1 | 0.096083 | 0.024387 | -0.095913 | -0.02428 | 0.00016919 | 0.00010719 | 0.14503 | 0.14503 | 0.14503 | 0.98655 | -0.25698 | 0.98466 | -0.29365 | 19.9219
2 | -0.10219 | -0.025919 | 0.10225 | 0.025958 | 6.195e-05 | 3.8849e-05 | 0.15424 | 0.15424 | 0.15424 | 0.98656 | -0.25679 | 0.98722 | -0.24419 | 14.125
3 | 0.0030603 | 0.00076681 | -0.0030602 | -0.00076689 | 8.7033e-08 | -8.232e-08 | 0.0046247 | 0.0046248 | 0.0046248 | 0.98466 | -0.29365 | 0.98463 | -0.29425 | 1.2705
4 | 0.092853 | 0.023513 | -0.092809 | -0.023485 | 4.4632e-05 | 2.8487e-05 | 0.14041 | 0.14041 | 0.14041 | 0.98466 | -0.29365 | 0.98414 | -0.30367 | 38.5732
5 | 0.0032301 | 0.0008093 | -0.0032299 | -0.00080948 | 2.2472e-07 | -1.794e-07 | 0.0048686 | 0.0048687 | 0.0048687 | 0.98722 | -0.24419 | 0.98714 | -0.24565 | 1.3375
6 | -0.10548 | -0.026767 | 0.10552 | 0.026789 | 3.5438e-05 | 2.2251e-05 | 0.15911 | 0.15911 | 0.15911 | 0.98722 | -0.24419 | 0.98758 | -0.2372 | 14.5708
7 | 0.0022738 | 0.00056978 | -0.0022737 | -0.00056985 | 3.1137e-08 | -6.9514e-08 | 0.0034362 | 0.0034362 | 0.0034362 | 0.98463 | -0.29425 | 0.98461 | -0.29454 | 0.94401
8 | 0.091296 | 0.023106 | -0.091234 | -0.023066 | 6.1693e-05 | 3.9374e-05 | 0.13812 | 0.13812 | 0.13812 | 0.98414 | -0.30367 | 0.98341 | -0.31776 | 37.9448
9 | -0.1118 | -0.028364 | 0.11187 | 0.028409 | 7.2183e-05 | 4.5417e-05 | 0.16858 | 0.16858 | 0.16858 | 0.98758 | -0.2372 | 0.98828 | -0.22379 | 15.4376
10 | 0.086166 | 0.021796 | -0.086111 | -0.021761 | 5.4289e-05 | 3.4637e-05 | 0.13045 | 0.13045 | 0.13045 | 0.98341 | -0.31776 | 0.98274 | -0.3309 | 35.838
11 | -0.1182 | -0.029994 | 0.11828 | 0.030045 | 8.0595e-05 | 5.0799e-05 | 0.1781 | 0.1781 | 0.1781 | 0.98828 | -0.22379 | 0.98901 | -0.20962 | 16.3094
12 | 0.077244 | 0.019539 | -0.077106 | -0.019451 | 0.00013818 | 8.8097e-05 | 0.11702 | 0.11702 | 0.11702 | 0.98274 | -0.3309 | 0.98082 | -0.36826 | 32.1495
13 | 0.0088671 | 0.0022224 | -0.0088654 | -0.0022217 | 1.683e-06 | 7.6173e-07 | 0.013426 | 0.013426 | 0.013426 | 0.98274 | -0.3309 | 0.98253 | -0.33488 | 3.6886
14 | -0.11991 | -0.030454 | 0.12003 | 0.030527 | 0.00011644 | 7.342e-05 | 0.18055 | 0.18055 | 0.18055 | 0.98901 | -0.20962 | 0.99006 | -0.18947 | 16.534
15 | 0.071517 | 0.01805 | -0.071422 | -0.017989 | 9.5735e-05 | 6.0998e-05 | 0.10855 | 0.10855 | 0.10855 | 0.98082 | -0.36826 | 0.97939 | -0.39625 | 29.8202
16 | 0.0053674 | 0.001345 | -0.0053667 | -0.0013449 | 6.3562e-07 | 8.1953e-08 | 0.0081286 | 0.0081287 | 0.0081287 | 0.98253 | -0.33488 | 0.98241 | -0.33737 | 2.2332
17 | -0.012253 | -0.003072 | 0.012255 | 0.0030729 | 1.7543e-06 | 9.5612e-07 | 0.018707 | 0.018707 | 0.018707 | 0.9747 | -0.4881 | 0.97486 | -0.4851 | 5.1392
18 | 0.010884 | 0.0027288 | -0.010882 | -0.002728 | 1.4609e-06 | 7.5912e-07 | 0.016616 | 0.016616 | 0.016616 | 0.9747 | -0.4881 | 0.97456 | -0.49092 | 4.5649
19 | -0.021649 | -0.0054272 | 0.021664 | 0.0054369 | 1.5848e-05 | 9.6601e-06 | 0.033045 | 0.033045 | 0.033045 | 0.97486 | -0.4851 | 0.97564 | -0.46975 | 9.0783
20 | 0.0093936 | 0.0023543 | -0.0093916 | -0.0023534 | 1.9133e-06 | 9.1516e-07 | 0.014338 | 0.014338 | 0.014338 | 0.97486 | -0.4851 | 0.97464 | -0.48938 | 3.9391
21 | 0.010882 | 0.002728 | -0.010881 | -0.0027273 | 1.2929e-06 | 6.719e-07 | 0.016616 | 0.016616 | 0.016616 | 0.97456 | -0.49092 | 0.97443 | -0.49341 | 4.5649
22 | -0.022967 | -0.0057633 | 0.022972 | 0.0057666 | 5.4867e-06 | 3.3626e-06 | 0.035031 | 0.035031 | 0.035031 | 0.97564 | -0.46975 | 0.97589 | -0.46474 | 9.6239
23 | 0.0074029 | 0.0018549 | -0.0074029 | -0.0018549 | 2.76e-08 | 1.0484e-08 | 0.011302 | 0.011302 | 0.011302 | 0.97464 | -0.48938 | 0.97464 | -0.48945 | 3.105
24 | 0.0091021 | 0.0022815 | -0.009101 | -0.0022809 | 1.1264e-06 | 5.2724e-07 | 0.013899 | 0.0139 | 0.0139 | 0.97443 | -0.49341 | 0.9743 | -0.49601 | 3.8186
25 | -0.04221 | -0.010606 | 0.042259 | 0.010637 | 4.9608e-05 | 3.135e-05 | 0.06437 | 0.06437 | 0.06437 | 0.97589 | -0.46474 | 0.97714 | -0.44015 | 17.6841
26 | 0.019237 | 0.0048391 | -0.019226 | -0.0048325 | 1.1006e-05 | 6.6179e-06 | 0.029339 | 0.029339 | 0.029339 | 0.97589 | -0.46474 | 0.97528 | -0.47672 | 8.0602
27 | 0.00017867 | 4.4379e-05 | -0.00017867 | -4.4778e-05 | 8.9387e-10 | -3.9886e-07 | 0.00027263 | 0.00027278 | 0.00027278 | 0.97464 | -0.48945 | 0.97463 | -0.48956 | 0.074939
28 | 0.0076916 | 0.0019277 | -0.0076904 | -0.0019272 | 1.2263e-06 | 4.8977e-07 | 0.011747 | 0.011747 | 0.011747 | 0.9743 | -0.49601 | 0.97413 | -0.49936 | 3.2273
29 | -0.051332 | -0.012911 | 0.051341 | 0.012916 | 8.7783e-06 | 5.5701e-06 | 0.078186 | 0.078186 | 0.078186 | 0.97714 | -0.44015 | 0.97732 | -0.43657 | 21.4796
30 | 0.018578 | 0.0046701 | -0.018568 | -0.0046639 | 1.0326e-05 | 6.1816e-06 | 0.02835 | 0.028351 | 0.028351 | 0.97528 | -0.47672 | 0.97469 | -0.48837 | 7.7886
31 | 0.005729 | 0.0014357 | -0.0057286 | -0.0014356 | 3.3964e-07 | 7.0147e-08 | 0.0087511 | 0.0087512 | 0.0087512 | 0.97413 | -0.49936 | 0.97407 | -0.5006 | 2.4042
32 | -0.051341 | -0.012916 | 0.05142 | 0.012967 | 7.9219e-05 | 5.0267e-05 | 0.078186 | 0.078186 | 0.078186 | 0.97732 | -0.43657 | 0.97897 | -0.40433 | 21.4796
33 | 0.017961 | 0.0045117 | -0.017952 | -0.0045066 | 8.5716e-06 | 5.1072e-06 | 0.027424 | 0.027424 | 0.027424 | 0.97469 | -0.48837 | 0.97418 | -0.49837 | 7.534
34 | 0.0019988 | 0.00050081 | -0.0019988 | -0.00050094 | 4.4491e-08 | -1.2992e-07 | 0.0030534 | 0.0030535 | 0.0030535 | 0.97407 | -0.5006 | 0.97405 | -0.50107 | 0.83886
35 | 0.011586 | 0.0029049 | -0.011583 | -0.0029031 | 3.3479e-06 | 1.7698e-06 | 0.017479 | 0.017479 | 0.017479 | 0.98637 | -0.2621 | 0.98606 | -0.26816 | 4.802
36 | -0.016411 | -0.0041141 | 0.016412 | 0.0041145 | 7.4948e-07 | 4.3804e-07 | 0.024758 | 0.024758 | 0.024758 | 0.98637 | -0.2621 | 0.98642 | -0.26114 | 6.8015
37 | 0.010747 | 0.0026937 | -0.010747 | -0.0026936 | 1.9345e-07 | 9.8789e-08 | 0.016218 | 0.016218 | 0.016218 | 0.98606 | -0.26816 | 0.98604 | -0.26854 | 4.4555
38 | -0.026555 | -0.0066574 | 0.026578 | 0.0066712 | 2.2371e-05 | 1.3842e-05 | 0.040059 | 0.040059 | 0.040059 | 0.98642 | -0.26114 | 0.98733 | -0.24347 | 11.0053
39 | 0.010144 | 0.0025429 | -0.010141 | -0.0025415 | 2.6706e-06 | 1.321e-06 | 0.015302 | 0.015302 | 0.015302 | 0.98642 | -0.26114 | 0.98614 | -0.26666 | 4.2038
40 | 0.007974 | 0.0019986 | -0.0079733 | -0.0019983 | 7.8117e-07 | 3.1647e-07 | 0.012034 | 0.012034 | 0.012034 | 0.98604 | -0.26854 | 0.98593 | -0.2706 | 3.3059
41 | -0.029996 | -0.0075279 | 0.030005 | 0.0075334 | 8.8427e-06 | 5.5118e-06 | 0.045212 | 0.045212 | 0.045212 | 0.98733 | -0.24347 | 0.98765 | -0.23729 | 12.4208
42 | 0.0034189 | 0.0008567 | -0.0034187 | -0.0008568 | 1.6814e-07 | -1.0836e-07 | 0.0051526 | 0.0051526 | 0.0051526 | 0.98733 | -0.24347 | 0.98727 | -0.24451 | 1.4156
43 | -0.037109 | -0.0093138 | 0.037147 | 0.0093378 | 3.8152e-05 | 2.4e-05 | 0.055914 | 0.055914 | 0.055914 | 0.98765 | -0.23729 | 0.98875 | -0.21576 | 15.361
44 | 0.0071035 | 0.0017804 | -0.0071027 | -0.0017801 | 7.6217e-07 | 2.6074e-07 | 0.010702 | 0.010702 | 0.010702 | 0.98765 | -0.23729 | 0.98753 | -0.23955 | 2.9402
45 | -0.042092 | -0.010577 | 0.0421 | 0.010582 | 7.9192e-06 | 5.0008e-06 | 0.063356 | 0.063356 | 0.063356 | 0.98875 | -0.21576 | 0.98896 | -0.21182 | 17.4055
46 | 0.022583 | 0.0056671 | -0.022572 | -0.0056602 | 1.1347e-05 | 6.9273e-06 | 0.034019 | 0.034019 | 0.034019 | 0.98788 | -0.23281 | 0.98734 | -0.24335 | 9.3459
47 | -0.022583 | -0.0056671 | 0.022598 | 0.0056759 | 1.4421e-05 | 8.8036e-06 | 0.034019 | 0.034019 | 0.034019 | 0.98788 | -0.23281 | 0.98857 | -0.21942 | 9.3459
48 | 0.012281 | 0.0030789 | -0.012278 | -0.0030771 | 3.4399e-06 | 1.8592e-06 | 0.018509 | 0.018509 | 0.018509 | 0.98734 | -0.24335 | 0.98704 | -0.24923 | 5.085
49 | 0.010291 | 0.0025813 | -0.010287 | -0.0025795 | 3.6276e-06 | 1.8076e-06 | 0.01551 | 0.01551 | 0.01551 | 0.98734 | -0.24335 | 0.98696 | -0.25075 | 4.261
50 | -0.022598 | -0.0056759 | 0.022599 | 0.0056769 | 1.5441e-06 | 9.4261e-07 | 0.034019 | 0.034019 | 0.034019 | 0.98857 | -0.21942 | 0.98864 | -0.21799 | 9.3458
51 | -0.052209 | -0.013116 | 0.052242 | 0.013137 | 3.3574e-05 | 2.1301e-05 | 0.078566 | 0.078565 | 0.078566 | 0.98896 | -0.21182 | 0.98965 | -0.19835 | 21.5839
52 | 0.010287 | 0.0025795 | -0.010285 | -0.0025785 | 1.9301e-06 | 9.6191e-07 | 0.01551 | 0.01551 | 0.01551 | 0.98696 | -0.25075 | 0.98676 | -0.25468 | 4.261
53 | -0.022599 | -0.0056769 | 0.022606 | 0.0056808 | 6.3706e-06 | 3.8889e-06 | 0.034019 | 0.034019 | 0.034019 | 0.98864 | -0.21799 | 0.98895 | -0.21209 | 9.3458
54 | -0.090268 | -0.022767 | 0.090323 | 0.022803 | 5.5072e-05 | 3.5142e-05 | 0.13538 | 0.13538 | 0.13538 | 0.99256 | -0.14224 | 0.99322 | -0.12951 | 37.1921
55 | 0.081325 | 0.020526 | -0.081154 | -0.020417 | 0.00017129 | 0.00010923 | 0.12197 | 0.12197 | 0.12197 | 0.99256 | -0.14224 | 0.99027 | -0.18632 | 33.5089
56 | -0.13546 | -0.034182 | 0.13577 | 0.034382 | 0.00031299 | 0.00020005 | 0.20302 | 0.20302 | 0.20302 | 0.99322 | -0.12951 | 0.99572 | -0.08138 | 55.776
57 | 0.045136 | 0.011379 | -0.045104 | -0.011359 | 3.2169e-05 | 2.0346e-05 | 0.067645 | 0.067645 | 0.067645 | 0.99322 | -0.12951 | 0.99244 | -0.14441 | 18.5839
58 | 0.053855 | 0.013553 | -0.053824 | -0.013533 | 3.0959e-05 | 1.9651e-05 | 0.080944 | 0.080944 | 0.080944 | 0.99027 | -0.18632 | 0.98965 | -0.19835 | 22.2374
59 | 0.027299 | 0.0068639 | -0.027271 | -0.0068462 | 2.8491e-05 | 1.7654e-05 | 0.041028 | 0.041029 | 0.041029 | 0.99027 | -0.18632 | 0.98914 | -0.2082 | 11.2716
60 | -0.13678 | -0.034635 | 0.13694 | 0.034735 | 0.00015619 | 9.9831e-05 | 0.20454 | 0.20454 | 0.20454 | 0.99572 | -0.08138 | 0.99696 | -0.057629 | 56.1911
61 | 0.043856 | 0.011046 | -0.043849 | -0.011042 | 7.011e-06 | 4.4312e-06 | 0.065774 | 0.065774 | 0.065774 | 0.99244 | -0.14441 | 0.99227 | -0.14776 | 18.0698
62 | 0.026061 | 0.0065431 | -0.026047 | -0.0065342 | 1.4414e-05 | 8.904e-06 | 0.039209 | 0.039209 | 0.039209 | 0.98914 | -0.2082 | 0.98855 | -0.2198 | 10.7718
63 | -0.13774 | -0.034936 | 0.13781 | 0.034979 | 6.801e-05 | 4.347e-05 | 0.20573 | 0.20573 | 0.20573 | 0.99696 | -0.057629 | 0.9975 | -0.047365 | 56.5192
64 | 0.042215 | 0.010632 | -0.042174 | -0.010607 | 4.0994e-05 | 2.5884e-05 | 0.063325 | 0.063325 | 0.063325 | 0.99227 | -0.14776 | 0.99122 | -0.16808 | 17.397
65 | 0.024575 | 0.0061655 | -0.024571 | -0.0061627 | 4.4237e-06 | 2.7207e-06 | 0.036995 | 0.036995 | 0.036995 | 0.98855 | -0.2198 | 0.98835 | -0.22357 | 10.1634
66 | -0.30591 | -0.077991 | 0.30597 | 0.078031 | 6.1263e-05 | 3.9117e-05 | 0.45681 | 0.45681 | 0.45681 | 0.9975 | -0.047365 | 0.99772 | -0.043218 | 41.8323
67 | 0.1681 | 0.043012 | -0.16794 | -0.042907 | 0.00016606 | 0.00010545 | 0.25108 | 0.25108 | 0.25108 | 0.9975 | -0.047365 | 0.99643 | -0.067793 | 22.9926
68 | 0.038541 | 0.0096959 | -0.038537 | -0.0096936 | 3.763e-06 | 2.3697e-06 | 0.05787 | 0.05787 | 0.05787 | 0.99122 | -0.16808 | 0.99111 | -0.17013 | 15.8985
69 | 0.02312 | 0.0057991 | -0.023111 | -0.0057936 | 8.9941e-06 | 5.5027e-06 | 0.03481 | 0.03481 | 0.03481 | 0.98835 | -0.22357 | 0.98793 | -0.23174 | 9.5633
70 | -0.30742 | -0.078394 | 0.30791 | 0.078706 | 0.00048912 | 0.00031231 | 0.45897 | 0.45897 | 0.45897 | 0.99772 | -0.043218 | 0.99945 | -0.010321 | 42.0301
71 | 0.16677 | 0.042614 | -0.1667 | -0.042569 | 7.1273e-05 | 4.5257e-05 | 0.24934 | 0.24934 | 0.24934 | 0.99643 | -0.067793 | 0.99596 | -0.076635 | 22.833
72 | 0.031573 | 0.0079482 | -0.031556 | -0.0079375 | 1.7047e-05 | 1.065e-05 | 0.047415 | 0.047415 | 0.047415 | 0.99111 | -0.17013 | 0.99053 | -0.18143 | 13.026
73 | 0.016543 | 0.0041474 | -0.01654 | -0.0041458 | 2.7362e-06 | 1.6007e-06 | 0.024917 | 0.024917 | 0.024917 | 0.98793 | -0.23174 | 0.98775 | -0.23521 | 6.8453
74 | 0.14881 | 0.037839 | -0.14868 | -0.03776 | 0.00012474 | 7.9062e-05 | 0.22349 | 0.22349 | 0.22349 | 0.99164 | -0.15912 | 0.99073 | -0.17654 | 20.4662
75 | -0.15167 | -0.038556 | 0.1517 | 0.038575 | 2.8915e-05 | 1.8333e-05 | 0.22778 | 0.22778 | 0.22778 | 0.99164 | -0.15912 | 0.99185 | -0.15516 | 20.8593
76 | 0.14813 | 0.03762 | -0.14803 | -0.037562 | 9.2113e-05 | 5.8379e-05 | 0.22265 | 0.22265 | 0.22265 | 0.99073 | -0.17654 | 0.99006 | -0.18947 | 20.3894
77 | -0.15507 | -0.03942 | 0.1552 | 0.039504 | 0.00013145 | 8.3378e-05 | 0.23284 | 0.23284 | 0.23284 | 0.99185 | -0.15516 | 0.99277 | -0.13758 | 21.3228
78 | 0.028009 | 0.007035 | -0.028001 | -0.0070305 | 7.2557e-06 | 4.5033e-06 | 0.042101 | 0.042101 | 0.042101 | 0.99006 | -0.18947 | 0.98978 | -0.1949 | 11.5662
79 | -0.16198 | -0.041203 | 0.162 | 0.041216 | 2.0984e-05 | 1.3319e-05 | 0.243 | 0.243 | 0.243 | 0.99277 | -0.13758 | 0.99291 | -0.13489 | 22.2532
80 | 0.0018316 | 0.00045903 | -0.0018316 | -0.00045905 | 5.3913e-09 | -2.0919e-08 | 0.0027536 | 0.0027536 | 0.0027536 | 0.98978 | -0.1949 | 0.98978 | -0.19496 | 0.75649
81 | 0.02617 | 0.0065715 | -0.02616 | -0.0065658 | 9.3028e-06 | 5.748e-06 | 0.039347 | 0.039348 | 0.039348 | 0.98978 | -0.1949 | 0.9894 | -0.20235 | 10.8098
82 | -0.16283 | -0.041422 | 0.16309 | 0.041587 | 0.00025878 | 0.00016427 | 0.24424 | 0.24424 | 0.24424 | 0.99291 | -0.13489 | 0.99463 | -0.10197 | 22.3663
83 | 0.024182 | 0.0060698 | -0.024163 | -0.0060585 | 1.8498e-05 | 1.136e-05 | 0.036371 | 0.036372 | 0.036372 | 0.9894 | -0.20235 | 0.98857 | -0.2184 | 9.9922
84 | -0.16309 | -0.041587 | 0.16318 | 0.041647 | 9.4661e-05 | 6.0088e-05 | 0.24424 | 0.24424 | 0.24424 | 0.99463 | -0.10197 | 0.99526 | -0.089954 | 22.3663
85 | 0.00067291 | 0.00016846 | -0.00067291 | -0.00016865 | 5.8113e-09 | -1.8996e-07 | 0.0010128 | 0.0010129 | 0.0010129 | 0.98857 | -0.2184 | 0.98856 | -0.21858 | 0.27826
86 | 0.0090386 | 0.0022651 | -0.0090359 | -0.0022638 | 2.6804e-06 | 1.2205e-06 | 0.013605 | 0.013605 | 0.013605 | 0.98857 | -0.2184 | 0.98825 | -0.22463 | 3.7377
87 | 0.014452 | 0.0036249 | -0.014449 | -0.0036234 | 2.7418e-06 | 1.5567e-06 | 0.021754 | 0.021754 | 0.021754 | 0.98857 | -0.2184 | 0.98837 | -0.22238 | 5.9763
88 | -0.16402 | -0.041857 | 0.16409 | 0.041902 | 7.083e-05 | 4.4964e-05 | 0.24549 | 0.24549 | 0.24549 | 0.99526 | -0.089954 | 0.99573 | -0.081019 | 22.4812
89 | -0.30791 | -0.078706 | 0.30806 | 0.078804 | 0.00015381 | 9.8211e-05 | 0.45897 | 0.45897 | 0.45897 | 0.99945 | -0.010321 | 1 | 0 | 42.0301
90 | 0.16595 | 0.04238 | -0.16591 | -0.042358 | 3.5164e-05 | 2.2327e-05 | 0.24821 | 0.24821 | 0.24821 | 0.99596 | -0.076635 | 0.99573 | -0.081019 | 22.73
91 | 0.017514 | 0.0043924 | -0.017509 | -0.0043894 | 5.0909e-06 | 2.9961e-06 | 0.026062 | 0.026062 | 0.026062 | 1 | 0 | 0.99968 | -0.0061003 | 7.16
92 | 0.00594 | 0.0014879 | -0.0059398 | -0.0014879 | 2.0345e-07 | 4.3305e-08 | 0.0089436 | 0.0089436 | 0.0089436 | 0.98825 | -0.22463 | 0.98821 | -0.22535 | 2.457
93 | 0.013132 | 0.0032934 | -0.01313 | -0.0032921 | 2.3327e-06 | 1.289e-06 | 0.019771 | 0.019771 | 0.019771 | 0.98837 | -0.22238 | 0.98817 | -0.22611 | 5.4317
94 | 0.01784 | 0.0044784 | -0.017835 | -0.0044753 | 5.2619e-06 | 3.1325e-06 | 0.027252 | 0.027252 | 0.027252 | 0.97418 | -0.49837 | 0.97387 | -0.50456 | 7.4869
95 | 0.01695 | 0.0042537 | -0.016944 | -0.0042497 | 6.6804e-06 | 3.9452e-06 | 0.025901 | 0.025901 | 0.025901 | 0.97387 | -0.50456 | 0.97345 | -0.51283 | 7.1157
96 | 0.016563 | 0.0041543 | -0.01656 | -0.0041524 | 3.2731e-06 | 1.9255e-06 | 0.025319 | 0.025319 | 0.025319 | 0.97345 | -0.51283 | 0.97324 | -0.51697 | 6.9559
97 | 0.01454 | 0.0036463 | -0.014539 | -0.0036454 | 1.589e-06 | 9.1045e-07 | 0.022232 | 0.022232 | 0.022232 | 0.97324 | -0.51697 | 0.97312 | -0.51927 | 6.1077
98 | 0.013759 | 0.0034501 | -0.013756 | -0.0034484 | 3.0548e-06 | 1.7265e-06 | 0.02104 | 0.02104 | 0.02104 | 0.97312 | -0.51927 | 0.97289 | -0.52393 | 5.7803
99 | -0.05849 | -0.014739 | 0.058512 | 0.014753 | 2.2617e-05 | 1.4379e-05 | 0.088932 | 0.088932 | 0.088932 | 0.97897 | -0.40433 | 0.97939 | -0.39625 | 24.4319
100 | 0.010876 | 0.0027271 | -0.010872 | -0.0027251 | 3.9778e-06 | 2.0393e-06 | 0.016377 | 0.016377 | 0.016377 | 0.98817 | -0.22611 | 0.98778 | -0.23379 | 4.4993
101 | 0.0098423 | 0.0024672 | -0.0098396 | -0.0024658 | 2.7099e-06 | 1.3137e-06 | 0.014827 | 0.014827 | 0.014827 | 0.98778 | -0.23379 | 0.98748 | -0.23957 | 4.0733
102 | 0.0098396 | 0.0024658 | -0.0098361 | -0.0024641 | 3.5064e-06 | 1.7002e-06 | 0.014827 | 0.014827 | 0.014827 | 0.98748 | -0.23957 | 0.9871 | -0.24705 | 4.0734
103 | 0.00092454 | 0.00023136 | -0.00092452 | -0.00023171 | 2.0362e-08 | -3.4593e-07 | 0.001392 | 0.0013921 | 0.0013921 | 0.98821 | -0.22535 | 0.98819 | -0.22581 | 0.38246
104 | 0.0050152 | 0.0012565 | -0.005015 | -0.0012565 | 2.5202e-07 | 1.0315e-08 | 0.0075516 | 0.0075516 | 0.0075516 | 0.98821 | -0.22535 | 0.98816 | -0.2264 | 2.0746
105 | 0.0064492 | 0.0016153 | -0.0064479 | -0.0016149 | 1.3246e-06 | 3.701e-07 | 0.0097216 | 0.0097217 | 0.0097217 | 0.9871 | -0.24705 | 0.98688 | -0.25136 | 2.6708
106 | 0.0042948 | 0.001076 | -0.0042944 | -0.0010761 | 3.9534e-07 | -6.9846e-08 | 0.0064672 | 0.0064673 | 0.0064673 | 0.98816 | -0.2264 | 0.98806 | -0.22833 | 1.7767
107 | 0.0029651 | 0.00074207 | -0.0029649 | -0.00074232 | 2.3565e-07 | -2.509e-07 | 0.0044704 | 0.0044706 | 0.0044706 | 0.98688 | -0.25136 | 0.98679 | -0.25303 | 1.2282
108 | 0.0024474 | 0.00061317 | -0.0024474 | -0.00061319 | 1.0912e-08 | -2.0451e-08 | 0.0036857 | 0.0036857 | 0.0036857 | 0.98806 | -0.22833 | 0.98806 | -0.22843 | 1.0126
109 | -0.0025299 | -0.00063391 | 0.0025299 | 0.00063391 | 2.0726e-09 | -3.4394e-09 | 0.0038319 | 0.0038319 | 0.0038319 | 0.98241 | -0.33739 | 0.98241 | -0.33737 | 1.0527
110 | 0.0013977 | 0.00035016 | -0.0013976 | -0.00035028 | 1.8463e-08 | -1.2728e-07 | 0.0021169 | 0.002117 | 0.002117 | 0.98241 | -0.33739 | 0.98239 | -0.33766 | 0.58159
111 | 0.012909 | 0.0032363 | -0.012907 | -0.003235 | 2.2664e-06 | 1.2528e-06 | 0.019614 | 0.019614 | 0.019614 | 0.97939 | -0.39625 | 0.9792 | -0.39993 | 5.3884
112 | 0.01242 | 0.0031134 | -0.012416 | -0.0031112 | 4.0456e-06 | 2.2181e-06 | 0.018996 | 0.018997 | 0.018997 | 0.97289 | -0.52393 | 0.97254 | -0.53076 | 5.2188
113 | 0.010681 | 0.0026763 | -0.010679 | -0.0026753 | 2.0005e-06 | 1.0325e-06 | 0.016342 | 0.016342 | 0.016342 | 0.97254 | -0.53076 | 0.97234 | -0.5347 | 4.4895
114 | 0.0055449 | 0.0013889 | -0.0055446 | -0.0013889 | 2.6136e-07 | 4.7212e-08 | 0.0084853 | 0.0084854 | 0.0084854 | 0.97234 | -0.5347 | 0.97229 | -0.53569 | 2.3311
115 | 0.0051338 | 0.0012864 | -0.0051334 | -0.0012863 | 3.589e-07 | 3.7383e-08 | 0.0078564 | 0.0078564 | 0.0078564 | 0.97234 | -0.5347 | 0.97227 | -0.53617 | 2.1584
116 | 0.0055446 | 0.0013889 | -0.005544 | -0.0013888 | 6.3707e-07 | 1.1514e-07 | 0.0084854 | 0.0084855 | 0.0084855 | 0.97229 | -0.53569 | 0.97217 | -0.5381 | 2.3312
117 | 0.0024154 | 0.00060511 | -0.0024152 | -0.00060532 | 1.1393e-07 | -2.028e-07 | 0.0036965 | 0.0036966 | 0.0036966 | 0.97227 | -0.53617 | 0.97222 | -0.53716 | 1.0156
118 | 0.0029649 | 0.00074232 | -0.0029648 | -0.00074243 | 1.0608e-07 | -1.1292e-07 | 0.0044706 | 0.0044706 | 0.0044706 | 0.98679 | -0.25303 | 0.98675 | -0.25378 | 1.2282
119 | 0.0022006 | 0.0005509 | -0.0022005 | -0.00055098 | 3.0566e-08 | -7.5e-08 | 0.0033182 | 0.0033182 | 0.0033182 | 0.98675 | -0.25378 | 0.98674 | -0.25408 | 0.9116
120 | -0.0053261 | -0.0013348 | 0.0053261 | 0.0013348 | 3.0937e-10 | 2.6263e-11 | 0.008035 | 0.008035 | 0.008035 | 0.98635 | -0.26259 | 0.98635 | -0.26259 | 2.2074
121 | -0.0094128 | -0.0023591 | 0.0094164 | 0.0023608 | 3.5465e-06 | 1.6709e-06 | 0.0142 | 0.0142 | 0.0142 | 0.98635 | -0.26259 | 0.98676 | -0.25468 | 3.9012
122 | 0.0017984 | 0.00045019 | -0.0017983 | -0.00045048 | 7.3889e-08 | -2.9494e-07 | 0.0027118 | 0.0027119 | 0.0027119 | 0.98674 | -0.25408 | 0.98669 | -0.25494 | 0.74502
123 | 0.0011586 | 0.00029015 | -0.0011585 | -0.00029036 | 1.9581e-08 | -2.0595e-07 | 0.0017471 | 0.0017472 | 0.0017472 | 0.98669 | -0.25494 | 0.98668 | -0.25529 | 0.48
124 | 0.0017 | 0.00042588 | -0.0017 | -0.00042605 | 3.7957e-08 | -1.7348e-07 | 0.0025602 | 0.0025602 | 0.0025602 | 0.98806 | -0.22843 | 0.98803 | -0.2289 | 0.70336
125 | -0.024832 | -0.0062388 | 0.024848 | 0.0062487 | 1.6046e-05 | 9.8762e-06 | 0.037369 | 0.037369 | 0.037369 | 0.98895 | -0.21209 | 0.98964 | -0.19856 | 10.2663
126 | -0.026671 | -0.0067056 | 0.026693 | 0.0067191 | 2.1834e-05 | 1.3509e-05 | 0.04011 | 0.04011 | 0.04011 | 0.98964 | -0.19856 | 0.99053 | -0.18143 | 11.0193
127 | 0.0048625 | 0.0012184 | -0.0048623 | -0.0012184 | 1.7986e-07 | -5.9092e-10 | 0.0073046 | 0.0073046 | 0.0073046 | 0.99053 | -0.18143 | 0.99049 | -0.18221 | 2.0068
128 | 0.0048623 | 0.0012184 | -0.0048621 | -0.0012184 | 2.564e-07 | -8.2397e-10 | 0.0073046 | 0.0073047 | 0.0073047 | 0.99049 | -0.18221 | 0.99043 | -0.18331 | 2.0068
129 | 0.00072967 | 0.0001827 | -0.00072967 | -0.00018287 | 6.198e-09 | -1.7303e-07 | 0.0010962 | 0.0010963 | 0.0010963 | 0.99043 | -0.18331 | 0.99042 | -0.18349 | 0.30117
130 | 0.0078775 | 0.0019746 | -0.0078758 | -0.0019739 | 1.6732e-06 | 6.7928e-07 | 0.011971 | 0.011971 | 0.011971 | 0.9792 | -0.39993 | 0.97897 | -0.40439 | 3.2888
131 | 0.0029386 | 0.00073578 | -0.0029383 | -0.00073606 | 2.85e-07 | -2.8339e-07 | 0.0044976 | 0.0044977 | 0.0044977 | 0.97217 | -0.5381 | 0.97207 | -0.54014 | 1.2356
132 | 0.0018527 | 0.00046398 | -0.0018526 | -0.0004643 | 9.205e-08 | -3.1942e-07 | 0.0028359 | 0.002836 | 0.002836 | 0.97207 | -0.54014 | 0.97201 | -0.54118 | 0.77913
133 | -0.0015266 | -0.00038261 | 0.0015266 | 0.00038255 | 1.0091e-08 | -6.178e-08 | 0.0022731 | 0.0022731 | 0.0022731 | 0.99936 | -0.012351 | 0.99936 | -0.012212 | 0.62448
134 | 0.0080962 | 0.0020294 | -0.0080943 | -0.0020286 | 1.9419e-06 | 7.7606e-07 | 0.012055 | 0.012055 | 0.012055 | 0.99936 | -0.012212 | 0.9991 | -0.017247 | 3.3119
135 | -0.0096229 | -0.0024119 | 0.0096246 | 0.0024127 | 1.6753e-06 | 7.8699e-07 | 0.014328 | 0.014328 | 0.014328 | 0.99936 | -0.012212 | 0.99955 | -0.0085585 | 3.9363
136 | 0.015244 | 0.0038217 | -0.015242 | -0.0038207 | 1.7854e-06 | 1.0215e-06 | 0.022691 | 0.022691 | 0.022691 | 0.99968 | -0.0061003 | 0.99955 | -0.0085585 | 6.2339
137 | 0.0038864 | 0.00097348 | -0.0038861 | -0.00097358 | 2.6279e-07 | -9.3493e-08 | 0.0058545 | 0.0058546 | 0.0058546 | 0.98775 | -0.23521 | 0.98768 | -0.23663 | 1.6084
138 | 0.012654 | 0.0031723 | -0.012652 | -0.0031713 | 1.7634e-06 | 9.6299e-07 | 0.019063 | 0.019063 | 0.019063 | 0.98775 | -0.23521 | 0.9876 | -0.23813 | 5.237
139 | 0.0038861 | 0.00097358 | -0.0038858 | -0.00097369 | 3.197e-07 | -1.1368e-07 | 0.0058546 | 0.0058547 | 0.0058547 | 0.98768 | -0.23663 | 0.98759 | -0.23836 | 1.6084
140 | 0.011272 | 0.0028256 | -0.01127 | -0.0028246 | 1.8846e-06 | 9.8327e-07 | 0.016984 | 0.016984 | 0.016984 | 0.9876 | -0.23813 | 0.98742 | -0.24164 | 4.666
141 | 0.0011825 | 0.0002962 | -0.0011825 | -0.00029637 | 1.7132e-08 | -1.7318e-07 | 0.0017817 | 0.0017818 | 0.0017818 | 0.98759 | -0.23836 | 0.98758 | -0.23866 | 0.48949
142 | 0.0022883 | 0.00057348 | -0.0022883 | -0.00057349 | 6.396e-09 | -1.4254e-08 | 0.0034484 | 0.0034484 | 0.0034484 | 0.98742 | -0.24164 | 0.98742 | -0.2417 | 0.94735

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33039 | 0.08399

## res_load
| p_mw | q_mvar
0 | 0.004677 | 0.0011722
1 | 0.001432 | 0.00035888
2 | 0.00078649 | 0.00019711
3 | 0.0015128 | 0.00037915
4 | 0.0032299 | 0.00080948
5 | 0.0062826 | 0.0015746
6 | 0.0022737 | 0.00056985
7 | 0.0050684 | 0.0012703
8 | 0.0063224 | 0.0015845
9 | 0.001631 | 0.00040876
10 | 0.0055887 | 0.0014006
11 | 0.0034981 | 0.0008767
12 | 0.0013694 | 0.0003432
13 | 0.0013023 | 0.00032639
14 | 0.0019888 | 0.00049843
15 | 0.001779 | 0.00044587
16 | 0.0072242 | 0.0018106
17 | 0.0014093 | 0.00035321
18 | 0.0090726 | 0.0022738
19 | 0.00064807 | 0.00016242
20 | 0.00017867 | 4.4778e-05
21 | 0.0019614 | 0.00049158
22 | 0.00060719 | 0.00015218
23 | 0.0037298 | 0.00093478
24 | 0.0048246 | 0.0012092
25 | 0.00083589 | 0.00020949
26 | 0.0027729 | 0.00069495
27 | 0.010141 | 0.0025415
28 | 0.0079733 | 0.0019983
29 | 0.0034187 | 0.0008568
30 | 0.0049452 | 0.0012394
31 | 0.0071027 | 0.0017801
32 | 0.010108 | 0.0025334
33 | 0.012278 | 0.0030771
34 | 0.0089429 | 0.0022413
35 | 0.0010112 | 0.00025343
36 | 0.0012481 | 0.0003128
37 | 0.001582 | 0.00039647
38 | 0.0012094 | 0.0003031
39 | 0.00080022 | 0.00020055
40 | 0.0016333 | 0.00040934
41 | 0.0014715 | 0.00036878
42 | 0.0036335 | 0.00091063
43 | 0.0014509 | 0.00036363
44 | 0.0014486 | 0.00036305
45 | 0.0011673 | 0.00029256
46 | 0.0069642 | 0.0017454
47 | 0.0065684 | 0.0016462
48 | 0.0028607 | 0.00071696
49 | 0.00055867 | 0.00014002
50 | 0.0033736 | 0.00084551
51 | 0.0067788 | 0.0016989
52 | 0.0008245 | 0.00020664
53 | 0.0018316 | 0.00045905
54 | 0.0019788 | 0.00049594
55 | 0.00083912 | 0.0002103
56 | 0.00075304 | 0.00018873
57 | 0.0031647 | 0.00079315
58 | 0.0018182 | 0.00045568
59 | 0.00067291 | 0.00016865
60 | 0.003096 | 0.00077592
61 | 0.0013168 | 0.00033002
62 | 0.00011234 | 2.8155e-05
63 | 0.00088437 | 0.00022164
64 | 0.00038068 | 9.5407e-05
65 | 0.0020193 | 0.00050609
66 | 0.0007793 | 0.00019531
67 | 0.0070701 | 0.0017719
68 | 0.0022541 | 0.00056494
69 | 0.0010292 | 0.00025795
70 | 0.0033869 | 0.00084883
71 | 0.00092452 | 0.00023171
72 | 0.00072015 | 0.00018049
73 | 0.0034828 | 0.00087286
74 | 0.001847 | 0.00046291
75 | 0.0011322 | 0.00028376
76 | 0.0028369 | 0.00071098
77 | 0.0013976 | 0.00035028
78 | 0.0013364 | 0.00033494
79 | 0.0017352 | 0.00043488
80 | 0.0027181 | 0.00068122
81 | 0.00076421 | 0.00019153
82 | 0.0053261 | 0.0013348
83 | 0.0040868 | 0.0010242
84 | 0.00040217 | 0.00010079
85 | 0.0008688 | 0.00021774
86 | 0.00063972 | 0.00016033
87 | 0.00074737 | 0.00018731
88 | 0.0017 | 0.00042605
89 | 0.0022267 | 0.00055807
90 | 0.0018232 | 0.00045693
91 | 0.0041324 | 0.0010357
92 | 0.00072967 | 0.00018287
93 | 0.0050293 | 0.0012605
94 | 0.0026054 | 0.00065298
95 | 0.0024152 | 0.00060532
96 | 0.0010856 | 0.00027209
97 | 0.0015266 | 0.00038261
98 | 0.0022649 | 0.00056763
99 | 0.0018526 | 0.0004643
100 | 0.0056179 | 0.001408
101 | 0.0080943 | 0.0020286
102 | 0.0011585 | 0.00029036
103 | 0.0013795 | 0.00034573
104 | 0.0027032 | 0.00067749
105 | 0.0089822 | 0.0022512
106 | 0.0022883 | 0.00057349
107 | 0.0011825 | 0.00029637
108 | 0.0019988 | 0.00050094
109 | 0.0078758 | 0.0019739

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1