## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2523-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2523-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2523-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2523-1_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2523-1_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2523-1_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2523-1_0_3_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_2523-1_0_3_node_88 | 0.4 | n |  | TRUE
8 | bus_LV_2523-1_0_3_node_95 | 0.4 | n |  | TRUE
9 | bus_LV_2523-1_0_3_node_101 | 0.4 | n |  | TRUE
10 | bus_LV_2523-1_0_3_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_2523-1_0_3_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_2523-1_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2523-1_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2523-1_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2523-1_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2523-1_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2523-1_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2523-1_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2523-1_0_3_node_86 | 0.4 | n |  | TRUE
20 | bus_LV_2523-1_0_3_node_85 | 0.4 | n |  | TRUE
21 | bus_LV_2523-1_0_3_node_67 | 0.4 | n |  | TRUE
22 | bus_LV_2523-1_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2523-1_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2523-1_0_3_node_82 | 0.4 | n |  | TRUE
25 | bus_LV_2523-1_0_3_node_54 | 0.4 | n |  | TRUE
26 | bus_LV_2523-1_0_3_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_2523-1_0_3_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2523-1_0_3_node_59 | 0.4 | n |  | TRUE
29 | bus_LV_2523-1_0_3_node_90 | 0.4 | n |  | TRUE
30 | bus_LV_2523-1_0_3_node_60 | 0.4 | n |  | TRUE
31 | bus_LV_2523-1_0_3_node_92 | 0.4 | n |  | TRUE
32 | bus_LV_2523-1_0_3_node_89 | 0.4 | n |  | TRUE
33 | bus_LV_2523-1_0_3_node_115 | 0.4 | n |  | TRUE
34 | bus_LV_2523-1_0_3_node_116 | 0.4 | n |  | TRUE
35 | bus_LV_2523-1_0_3_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_2523-1_0_3_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_2523-1_0_3_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_2523-1_0_3_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_2523-1_0_3_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_2523-1_0_3_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_2523-1_0_3_node_43 | 0.4 | n |  | TRUE
42 | bus_LV_2523-1_0_3_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2523-1_0_3_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_2523-1_0_3_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_2523-1_0_3_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_2523-1_0_3_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_2523-1_0_3_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_2523-1_0_3_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_2523-1_0_3_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_2523-1_0_3_node_35 | 0.4 | n |  | TRUE
51 | bus_LV_2523-1_0_3_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_2523-1_0_3_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_2523-1_0_3_node_30 | 0.4 | n |  | TRUE
54 | bus_LV_2523-1_0_3_node_32 | 0.4 | n |  | TRUE
55 | bus_LV_2523-1_0_3_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_2523-1_0_3_node_34 | 0.4 | n |  | TRUE
57 | bus_LV_2523-1_0_3_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_2523-1_0_3_node_37 | 0.4 | n |  | TRUE
59 | bus_LV_2523-1_0_3_node_38 | 0.4 | n |  | TRUE
60 | bus_LV_2523-1_0_3_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_2523-1_0_3_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_2523-1_0_3_node_40 | 0.4 | n |  | TRUE
63 | bus_LV_2523-1_0_3_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_2523-1_0_3_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_2523-1_0_3_node_53 | 0.4 | n |  | TRUE
66 | bus_LV_2523-1_0_3_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_2523-1_0_3_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_2523-1_0_3_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_2523-1_0_3_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_2523-1_0_3_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_2523-1_0_3_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_2523-1_0_3_node_56 | 0.4 | n |  | TRUE
73 | bus_LV_2523-1_0_3_node_57 | 0.4 | n |  | TRUE
74 | bus_LV_2523-1_0_3_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_2523-1_0_3_node_64 | 0.4 | n |  | TRUE
76 | bus_LV_2523-1_0_3_node_61 | 0.4 | n |  | TRUE
77 | bus_LV_2523-1_0_3_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_2523-1_0_3_node_105 | 0.4 | n |  | TRUE
79 | bus_LV_2523-1_0_3_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_2523-1_0_3_node_103 | 0.4 | n |  | TRUE
81 | bus_LV_2523-1_0_3_node_104 | 0.4 | n |  | TRUE
82 | bus_LV_2523-1_0_3_node_68 | 0.4 | n |  | TRUE
83 | bus_LV_2523-1_0_3_node_69 | 0.4 | n |  | TRUE
84 | bus_LV_2523-1_0_3_node_70 | 0.4 | n |  | TRUE
85 | bus_LV_2523-1_0_3_node_71 | 0.4 | n |  | TRUE
86 | bus_LV_2523-1_0_3_node_72 | 0.4 | n |  | TRUE
87 | bus_LV_2523-1_0_3_node_76 | 0.4 | n |  | TRUE
88 | bus_LV_2523-1_0_3_node_83 | 0.4 | n |  | TRUE
89 | bus_LV_2523-1_0_3_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_2523-1_0_3_node_80 | 0.4 | n |  | TRUE
91 | bus_LV_2523-1_0_3_node_73 | 0.4 | n |  | TRUE
92 | bus_LV_2523-1_0_3_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_2523-1_0_3_node_93 | 0.4 | n |  | TRUE
94 | bus_LV_2523-1_0_3_node_94 | 0.4 | n |  | TRUE
95 | bus_LV_2523-1_0_3_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_2523-1_0_3_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_2523-1_0_3_node_79 | 0.4 | n |  | TRUE
98 | bus_LV_2523-1_0_3_node_81 | 0.4 | n |  | TRUE
99 | bus_LV_2523-1_0_3_node_84 | 0.4 | n |  | TRUE
100 | bus_LV_2523-1_0_3_node_87 | 0.4 | n |  | TRUE
101 | bus_LV_2523-1_0_3_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_2523-1_0_3_node_96 | 0.4 | n |  | TRUE
103 | bus_LV_2523-1_0_3_node_97 | 0.4 | n |  | TRUE
104 | bus_LV_2523-1_0_3_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_2523-1_0_3_node_99 | 0.4 | n |  | TRUE
106 | bus_LV_2523-1_0_3_node_100 | 0.4 | n |  | TRUE
107 | bus_LV_2523-1_0_3_node_106 | 0.4 | n |  | TRUE
108 | bus_LV_2523-1_0_3_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_2523-1_0_3_node_109 | 0.4 | n |  | TRUE
110 | bus_LV_2523-1_0_3_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_2523-1_0_3_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_2523-1_0_3_node_102 | 0.4 | n |  | TRUE
113 | bus_LV_2523-1_0_3_node_108 | 0.4 | n |  | TRUE
114 | bus_LV_2523-1_0_3_node_111 | 0.4 | n |  | TRUE
115 | bus_LV_2523-1_0_3_node_112 | 0.4 | n |  | TRUE
116 | bus_LV_2523-1_0_3_node_114 | 0.4 | n |  | TRUE
117 | bus_MV_392_1_node_131 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2523-1_0_3_load_0 | 0 | 0.0010985 | 0.00027531 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2523-1_0_3_load_1 | 1 | 0.0011013 | 0.00027601 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2523-1_0_3_load_3 | 3 | 0.0014826 | 0.00037157 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2523-1_0_3_load_4 | 4 | 0.001428 | 0.00035788 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2523-1_0_3_load_5 | 5 | 0.0020913 | 0.00052412 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2523-1_0_3_load_88 | 7 | 0.00070628 | 0.00017701 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2523-1_0_3_load_95 | 8 | 0.0022993 | 0.00057626 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2523-1_0_3_load_101 | 9 | 0.0014002 | 0.00035093 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2523-1_0_3_load_16 | 10 | 0.0010298 | 0.00025809 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2523-1_0_3_load_6 | 12 | 0.0017795 | 0.00044599 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2523-1_0_3_load_7 | 13 | 0.0023945 | 0.00060011 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2523-1_0_3_load_9 | 15 | 0.001208 | 0.00030274 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2523-1_0_3_load_86 | 19 | 0.0017096 | 0.00042846 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2523-1_0_3_load_85 | 20 | 0.016643 | 0.0041711 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2523-1_0_3_load_67 | 21 | 0.0038592 | 0.0009672 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2523-1_0_3_load_13 | 22 | 0.0022173 | 0.0005557 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2523-1_0_3_load_14 | 23 | 0.0026404 | 0.00066175 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2523-1_0_3_load_82 | 24 | 0.0020571 | 0.00051555 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2523-1_0_3_load_54 | 25 | 0.001705 | 0.0004273 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2523-1_0_3_load_66 | 26 | 0.0014232 | 0.00035669 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2523-1_0_3_load_23 | 27 | 0.0018223 | 0.00045671 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2523-1_0_3_load_59 | 28 | 0.0013706 | 0.00034349 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2523-1_0_3_load_89 | 32 | 0.0048613 | 0.0012184 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2523-1_0_3_load_115 | 33 | 0.070914 | 0.017773 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2523-1_0_3_load_18 | 35 | 0.0026236 | 0.00065754 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2523-1_0_3_load_19 | 36 | 0.0015156 | 0.00037983 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2523-1_0_3_load_21 | 38 | 0.0025668 | 0.0006433 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2523-1_0_3_load_22 | 39 | 0.0017662 | 0.00044265 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2523-1_0_3_load_45 | 40 | 0.0027843 | 0.0006978 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2523-1_0_3_load_24 | 42 | 0.0013545 | 0.00033947 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2523-1_0_3_load_25 | 43 | 0.0016352 | 0.00040982 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2523-1_0_3_load_27 | 45 | 0.0033974 | 0.00085148 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2523-1_0_3_load_28 | 46 | 0.00028783 | 7.2137e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2523-1_0_3_load_29 | 47 | 0.0018354 | 0.00046001 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2523-1_0_3_load_36 | 49 | 0.00024778 | 6.2099e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2523-1_0_3_load_35 | 50 | 0.0011074 | 0.00027754 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2523-1_0_3_load_48 | 51 | 0.002007 | 0.000503 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2523-1_0_3_load_30 | 53 | 0.00079929 | 0.00020032 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2523-1_0_3_load_33 | 55 | 0.0037522 | 0.00094038 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2523-1_0_3_load_34 | 56 | 0.003308 | 0.00082906 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2523-1_0_3_load_58 | 57 | 0.00082077 | 0.0002057 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2523-1_0_3_load_37 | 58 | 0.002891 | 0.00072457 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2523-1_0_3_load_38 | 59 | 0.0030446 | 0.00076305 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2523-1_0_3_load_39 | 60 | 0.002023 | 0.000507 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2523-1_0_3_load_50 | 61 | 0.0039727 | 0.00099566 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2523-1_0_3_load_40 | 62 | 0.0017633 | 0.00044192 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2523-1_0_3_load_51 | 63 | 0.0028312 | 0.00070958 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2523-1_0_3_load_53 | 65 | 0.0025032 | 0.00062737 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2523-1_0_3_load_47 | 67 | 0.00096283 | 0.00024131 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2523-1_0_3_load_42 | 68 | 0.0014282 | 0.00035795 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2523-1_0_3_load_44 | 69 | 0.0011158 | 0.00027964 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2523-1_0_3_load_49 | 70 | 0.0011558 | 0.00028967 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2523-1_0_3_load_57 | 73 | 0.0016243 | 0.00040708 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2523-1_0_3_load_62 | 74 | 0.0032446 | 0.00081318 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2523-1_0_3_load_64 | 75 | 0.0017276 | 0.00043297 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2523-1_0_3_load_61 | 76 | 0.0034127 | 0.0008553 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2523-1_0_3_load_65 | 77 | 0.0011148 | 0.00027939 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2523-1_0_3_load_63 | 79 | 0.006552 | 0.0016421 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2523-1_0_3_load_68 | 82 | 0.0024305 | 0.00060913 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2523-1_0_3_load_69 | 83 | 0.0021732 | 0.00054465 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2523-1_0_3_load_72 | 86 | 0.0018637 | 0.00046708 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2523-1_0_3_load_76 | 87 | 0.00096872 | 0.00024278 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2523-1_0_3_load_83 | 88 | 0.0058907 | 0.0014763 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2523-1_0_3_load_73 | 91 | 0.00091358 | 0.00022896 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2523-1_0_3_load_93 | 93 | 0.00047395 | 0.00011878 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2523-1_0_3_load_94 | 94 | 0.00072396 | 0.00018144 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2523-1_0_3_load_77 | 95 | 0.00049255 | 0.00012344 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2523-1_0_3_load_78 | 96 | 0.001519 | 0.0003807 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2523-1_0_3_load_81 | 98 | 0.00045183 | 0.00011324 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2523-1_0_3_load_84 | 99 | 0.00075317 | 0.00018876 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2523-1_0_3_load_87 | 100 | 0.00065515 | 0.0001642 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2523-1_0_3_load_91 | 101 | 0.00048824 | 0.00012237 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2523-1_0_3_load_96 | 102 | 0.0013897 | 0.0003483 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2523-1_0_3_load_98 | 104 | 0.006164 | 0.0015448 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2523-1_0_3_load_99 | 105 | 0.0012354 | 0.00030962 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2523-1_0_3_load_106 | 107 | 0.001665 | 0.0004173 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2523-1_0_3_load_110 | 108 | 0.00084007 | 0.00021054 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2523-1_0_3_load_109 | 109 | 0.0008468 | 0.00021223 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2523-1_0_3_load_107 | 110 | 0.0010793 | 0.0002705 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2523-1_0_3_load_102 | 112 | 0.0016403 | 0.00041111 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2523-1_0_3_load_108 | 113 | 0.0022925 | 0.00057456 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2523-1_0_3_load_111 | 114 | 0.0014738 | 0.00036937 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2523-1_0_3_load_112 | 115 | 0.0045648 | 0.001144 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2523-1_0_3_load_114 | 116 | 0.0010033 | 0.00025146 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2523-1_0_3_line_0 |  | 0 | 1 | 0.01948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2523-1_0_3_line_1 |  | 0 | 2 | 0.012188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2523-1_0_3_line_2 |  | 1 | 3 | 0.014989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2523-1_0_3_line_3 |  | 2 | 4 | 0.036043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2523-1_0_3_line_4 |  | 2 | 5 | 0.01434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2523-1_0_3_line_5 |  | 4 | 6 | 0.018988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2523-1_0_3_line_6 |  | 5 | 7 | 0.016188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2523-1_0_3_line_7 |  | 6 | 10 | 0.012087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2523-1_0_3_line_8 |  | 6 | 11 | 0.007003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2523-1_0_3_line_9 |  | 8 | 9 | 0.00028508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2523-1_0_3_line_10 |  | 9 | 80 | 0.023957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2523-1_0_3_line_11 |  | 10 | 28 | 0.011664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2523-1_0_3_line_12 |  | 11 | 29 | 0.032393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2523-1_0_3_line_13 |  | 12 | 13 | 0.022926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2523-1_0_3_line_14 |  | 12 | 14 | 0.060485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2523-1_0_3_line_15 |  | 13 | 15 | 0.027562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2523-1_0_3_line_16 |  | 14 | 16 | 0.005682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2523-1_0_3_line_17 |  | 14 | 17 | 0.013636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2523-1_0_3_line_18 |  | 15 | 18 | 0.016399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2523-1_0_3_line_19 |  | 16 | 19 | 0.017584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2523-1_0_3_line_20 |  | 16 | 20 | 0.04755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2523-1_0_3_line_21 |  | 17 | 21 | 0.060191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2523-1_0_3_line_22 |  | 18 | 22 | 0.0087786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2523-1_0_3_line_23 |  | 18 | 23 | 0.036972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2523-1_0_3_line_24 |  | 19 | 24 | 0.021017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2523-1_0_3_line_25 |  | 22 | 25 | 0.011819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2523-1_0_3_line_26 |  | 23 | 26 | 0.020231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2523-1_0_3_line_27 |  | 24 | 97 | 0.014023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_2523-1_0_3_line_28 |  | 25 | 27 | 0.0083365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2523-1_0_3_line_29 |  | 27 | 37 | 0.011803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2523-1_0_3_line_30 |  | 28 | 30 | 0.033605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2523-1_0_3_line_31 |  | 29 | 31 | 0.029794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2523-1_0_3_line_32 |  | 29 | 32 | 0.017835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2523-1_0_3_line_33 |  | 30 | 77 | 0.00349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2523-1_0_3_line_34 |  | 30 | 75 | 0.031958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2523-1_0_3_line_35 |  | 31 | 34 | 0.010468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_2523-1_0_3_line_36 |  | 31 | 86 | 0.0069952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_2523-1_0_3_line_37 |  | 32 | 101 | 0.028608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2523-1_0_3_line_38 |  | 33 | 34 | 0.029375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2523-1_0_3_line_39 |  | 35 | 36 | 0.015783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2523-1_0_3_line_40 |  | 35 | 37 | 0.033049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2523-1_0_3_line_41 |  | 36 | 38 | 0.014348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2523-1_0_3_line_42 |  | 37 | 39 | 0.015267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2523-1_0_3_line_43 |  | 39 | 40 | 0.0096396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2523-1_0_3_line_44 |  | 40 | 41 | 0.016171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2523-1_0_3_line_45 |  | 41 | 68 | 0.023316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2523-1_0_3_line_46 |  | 41 | 48 | 0.034091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2523-1_0_3_line_47 |  | 42 | 43 | 0.068811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2523-1_0_3_line_48 |  | 42 | 44 | 0.013722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2523-1_0_3_line_49 |  | 43 | 45 | 0.0045184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2523-1_0_3_line_50 |  | 44 | 46 | 0.0074578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2523-1_0_3_line_51 |  | 44 | 47 | 0.045118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2523-1_0_3_line_52 |  | 45 | 48 | 0.023467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2523-1_0_3_line_53 |  | 46 | 49 | 0.018126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2523-1_0_3_line_54 |  | 47 | 50 | 0.022278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2523-1_0_3_line_55 |  | 48 | 51 | 0.035863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2523-1_0_3_line_56 |  | 50 | 52 | 0.050731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2523-1_0_3_line_57 |  | 51 | 66 | 0.0033664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2523-1_0_3_line_58 |  | 52 | 53 | 0.011844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2523-1_0_3_line_59 |  | 53 | 54 | 0.097207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2523-1_0_3_line_60 |  | 54 | 55 | 0.023421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2523-1_0_3_line_61 |  | 54 | 56 | 0.025629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2523-1_0_3_line_62 |  | 56 | 57 | 0.015887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2523-1_0_3_line_63 |  | 58 | 59 | 0.022511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2523-1_0_3_line_64 |  | 58 | 60 | 0.025038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2523-1_0_3_line_65 |  | 59 | 61 | 0.053776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2523-1_0_3_line_66 |  | 60 | 62 | 0.023674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2523-1_0_3_line_67 |  | 61 | 63 | 0.02075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2523-1_0_3_line_68 |  | 62 | 66 | 0.018117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2523-1_0_3_line_69 |  | 63 | 64 | 0.011687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2523-1_0_3_line_70 |  | 64 | 65 | 0.052857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2523-1_0_3_line_71 |  | 66 | 67 | 0.0075677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2523-1_0_3_line_72 |  | 67 | 70 | 0.016143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2523-1_0_3_line_73 |  | 68 | 69 | 0.021935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2523-1_0_3_line_74 |  | 71 | 72 | 0.045034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2523-1_0_3_line_75 |  | 71 | 73 | 0.042781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2523-1_0_3_line_76 |  | 72 | 74 | 0.00037073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2523-1_0_3_line_77 |  | 72 | 75 | 0.04729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2523-1_0_3_line_78 |  | 74 | 76 | 0.023943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2523-1_0_3_line_79 |  | 76 | 79 | 0.066185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2523-1_0_3_line_80 |  | 77 | 78 | 0.036262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2523-1_0_3_line_81 |  | 78 | 80 | 0.038736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2523-1_0_3_line_82 |  | 78 | 81 | 0.024126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2523-1_0_3_line_83 |  | 80 | 112 | 0.0085227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2523-1_0_3_line_84 |  | 81 | 113 | 0.018121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2523-1_0_3_line_85 |  | 81 | 114 | 0.029633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2523-1_0_3_line_86 |  | 82 | 83 | 0.028667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2523-1_0_3_line_87 |  | 82 | 84 | 0.019038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2523-1_0_3_line_88 |  | 84 | 85 | 0.062969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_2523-1_0_3_line_89 |  | 84 | 86 | 0.025174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_2523-1_0_3_line_90 |  | 85 | 87 | 0.017847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2523-1_0_3_line_91 |  | 85 | 88 | 0.018631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
92 | LV_2523-1_0_3_line_92 |  | 87 | 89 | 0.018895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2523-1_0_3_line_93 |  | 88 | 90 | 0.0046393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_2523-1_0_3_line_94 |  | 89 | 92 | 0.026795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2523-1_0_3_line_95 |  | 89 | 91 | 0.01534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2523-1_0_3_line_96 |  | 90 | 99 | 0.016262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2523-1_0_3_line_97 |  | 90 | 96 | 0.026926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_2523-1_0_3_line_98 |  | 92 | 93 | 0.017182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2523-1_0_3_line_99 |  | 93 | 94 | 0.014116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2523-1_0_3_line_100 |  | 95 | 96 | 0.025749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_2523-1_0_3_line_101 |  | 95 | 97 | 0.0054939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_2523-1_0_3_line_102 |  | 97 | 98 | 0.016888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2523-1_0_3_line_103 |  | 98 | 100 | 0.037336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2523-1_0_3_line_104 |  | 102 | 103 | 0.017841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2523-1_0_3_line_105 |  | 102 | 104 | 0.010785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2523-1_0_3_line_106 |  | 103 | 105 | 0.038119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2523-1_0_3_line_107 |  | 103 | 106 | 0.004733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2523-1_0_3_line_108 |  | 105 | 107 | 0.0046804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2523-1_0_3_line_109 |  | 106 | 108 | 0.014332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2523-1_0_3_line_110 |  | 106 | 109 | 0.022607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2523-1_0_3_line_111 |  | 107 | 110 | 0.016852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2523-1_0_3_line_112 |  | 108 | 111 | 0.028018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2523-1_0_3_line_113 |  | 110 | 113 | 0.015907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2523-1_0_3_line_114 |  | 111 | 116 | 0.013478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2523-1_0_3_line_115 |  | 114 | 115 | 0.0041065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2523-1_0_3_trafo_116 | 0.63 MVA 20/0.4 kV | 117 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2613686.0724 | 1226172.3845 | 2613676.9513 | 1226189.597
1 | 2613691.779 | 1226161.6155 | 2613686.0724 | 1226172.3845
2 | 2613676.9513 | 1226189.597 | 2613674.2559 | 1226194.6837 | 2613672.6073 | 1226196.3809 | 2613670.8623 | 1226197.1552 | 2613668.7246 | 1226197.2837 | 2613665.9594 | 1226196.7548
3 | 2613691.779 | 1226161.6155 | 2613664.4456 | 1226138.1206
4 | 2613691.779 | 1226161.6155 | 2613698.5262 | 1226148.9617
5 | 2613650.0462 | 1226125.7434 | 2613664.4456 | 1226138.1206
6 | 2613706.1429 | 1226134.677 | 2613698.5262 | 1226148.9617
7 | 2613650.0462 | 1226125.7434 | 2613644.6753 | 1226136.572
8 | 2613653.2513 | 1226119.5137 | 2613650.0462 | 1226125.7434
9 | 2613637.2587 | 1226220.1032 | 2613637.3838 | 1226219.847
10 | 2613627.5358 | 1226241.9604 | 2613629.9008 | 1226235.184 | 2613637.2587 | 1226220.1032
11 | 2613644.6753 | 1226136.572 | 2613639.4926 | 1226147.0215
12 | 2613653.2513 | 1226119.5137 | 2613668.0817 | 1226090.6973
13 | 2613729.2554 | 1225843.3201 | 2613706.6552 | 1225839.4716
14 | 2613787.6606 | 1225854.533 | 2613781.1662 | 1225850.6824 | 2613777.1235 | 1225848.5718 | 2613773.6852 | 1225847.3187 | 2613769.3669 | 1225846.4083 | 2613765.0398 | 1225846.0203 | 2613746.1976 | 1225845.6211 | 2613738.8166 | 1225844.9482 | 2613729.2554 | 1225843.3201
15 | 2613679.5094 | 1225834.7064 | 2613684.6809 | 1225835.7297 | 2613706.6552 | 1225839.4716
16 | 2613787.6606 | 1225854.533 | 2613785.0113 | 1225859.5632
17 | 2613787.6606 | 1225854.533 | 2613790.1037 | 1225850.2027 | 2613792.2337 | 1225846.8835 | 2613794.9637 | 1225843.0208
18 | 2613663.422 | 1225831.5231 | 2613679.5094 | 1225834.7064
19 | 2613785.0113 | 1225859.5632 | 2613777.0478 | 1225875.2403
20 | 2613785.0113 | 1225859.5632 | 2613792.7042 | 1225863.0274 | 2613792.8916 | 1225902.1404
21 | 2613794.9637 | 1225843.0208 | 2613787.5967 | 1225839.524 | 2613735.9122 | 1225833.4879
22 | 2613663.422 | 1225831.5231 | 2613654.8098 | 1225829.8216
23 | 2613663.422 | 1225831.5231 | 2613668.2035 | 1225828.7435 | 2613681.8545 | 1225828.7636 | 2613694.7126 | 1225827.5034 | 2613699.5437 | 1225828.1215
24 | 2613777.0478 | 1225875.2403 | 2613767.5295 | 1225893.9782
25 | 2613643.2149 | 1225827.5307 | 2613654.8098 | 1225829.8216
26 | 2613711.445 | 1225819.1257 | 2613709.2234 | 1225829.36 | 2613699.5437 | 1225828.1215
27 | 2613761.1789 | 1225906.4803 | 2613767.5295 | 1225893.9782
28 | 2613635.0365 | 1225825.9149 | 2613643.2149 | 1225827.5307
29 | 2613623.4571 | 1225823.6272 | 2613635.0365 | 1225825.9149
30 | 2613624.561 | 1226177.1266 | 2613639.4926 | 1226147.0215
31 | 2613681.7171 | 1226064.1906 | 2613668.0817 | 1226090.6973
32 | 2613668.0817 | 1226090.6973 | 2613682.4974 | 1226101.1984
33 | 2613624.561 | 1226177.1266 | 2613623.0008 | 1226180.2484
34 | 2613624.561 | 1226177.1266 | 2613607.4542 | 1226167.3374 | 2613604.3835 | 1226164.5065 | 2613602.8806 | 1226162.135 | 2613602.3018 | 1226160.0325 | 2613602.5097 | 1226158.5877 | 2613603.2559 | 1226157.0885
35 | 2613681.7171 | 1226064.1906 | 2613672.337 | 1226059.4886
36 | 2613681.7171 | 1226064.1906 | 2613684.9172 | 1226057.9703
37 | 2613706.4964 | 1226116.0446 | 2613701.5191 | 1226115.0548 | 2613682.4974 | 1226101.1984
38 | 2613672.337 | 1226059.4886 | 2613658.9652 | 1226085.6437
39 | 2613614.6639 | 1225871.6612 | 2613617.506 | 1225856.1358
40 | 2613623.4571 | 1225823.6272 | 2613617.506 | 1225856.1358
41 | 2613614.6639 | 1225871.6612 | 2613613.4256 | 1225878.4255 | 2613611.0225 | 1225885.4994
42 | 2613623.4571 | 1225823.6272 | 2613608.5166 | 1225820.4859
43 | 2613599.0833 | 1225818.5025 | 2613608.5166 | 1225820.4859
44 | 2613583.2584 | 1225815.1752 | 2613599.0833 | 1225818.5025
45 | 2613583.2584 | 1225815.1752 | 2613578.8869 | 1225838.0776
46 | 2613550.0163 | 1225807.3841 | 2613562.4158 | 1225811.1477 | 2613583.2584 | 1225815.1752
47 | 2613525.1002 | 1225794.7515 | 2613519.4909 | 1225791.4723 | 2613501.5718 | 1225778.3129 | 2613480.4625 | 1225761.3887 | 2613474.978 | 1225756.5846 | 2613471.004 | 1225752.45
48 | 2613462.0417 | 1225742.0803 | 2613466.7429 | 1225748.0166 | 2613471.004 | 1225752.45
49 | 2613525.1002 | 1225794.7515 | 2613529.001 | 1225797.0318
50 | 2613462.0417 | 1225742.0803 | 2613462.7232 | 1225738.98 | 2613463.1326 | 1225735.6123 | 2613463.1373 | 1225734.7213
51 | 2613462.0417 | 1225742.0803 | 2613457.5189 | 1225741.0028 | 2613454.5019 | 1225741.1183 | 2613452.4392 | 1225741.5473 | 2613450.7701 | 1225742.2328 | 2613448.6674 | 1225743.6066 | 2613426.9584 | 1225765.773
52 | 2613550.0163 | 1225807.3841 | 2613537.1889 | 1225801.8184 | 2613529.001 | 1225797.0318
53 | 2613458.4961 | 1225717.3318 | 2613459.0705 | 1225718.4708 | 2613460.8786 | 1225723.3667 | 2613462.7355 | 1225730.186 | 2613463.1458 | 1225733.1108 | 2613463.1373 | 1225734.7213
54 | 2613411.1757 | 1225781.49 | 2613416.1286 | 1225776.8308 | 2613426.9584 | 1225765.773
55 | 2613550.0163 | 1225807.3841 | 2613550.7047 | 1225804.6507 | 2613550.9677 | 1225802.3388 | 2613550.9933 | 1225801.0604 | 2613550.7764 | 1225799.7813 | 2613550.1667 | 1225797.89 | 2613547.8127 | 1225793.104 | 2613546.0393 | 1225789.6647 | 2613545.3608 | 1225788.0066 | 2613544.8787 | 1225786.7047 | 2613544.6015 | 1225785.281 | 2613544.4684 | 1225783.8132 | 2613544.6239 | 1225782.0681 | 2613545.0669 | 1225780.5793 | 2613545.6761 | 1225779.3467 | 2613546.4063 | 1225778.2366 | 2613547.3253 | 1225777.4048 | 2613548.4792 | 1225776.607 | 2613549.8376 | 1225775.9207 | 2613550.4835 | 1225775.7305
56 | 2613378.361 | 1225819.7714 | 2613379.99 | 1225816.6844 | 2613382.2575 | 1225812.7538 | 2613385.0638 | 1225808.5688 | 2613397.2758 | 1225794.5657 | 2613411.1757 | 1225781.49
57 | 2613553.7957 | 1225775.2738 | 2613551.711 | 1225775.3691 | 2613550.4835 | 1225775.7305
58 | 2613378.361 | 1225819.7714 | 2613377.2311 | 1225823.4044 | 2613376.06 | 1225828.4714 | 2613375.7823 | 1225831.2971
59 | 2613375.7823 | 1225831.2971 | 2613367.4236 | 1225928.144
60 | 2613367.4236 | 1225928.144 | 2613373.4236 | 1225950.7831
61 | 2613367.4236 | 1225928.144 | 2613363.4864 | 1225929.6694 | 2613358.7378 | 1225931.3487 | 2613354.4298 | 1225932.6287 | 2613347.8329 | 1225933.8369 | 2613342.7192 | 1225934.5908
62 | 2613326.9932 | 1225936.8492 | 2613338.9922 | 1225935.1402 | 2613342.7192 | 1225934.5908
63 | 2613619.0402 | 1225789.3601 | 2613640.6666 | 1225795.6089
64 | 2613619.0402 | 1225789.3601 | 2613604.6257 | 1225785.1951 | 2613598.8759 | 1225783.77 | 2613594.8455 | 1225782.9666
65 | 2613640.6666 | 1225795.6089 | 2613660.5365 | 1225745.639
66 | 2613571.6286 | 1225778.3387 | 2613594.8455 | 1225782.9666
67 | 2613660.5365 | 1225745.639 | 2613669.8831 | 1225747.3106 | 2613680.4233 | 1225748.7466 | 2613681.0411 | 1225748.7304
68 | 2613553.7957 | 1225775.2738 | 2613557.8047 | 1225775.5831 | 2613571.6286 | 1225778.3387
69 | 2613692.4422 | 1225746.5729 | 2613687.9819 | 1225748.0635 | 2613683.9178 | 1225748.6546 | 2613681.0411 | 1225748.7304
70 | 2613692.4422 | 1225746.5729 | 2613690.9973 | 1225745.3244 | 2613689.4551 | 1225743.5754 | 2613687.9364 | 1225741.4484 | 2613666.667 | 1225700.6588
71 | 2613553.7957 | 1225775.2738 | 2613559.4297 | 1225780.3263
72 | 2613573.3818 | 1225788.2283 | 2613563.5622 | 1225783.6119 | 2613561.7004 | 1225782.3625 | 2613559.4297 | 1225780.3263
73 | 2613571.041 | 1225858.106 | 2613576.6997 | 1225849.5361 | 2613578.8869 | 1225838.0776
74 | 2613523.7766 | 1226111.5258 | 2613530.3527 | 1226116.1211 | 2613534.5694 | 1226121.6784 | 2613536.8618 | 1226123.4624 | 2613539.7382 | 1226125.1255 | 2613561.7806 | 1226134.3698
75 | 2613523.7766 | 1226111.5258 | 2613525.8246 | 1226107.4947 | 2613527.4707 | 1226103.5628 | 2613539.456 | 1226071.749
76 | 2613561.9142 | 1226134.0239 | 2613561.7806 | 1226134.3698
77 | 2613603.2559 | 1226157.0885 | 2613561.7806 | 1226134.3698
78 | 2613570.5416 | 1226111.6895 | 2613561.9142 | 1226134.0239
79 | 2613570.5416 | 1226111.6895 | 2613594.3902 | 1226049.9505
80 | 2613606.7901 | 1226212.6848 | 2613623.0008 | 1226180.2484
81 | 2613606.7901 | 1226212.6848 | 2613604.9312 | 1226216.8719 | 2613609.3209 | 1226219.5946 | 2613613.2165 | 1226222.9944 | 2613616.717 | 1226226.7824 | 2613621.2139 | 1226232.3403 | 2613627.5358 | 1226241.9604
82 | 2613595.8423 | 1226234.1725 | 2613597.4561 | 1226231.0522 | 2613601.5443 | 1226223.0679 | 2613604.9312 | 1226216.8719 | 2613606.7901 | 1226212.6848
83 | 2613627.5358 | 1226241.9604 | 2613630.7701 | 1226249.8455
84 | 2613595.8423 | 1226234.1725 | 2613587.6731 | 1226250.3477
85 | 2613595.8423 | 1226234.1725 | 2613602.7381 | 1226238.0349 | 2613606.8466 | 1226241.1128 | 2613610.8106 | 1226244.3793 | 2613613.6836 | 1226247.4765 | 2613615.776 | 1226250.5831 | 2613617.0284 | 1226253.0763 | 2613617.3181 | 1226253.7126
86 | 2613712.8479 | 1226045.2305 | 2613722.6458 | 1226050.9878 | 2613730.9045 | 1226055.5317 | 2613738.1849 | 1226058.5367
87 | 2613696.4336 | 1226035.5853 | 2613712.8479 | 1226045.2305
88 | 2613724.2663 | 1225979.0714 | 2613696.4336 | 1226035.5853
89 | 2613696.4336 | 1226035.5853 | 2613684.9172 | 1226057.9703
90 | 2613724.2663 | 1225979.0714 | 2613738.9809 | 1225989.1715
91 | 2613724.2663 | 1225979.0714 | 2613732.7092 | 1225962.4635
92 | 2613754.5591 | 1225999.8644 | 2613738.9809 | 1225989.1715
93 | 2613734.8116 | 1225958.3279 | 2613732.7092 | 1225962.4635
94 | 2613776.7017 | 1226015.0466 | 2613754.5591 | 1225999.8644
95 | 2613754.5591 | 1225999.8644 | 2613747.8719 | 1226013.6706
96 | 2613734.8116 | 1225958.3279 | 2613749.7032 | 1225964.8626
97 | 2613734.8116 | 1225958.3279 | 2613742.0592 | 1225944.4586 | 2613747.1301 | 1225934.386
98 | 2613776.7017 | 1226015.0466 | 2613769.1806 | 1226030.4949
99 | 2613763.0014 | 1226043.1871 | 2613769.1806 | 1226030.4949
100 | 2613758.7085 | 1225911.3874 | 2613747.1301 | 1225934.386
101 | 2613761.1789 | 1225906.4803 | 2613758.7085 | 1225911.3874
102 | 2613761.1789 | 1225906.4803 | 2613776.4707 | 1225913.6471
103 | 2613776.4707 | 1225913.6471 | 2613785.733 | 1225917.9881 | 2613783.5577 | 1225934.3816 | 2613778.049 | 1225943.402
104 | 2613553.6109 | 1226317.7925 | 2613569.6914 | 1226325.5203
105 | 2613579.4121 | 1226330.1917 | 2613569.6914 | 1226325.5203
106 | 2613553.6109 | 1226317.7925 | 2613570.7954 | 1226283.7664
107 | 2613553.6109 | 1226317.7925 | 2613551.4413 | 1226322.0012
108 | 2613572.9054 | 1226279.5886 | 2613570.7954 | 1226283.7664
109 | 2613551.4413 | 1226322.0012 | 2613544.9428 | 1226334.7754
110 | 2613551.4413 | 1226322.0012 | 2613531.6683 | 1226311.0423
111 | 2613572.9054 | 1226279.5886 | 2613580.5022 | 1226264.5465
112 | 2613532.1505 | 1226359.7019 | 2613534.5557 | 1226355.1936 | 2613544.9428 | 1226334.7754
113 | 2613587.6731 | 1226250.3477 | 2613580.5022 | 1226264.5465
114 | 2613532.1505 | 1226359.7019 | 2613526.3503 | 1226357.3763 | 2613519.1492 | 1226358.0101
115 | 2613619.0194 | 1226257.4501 | 2613617.3181 | 1226253.7126

## bus_geodata
| x | y | coords
0 | 2613686.0724 | 1226172.3845
1 | 2613676.9513 | 1226189.597
2 | 2613691.779 | 1226161.6155
3 | 2613665.9594 | 1226196.7548
4 | 2613664.4456 | 1226138.1206
5 | 2613698.5262 | 1226148.9617
6 | 2613650.0462 | 1226125.7434
7 | 2613706.1429 | 1226134.677
8 | 2613637.3838 | 1226219.847
9 | 2613637.2587 | 1226220.1032
10 | 2613644.6753 | 1226136.572
11 | 2613653.2513 | 1226119.5137
12 | 2613729.2554 | 1225843.3201
13 | 2613706.6552 | 1225839.4716
14 | 2613787.6606 | 1225854.533
15 | 2613679.5094 | 1225834.7064
16 | 2613785.0113 | 1225859.5632
17 | 2613794.9637 | 1225843.0208
18 | 2613663.422 | 1225831.5231
19 | 2613777.0478 | 1225875.2403
20 | 2613792.8916 | 1225902.1404
21 | 2613735.9122 | 1225833.4879
22 | 2613654.8098 | 1225829.8216
23 | 2613699.5437 | 1225828.1215
24 | 2613767.5295 | 1225893.9782
25 | 2613643.2149 | 1225827.5308
26 | 2613711.445 | 1225819.1257
27 | 2613635.0365 | 1225825.9149
28 | 2613639.4926 | 1226147.0215
29 | 2613668.0817 | 1226090.6973
30 | 2613624.561 | 1226177.1266
31 | 2613681.7171 | 1226064.1906
32 | 2613682.4974 | 1226101.1984
33 | 2613658.9652 | 1226085.6437
34 | 2613672.337 | 1226059.4886
35 | 2613617.506 | 1225856.1358
36 | 2613614.6639 | 1225871.6612
37 | 2613623.4571 | 1225823.6272
38 | 2613611.0225 | 1225885.4994
39 | 2613608.5166 | 1225820.4859
40 | 2613599.0833 | 1225818.5025
41 | 2613583.2584 | 1225815.1752
42 | 2613471.004 | 1225752.45
43 | 2613525.1002 | 1225794.7515
44 | 2613462.0417 | 1225742.0803
45 | 2613529.001 | 1225797.0318
46 | 2613463.1373 | 1225734.7213
47 | 2613426.9584 | 1225765.773
48 | 2613550.0163 | 1225807.3841
49 | 2613458.4961 | 1225717.3318
50 | 2613411.1757 | 1225781.49
51 | 2613550.4835 | 1225775.7305
52 | 2613378.361 | 1225819.7714
53 | 2613375.7823 | 1225831.2971
54 | 2613367.4236 | 1225928.144
55 | 2613373.4236 | 1225950.7831
56 | 2613342.7192 | 1225934.5908
57 | 2613326.9932 | 1225936.8492
58 | 2613619.0402 | 1225789.3601
59 | 2613640.6666 | 1225795.6089
60 | 2613594.8455 | 1225782.9666
61 | 2613660.5365 | 1225745.639
62 | 2613571.6286 | 1225778.3387
63 | 2613681.0411 | 1225748.7304
64 | 2613692.4422 | 1225746.5729
65 | 2613666.667 | 1225700.6588
66 | 2613553.7957 | 1225775.2738
67 | 2613559.4297 | 1225780.3263
68 | 2613578.8869 | 1225838.0776
69 | 2613571.041 | 1225858.106
70 | 2613573.3818 | 1225788.2283
71 | 2613523.7766 | 1226111.5258
72 | 2613561.7806 | 1226134.3698
73 | 2613539.456 | 1226071.749
74 | 2613561.9142 | 1226134.0239
75 | 2613603.2559 | 1226157.0885
76 | 2613570.5416 | 1226111.6895
77 | 2613623.0008 | 1226180.2484
78 | 2613606.7901 | 1226212.6848
79 | 2613594.3902 | 1226049.9505
80 | 2613627.5358 | 1226241.9604
81 | 2613595.8423 | 1226234.1725
82 | 2613712.8479 | 1226045.2305
83 | 2613738.1849 | 1226058.5367
84 | 2613696.4336 | 1226035.5853
85 | 2613724.2663 | 1225979.0714
86 | 2613684.9172 | 1226057.9703
87 | 2613738.9809 | 1225989.1715
88 | 2613732.7092 | 1225962.4635
89 | 2613754.5591 | 1225999.8644
90 | 2613734.8116 | 1225958.3279
91 | 2613747.8719 | 1226013.6706
92 | 2613776.7017 | 1226015.0466
93 | 2613769.1806 | 1226030.4949
94 | 2613763.0014 | 1226043.1871
95 | 2613758.7085 | 1225911.3874
96 | 2613747.1301 | 1225934.386
97 | 2613761.1789 | 1225906.4803
98 | 2613776.4707 | 1225913.6471
99 | 2613749.7032 | 1225964.8626
100 | 2613778.049 | 1225943.402
101 | 2613706.4964 | 1226116.0446
102 | 2613569.6914 | 1226325.5203
103 | 2613553.6109 | 1226317.7925
104 | 2613579.4121 | 1226330.1917
105 | 2613570.7954 | 1226283.7664
106 | 2613551.4413 | 1226322.0012
107 | 2613572.9054 | 1226279.5886
108 | 2613544.9428 | 1226334.7754
109 | 2613531.6683 | 1226311.0423
110 | 2613580.5022 | 1226264.5465
111 | 2613532.1505 | 1226359.7019
112 | 2613630.7701 | 1226249.8455
113 | 2613587.6731 | 1226250.3477
114 | 2613617.3181 | 1226253.7126
115 | 2613619.0194 | 1226257.4501
116 | 2613519.1492 | 1226358.0101
117 | 2613681.7171 | 1226064.1906

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99508 | -0.094156 | 0.0010985 | 0.00027531
1 | 0.99504 | -0.095042 | 0.0011013 | 0.00027601
2 | 0.99512 | -0.093365 | 0 | 0
3 | 0.99502 | -0.095433 | 0.0014826 | 0.00037157
4 | 0.99534 | -0.089253 | 0.001428 | 0.00035788
5 | 0.99509 | -0.094072 | 0.0020913 | 0.00052412
6 | 0.99547 | -0.086611 | 0 | 0
7 | 0.99508 | -0.094273 | 0.00070628 | 0.00017701
8 | 0.99175 | -0.15845 | 0.0022993 | 0.00057626
9 | 0.99175 | -0.15844 | 0.0014002 | 0.00035093
10 | 0.99494 | -0.096819 | 0.0010298 | 0.00025809
11 | 0.99583 | -0.079727 | 0 | 0
12 | 0.98319 | -0.3211 | 0.0017795 | 0.00044599
13 | 0.98172 | -0.34964 | 0.0023945 | 0.00060011
14 | 0.98717 | -0.24427 | 0 | 0
15 | 0.98001 | -0.38287 | 0.001208 | 0.00030274
16 | 0.98757 | -0.2367 | 0 | 0
17 | 0.98712 | -0.24522 | 0 | 0
18 | 0.97901 | -0.40233 | 0 | 0
19 | 0.98906 | -0.20807 | 0.0017096 | 0.00042846
20 | 0.98684 | -0.25085 | 0.016643 | 0.0041711
21 | 0.98691 | -0.24937 | 0.0038592 | 0.0009672
22 | 0.97851 | -0.41212 | 0.0022173 | 0.0005557
23 | 0.97887 | -0.40507 | 0.0026404 | 0.00066175
24 | 0.98996 | -0.19069 | 0.0020571 | 0.00051555
25 | 0.97786 | -0.42484 | 0.001705 | 0.0004273
26 | 0.97884 | -0.40559 | 0.0014232 | 0.00035669
27 | 0.97741 | -0.43355 | 0.0018223 | 0.00045671
28 | 0.99444 | -0.10647 | 0.0013706 | 0.00034349
29 | 0.99749 | -0.047951 | 0 | 0
30 | 0.99304 | -0.13351 | 0 | 0
31 | 0.99915 | -0.016032 | 0 | 0
32 | 0.9974 | -0.049622 | 0.0048613 | 0.0012184
33 | 0.99811 | -0.036376 | 0.070914 | 0.017773
34 | 1 | 0 | -0.25071 | -0.063413
35 | 0.9766 | -0.44957 | 0.0026236 | 0.00065754
36 | 0.97654 | -0.45075 | 0.0015156 | 0.00037983
37 | 0.9768 | -0.44552 | 0 | 0
38 | 0.9765 | -0.45142 | 0.0025668 | 0.0006433
39 | 0.97611 | -0.45914 | 0.0017662 | 0.00044265
40 | 0.97568 | -0.46745 | 0.0027843 | 0.0006978
41 | 0.97502 | -0.48056 | 0 | 0
42 | 0.97235 | -0.53309 | 0.0013545 | 0.00033947
43 | 0.97322 | -0.51595 | 0.0016352 | 0.00040982
44 | 0.9722 | -0.53617 | 0 | 0
45 | 0.97328 | -0.51469 | 0.0033974 | 0.00085148
46 | 0.97219 | -0.53624 | 0.00028783 | 7.2137e-05
47 | 0.97171 | -0.54585 | 0.0018354 | 0.00046001
48 | 0.97369 | -0.50668 | 0 | 0
49 | 0.97219 | -0.53632 | 0.00024778 | 6.2099e-05
50 | 0.9715 | -0.54988 | 0.0011074 | 0.00027754
51 | 0.97292 | -0.52196 | 0.002007 | 0.000503
52 | 0.97109 | -0.55802 | 0 | 0
53 | 0.97099 | -0.55992 | 0.00079929 | 0.00020032
54 | 0.97028 | -0.5741 | 0 | 0
55 | 0.9702 | -0.57573 | 0.0037522 | 0.00094038
56 | 0.97018 | -0.57606 | 0.003308 | 0.00082906
57 | 0.97017 | -0.5763 | 0.00082077 | 0.0002057
58 | 0.97179 | -0.54421 | 0.002891 | 0.00072457
59 | 0.97153 | -0.54934 | 0.0030446 | 0.00076305
60 | 0.97215 | -0.53716 | 0.002023 | 0.000507
61 | 0.97106 | -0.55859 | 0.0039727 | 0.00099566
62 | 0.97253 | -0.52962 | 0.0017633 | 0.00044192
63 | 0.97096 | -0.56064 | 0.0028312 | 0.00070958
64 | 0.97093 | -0.56118 | 0 | 0
65 | 0.97081 | -0.56363 | 0.0025032 | 0.00062737
66 | 0.97285 | -0.52327 | 0 | 0
67 | 0.97283 | -0.52357 | 0.00096283 | 0.00024131
68 | 0.97496 | -0.48165 | 0.0014282 | 0.00035795
69 | 0.97494 | -0.4821 | 0.0011158 | 0.00027964
70 | 0.97282 | -0.52391 | 0.0011558 | 0.00028967
71 | 0.99185 | -0.1566 | 0 | 0
72 | 0.99192 | -0.1553 | 0 | 0
73 | 0.99179 | -0.15783 | 0.0016243 | 0.00040708
74 | 0.99191 | -0.15538 | 0.0032446 | 0.00081318
75 | 0.99256 | -0.14287 | 0.0017276 | 0.00043297
76 | 0.99169 | -0.15961 | 0.0034127 | 0.0008553
77 | 0.99295 | -0.1353 | 0.0011148 | 0.00027939
78 | 0.99202 | -0.15321 | 0 | 0
79 | 0.9913 | -0.1673 | 0.006552 | 0.0016421
80 | 0.99183 | -0.15687 | 0 | 0
81 | 0.99152 | -0.16285 | 0 | 0
82 | 0.99739 | -0.049318 | 0.0024305 | 0.00060913
83 | 0.99734 | -0.05041 | 0.0021732 | 0.00054465
84 | 0.99747 | -0.047782 | 0 | 0
85 | 0.99432 | -0.10746 | 0 | 0
86 | 0.99878 | -0.023016 | 0.0018637 | 0.00046708
87 | 0.99427 | -0.10843 | 0.00096872 | 0.00024278
88 | 0.99342 | -0.12468 | 0.0058907 | 0.0014763
89 | 0.99424 | -0.10913 | 0 | 0
90 | 0.99321 | -0.12873 | 0 | 0
91 | 0.99422 | -0.10938 | 0.00091358 | 0.00022896
92 | 0.99421 | -0.1097 | 0 | 0
93 | 0.99419 | -0.11006 | 0.00047395 | 0.00011878
94 | 0.99418 | -0.11024 | 0.00072396 | 0.00018144
95 | 0.99083 | -0.17416 | 0.00049255 | 0.00012344
96 | 0.99198 | -0.1521 | 0.001519 | 0.0003807
97 | 0.99058 | -0.17885 | 0 | 0
98 | 0.99056 | -0.17918 | 0.00045183 | 0.00011324
99 | 0.99319 | -0.12895 | 0.00075317 | 0.00018876
100 | 0.99054 | -0.17961 | 0.00065515 | 0.0001642
101 | 0.99739 | -0.049867 | 0.00048824 | 0.00012237
102 | 0.99031 | -0.1864 | 0.0013897 | 0.0003483
103 | 0.99043 | -0.184 | 0 | 0
104 | 0.99025 | -0.18758 | 0.006164 | 0.0015448
105 | 0.99079 | -0.17706 | 0.0012354 | 0.00030962
106 | 0.99042 | -0.18423 | 0 | 0
107 | 0.99084 | -0.17611 | 0.001665 | 0.0004173
108 | 0.9904 | -0.1847 | 0.00084007 | 0.00021054
109 | 0.99041 | -0.18457 | 0.0008468 | 0.00021223
110 | 0.99104 | -0.17218 | 0.0010793 | 0.0002705
111 | 0.99037 | -0.1852 | 0 | 0
112 | 0.99182 | -0.15712 | 0.0016403 | 0.00041111
113 | 0.99125 | -0.16816 | 0.0022925 | 0.00057456
114 | 0.99136 | -0.16603 | 0.0014738 | 0.00036937
115 | 0.99134 | -0.16636 | 0.0045648 | 0.001144
116 | 0.99036 | -0.18544 | 0.0010033 | 0.00025146
117 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.002584 | 0.00064723 | -0.0025839 | -0.00064741 | 1.0907e-07 | -1.8324e-07 | 0.0038639 | 0.003864 | 0.003864 | 0.99508 | -0.094156 | 0.99504 | -0.095042 | 1.0615
1 | -0.0036825 | -0.00092254 | 0.0036827 | 0.00092247 | 1.3858e-07 | -6.9637e-08 | 0.0055066 | 0.0055066 | 0.0055066 | 0.99508 | -0.094156 | 0.99512 | -0.093365 | 1.5128
2 | 0.0014826 | 0.0003714 | -0.0014826 | -0.00037157 | 2.763e-08 | -1.7701e-07 | 0.0022171 | 0.0022172 | 0.0022172 | 0.99504 | -0.095042 | 0.99502 | -0.095433 | 0.60912
3 | -0.0064803 | -0.0016233 | 0.0064816 | 0.0016236 | 1.2691e-06 | 3.4383e-07 | 0.0096898 | 0.0096896 | 0.0096898 | 0.99512 | -0.093365 | 0.99534 | -0.089253 | 2.662
4 | 0.0027977 | 0.0007008 | -0.0027976 | -0.00070093 | 9.4107e-08 | -1.2607e-07 | 0.0041832 | 0.0041833 | 0.0041833 | 0.99512 | -0.093365 | 0.99509 | -0.094072 | 1.1493
5 | -0.0079096 | -0.0019815 | 0.0079106 | 0.0019819 | 9.9556e-07 | 3.9033e-07 | 0.011824 | 0.011824 | 0.011824 | 0.99534 | -0.089253 | 0.99547 | -0.086611 | 3.2485
6 | 0.00070629 | 0.00017681 | -0.00070628 | -0.00017701 | 6.7712e-09 | -2.0596e-07 | 0.0010561 | 0.0010562 | 0.0010562 | 0.99509 | -0.094072 | 0.99508 | -0.094273 | 0.29015
7 | 0.04815 | 0.012128 | -0.048126 | -0.012113 | 2.3494e-05 | 1.4879e-05 | 0.071995 | 0.071995 | 0.071995 | 0.99547 | -0.086611 | 0.99494 | -0.096819 | 19.7787
8 | -0.05606 | -0.01411 | 0.056079 | 0.014122 | 1.845e-05 | 1.1717e-05 | 0.083819 | 0.083819 | 0.083819 | 0.99547 | -0.086611 | 0.99583 | -0.079727 | 23.0272
9 | -0.0022993 | -0.00057626 | 0.0022993 | 0.00057626 | 1.2721e-09 | -2.8645e-09 | 0.0034499 | 0.0034499 | 0.0034499 | 0.99175 | -0.15845 | 0.99175 | -0.15844 | 0.94777
10 | -0.0036995 | -0.00092719 | 0.0036998 | 0.00092706 | 2.768e-07 | -1.3201e-07 | 0.0055508 | 0.0055507 | 0.0055508 | 0.99175 | -0.15844 | 0.99183 | -0.15687 | 1.5249
11 | 0.047096 | 0.011855 | -0.047075 | -0.011841 | 2.1712e-05 | 1.3744e-05 | 0.070454 | 0.070454 | 0.070454 | 0.99494 | -0.096819 | 0.99444 | -0.10647 | 19.3556
12 | -0.056079 | -0.014122 | 0.056164 | 0.014176 | 8.5342e-05 | 5.4197e-05 | 0.083819 | 0.083819 | 0.083819 | 0.99583 | -0.079727 | 0.99749 | -0.047951 | 23.0271
13 | 0.069511 | 0.017641 | -0.069415 | -0.01758 | 9.529e-05 | 6.0695e-05 | 0.10528 | 0.10528 | 0.10528 | 0.98319 | -0.3211 | 0.98172 | -0.34964 | 28.9232
14 | -0.07129 | -0.018087 | 0.071554 | 0.018255 | 0.00026443 | 0.00016846 | 0.10797 | 0.10797 | 0.10797 | 0.98319 | -0.3211 | 0.98717 | -0.24427 | 29.6631
15 | 0.067021 | 0.01698 | -0.066914 | -0.016912 | 0.0001068 | 6.8005e-05 | 0.10165 | 0.10165 | 0.10165 | 0.98172 | -0.34964 | 0.98001 | -0.38287 | 27.9262
16 | -0.075415 | -0.019222 | 0.075442 | 0.01924 | 2.759e-05 | 1.7585e-05 | 0.11379 | 0.11379 | 0.11379 | 0.98717 | -0.24427 | 0.98757 | -0.2367 | 31.2614
17 | 0.0038601 | 0.00096686 | -0.00386 | -0.00096692 | 1.7311e-07 | -6.3534e-08 | 0.0058184 | 0.0058184 | 0.0058184 | 0.98717 | -0.24427 | 0.98712 | -0.24522 | 1.5985
18 | 0.065706 | 0.016609 | -0.065645 | -0.01657 | 6.1273e-05 | 3.9008e-05 | 0.099817 | 0.099817 | 0.099817 | 0.98001 | -0.38287 | 0.97901 | -0.40233 | 27.4223
19 | -0.092096 | -0.023417 | 0.092224 | 0.023499 | 0.00012719 | 8.1178e-05 | 0.13889 | 0.13889 | 0.13889 | 0.98757 | -0.2367 | 0.98906 | -0.20807 | 38.1556
20 | 0.016654 | 0.0041777 | -0.016643 | -0.0041711 | 1.123e-05 | 6.579e-06 | 0.025095 | 0.025095 | 0.025095 | 0.98757 | -0.2367 | 0.98684 | -0.25085 | 6.8943
21 | 0.00386 | 0.00096692 | -0.0038592 | -0.0009672 | 7.6417e-07 | -2.8021e-07 | 0.0058184 | 0.0058187 | 0.0058187 | 0.98712 | -0.24522 | 0.98691 | -0.24937 | 1.5985
22 | 0.061581 | 0.015552 | -0.061552 | -0.015534 | 2.8866e-05 | 1.8364e-05 | 0.09364 | 0.09364 | 0.09364 | 0.97901 | -0.40233 | 0.97851 | -0.41212 | 25.7253
23 | 0.0040642 | 0.0010181 | -0.0040637 | -0.0010182 | 5.2903e-07 | -1.2625e-07 | 0.0061771 | 0.0061772 | 0.0061772 | 0.97901 | -0.40233 | 0.97887 | -0.40507 | 1.697
24 | -0.093933 | -0.023927 | 0.094012 | 0.023977 | 7.8854e-05 | 4.9927e-05 | 0.14146 | 0.14146 | 0.14146 | 0.98906 | -0.20807 | 0.98996 | -0.19069 | 19.4311
25 | 0.059334 | 0.014978 | -0.059298 | -0.014955 | 3.6115e-05 | 2.2965e-05 | 0.090268 | 0.090268 | 0.090268 | 0.97851 | -0.41212 | 0.97786 | -0.42484 | 24.799
26 | 0.0014232 | 0.00035645 | -0.0014232 | -0.00035669 | 3.551e-08 | -2.3159e-07 | 0.0021634 | 0.0021635 | 0.0021635 | 0.97887 | -0.40507 | 0.97884 | -0.40559 | 0.59437
27 | -0.096069 | -0.024493 | 0.096124 | 0.024527 | 5.4937e-05 | 3.4799e-05 | 0.14455 | 0.14455 | 0.14455 | 0.98996 | -0.19069 | 0.99058 | -0.17885 | 19.8558
28 | 0.057593 | 0.014528 | -0.057569 | -0.014513 | 2.403e-05 | 1.5275e-05 | 0.087674 | 0.087674 | 0.087674 | 0.97786 | -0.42484 | 0.97741 | -0.43355 | 24.0863
29 | 0.055747 | 0.014056 | -0.055715 | -0.014036 | 3.1904e-05 | 2.0271e-05 | 0.0849 | 0.0849 | 0.0849 | 0.97741 | -0.43355 | 0.9768 | -0.44552 | 23.3241
30 | 0.045704 | 0.011498 | -0.045645 | -0.011461 | 5.8964e-05 | 3.7302e-05 | 0.068404 | 0.068404 | 0.068404 | 0.99444 | -0.10647 | 0.99304 | -0.13351 | 18.7923
31 | -0.061514 | -0.015516 | 0.061608 | 0.015576 | 9.4154e-05 | 5.9869e-05 | 0.091799 | 0.091799 | 0.091799 | 0.99749 | -0.047951 | 0.99915 | -0.016032 | 25.2196
32 | 0.00535 | 0.0013404 | -0.0053496 | -0.0013404 | 4.2599e-07 | 3.9846e-08 | 0.0079808 | 0.0079809 | 0.0079809 | 0.99749 | -0.047951 | 0.9974 | -0.049622 | 2.1925
33 | 0.029063 | 0.0072999 | -0.029061 | -0.0072983 | 2.4827e-06 | 1.5438e-06 | 0.043555 | 0.043555 | 0.043555 | 0.99304 | -0.13351 | 0.99295 | -0.1353 | 11.9656
34 | 0.016582 | 0.0041606 | -0.016575 | -0.0041563 | 7.3999e-06 | 4.3227e-06 | 0.024849 | 0.024849 | 0.024849 | 0.99304 | -0.13351 | 0.99256 | -0.14287 | 6.8267
35 | -0.17788 | -0.045474 | 0.17802 | 0.045562 | 0.00013808 | 8.8095e-05 | 0.26523 | 0.26523 | 0.26523 | 0.99915 | -0.016032 | 1 | 0 | 36.4332
36 | 0.11628 | 0.029898 | -0.11624 | -0.029873 | 3.9453e-05 | 2.5067e-05 | 0.17344 | 0.17344 | 0.17344 | 0.99915 | -0.016032 | 0.99878 | -0.023016 | 23.8235
37 | 0.00048825 | 0.000122 | -0.00048824 | -0.00012237 | 5.6913e-09 | -3.6972e-07 | 0.00072829 | 0.00072842 | 0.00072842 | 0.9974 | -0.049622 | 0.99739 | -0.049867 | 0.20012
38 | -0.070914 | -0.017773 | 0.071037 | 0.017851 | 0.00012312 | 7.8413e-05 | 0.10572 | 0.10572 | 0.10572 | 0.99811 | -0.036376 | 1 | 0 | 29.0444
39 | 0.0040827 | 0.001023 | -0.0040824 | -0.001023 | 2.2903e-07 | -5.0895e-08 | 0.0062206 | 0.0062207 | 0.0062207 | 0.9766 | -0.44957 | 0.97654 | -0.45075 | 1.709
40 | -0.0067063 | -0.0016805 | 0.0067076 | 0.0016809 | 1.294e-06 | 4.1453e-07 | 0.010218 | 0.010218 | 0.010218 | 0.9766 | -0.44957 | 0.9768 | -0.44552 | 2.8072
41 | 0.0025669 | 0.00064318 | -0.0025668 | -0.0006433 | 8.2312e-08 | -1.2682e-07 | 0.0039113 | 0.0039114 | 0.0039114 | 0.97654 | -0.45075 | 0.9765 | -0.45142 | 1.0745
42 | 0.049008 | 0.012355 | -0.048976 | -0.012335 | 3.1932e-05 | 2.0245e-05 | 0.074682 | 0.074682 | 0.074682 | 0.9768 | -0.44552 | 0.97611 | -0.45914 | 20.517
43 | 0.047209 | 0.011892 | -0.047191 | -0.01188 | 1.8734e-05 | 1.1869e-05 | 0.071989 | 0.071989 | 0.071989 | 0.97611 | -0.45914 | 0.97568 | -0.46745 | 19.7773
44 | 0.044406 | 0.011182 | -0.044379 | -0.011165 | 2.7829e-05 | 1.7609e-05 | 0.067743 | 0.067743 | 0.067743 | 0.97568 | -0.46745 | 0.97502 | -0.48056 | 18.6108
45 | 0.0025442 | 0.00063713 | -0.002544 | -0.00063733 | 1.3181e-07 | -2.0642e-07 | 0.0038826 | 0.0038827 | 0.0038827 | 0.97502 | -0.48056 | 0.97496 | -0.48165 | 1.0667
46 | 0.041834 | 0.010527 | -0.041782 | -0.010495 | 5.2136e-05 | 3.2943e-05 | 0.063861 | 0.063861 | 0.063861 | 0.97502 | -0.48056 | 0.97369 | -0.50668 | 17.5442
47 | -0.013532 | -0.0033949 | 0.013543 | 0.0034011 | 1.1068e-05 | 6.229e-06 | 0.02071 | 0.02071 | 0.02071 | 0.97235 | -0.53309 | 0.97322 | -0.51595 | 5.6896
48 | 0.012178 | 0.0030554 | -0.012176 | -0.0030545 | 1.7873e-06 | 9.7372e-07 | 0.018637 | 0.018637 | 0.018637 | 0.97235 | -0.53309 | 0.9722 | -0.53617 | 5.1202
49 | -0.015179 | -0.003811 | 0.01518 | 0.0038115 | 9.1278e-07 | 5.2803e-07 | 0.02321 | 0.02321 | 0.02321 | 0.97322 | -0.51595 | 0.97328 | -0.51469 | 6.3764
50 | 0.00053561 | 0.00013392 | -0.00053561 | -0.00013401 | 1.8791e-09 | -9.1273e-08 | 0.00081968 | 0.00081971 | 0.00081971 | 0.9722 | -0.53617 | 0.97219 | -0.53624 | 0.2252
51 | 0.01164 | 0.0029206 | -0.011635 | -0.0029177 | 5.3714e-06 | 2.8785e-06 | 0.017818 | 0.017818 | 0.017818 | 0.9722 | -0.53617 | 0.97171 | -0.54585 | 4.895
52 | -0.018577 | -0.004663 | 0.018584 | 0.0046672 | 7.1e-06 | 4.2522e-06 | 0.028404 | 0.028404 | 0.028404 | 0.97328 | -0.51469 | 0.97369 | -0.50668 | 7.8034
53 | 0.00024778 | 6.1875e-05 | -0.00024778 | -6.2099e-05 | 9.7743e-10 | -2.2414e-07 | 0.00037916 | 0.00037924 | 0.00037924 | 0.97219 | -0.53624 | 0.97219 | -0.53632 | 0.10419
54 | 0.0097997 | 0.0024577 | -0.0097978 | -0.0024567 | 1.8815e-06 | 9.2827e-07 | 0.015007 | 0.015007 | 0.015007 | 0.97171 | -0.54585 | 0.9715 | -0.54988 | 4.1229
55 | 0.023198 | 0.0058273 | -0.023181 | -0.0058169 | 1.6907e-05 | 1.0375e-05 | 0.035457 | 0.035457 | 0.035457 | 0.97369 | -0.50668 | 0.97292 | -0.52196 | 9.7409
56 | 0.0086904 | 0.0021792 | -0.008687 | -0.0021777 | 3.3709e-06 | 1.5295e-06 | 0.013311 | 0.013311 | 0.013311 | 0.9715 | -0.54988 | 0.97109 | -0.55802 | 3.657
57 | 0.021174 | 0.0053139 | -0.021173 | -0.0053131 | 1.3242e-06 | 8.0567e-07 | 0.032387 | 0.032387 | 0.032387 | 0.97292 | -0.52196 | 0.97285 | -0.52327 | 8.8976
58 | 0.008687 | 0.0021777 | -0.0086862 | -0.0021773 | 7.8704e-07 | 3.5719e-07 | 0.013311 | 0.013311 | 0.013311 | 0.97109 | -0.55802 | 0.97099 | -0.55992 | 3.657
59 | 0.0078869 | 0.001977 | -0.0078816 | -0.0019748 | 5.3254e-06 | 2.2068e-06 | 0.012087 | 0.012087 | 0.012087 | 0.97099 | -0.55992 | 0.97028 | -0.5741 | 3.3206
60 | 0.0037525 | 0.00094028 | -0.0037522 | -0.00094038 | 2.9086e-07 | -1.0309e-07 | 0.0057547 | 0.0057548 | 0.0057548 | 0.97028 | -0.5741 | 0.9702 | -0.57573 | 1.581
61 | 0.0041292 | 0.0010345 | -0.0041288 | -0.0010346 | 3.8539e-07 | -6.9865e-08 | 0.0063323 | 0.0063324 | 0.0063324 | 0.97028 | -0.5741 | 0.97018 | -0.57606 | 1.7397
62 | 0.00082077 | 0.00020551 | -0.00082077 | -0.0002057 | 9.441e-09 | -1.9014e-07 | 0.0012588 | 0.0012589 | 0.0012589 | 0.97018 | -0.57606 | 0.97017 | -0.5763 | 0.34584
63 | 0.01236 | 0.0030988 | -0.012357 | -0.0030971 | 3.0237e-06 | 1.6564e-06 | 0.018926 | 0.018926 | 0.018926 | 0.97179 | -0.54421 | 0.97153 | -0.54934 | 5.1995
64 | -0.015251 | -0.0038233 | 0.015256 | 0.0038263 | 5.1203e-06 | 2.9667e-06 | 0.023353 | 0.023353 | 0.023353 | 0.97179 | -0.54421 | 0.97215 | -0.53716 | 6.4156
65 | 0.0093122 | 0.0023341 | -0.0093081 | -0.0023321 | 4.1024e-06 | 1.9599e-06 | 0.014263 | 0.014263 | 0.014263 | 0.97153 | -0.54934 | 0.97106 | -0.55859 | 3.9184
66 | -0.017279 | -0.0043333 | 0.017285 | 0.004337 | 6.2104e-06 | 3.681e-06 | 0.026449 | 0.026449 | 0.026449 | 0.97215 | -0.53716 | 0.97253 | -0.52962 | 7.2662
67 | 0.0053353 | 0.0013364 | -0.0053348 | -0.0013364 | 5.2009e-07 | 7.6184e-08 | 0.0081754 | 0.0081755 | 0.0081755 | 0.97106 | -0.55859 | 0.97096 | -0.56064 | 2.246
68 | -0.019048 | -0.0047789 | 0.019054 | 0.0047824 | 5.7716e-06 | 3.4689e-06 | 0.029147 | 0.029147 | 0.029147 | 0.97253 | -0.52962 | 0.97285 | -0.52327 | 8.0074
69 | 0.0025036 | 0.0006268 | -0.0025035 | -0.0006269 | 6.4511e-08 | -1.0326e-07 | 0.0038365 | 0.0038366 | 0.0038366 | 0.97096 | -0.56064 | 0.97093 | -0.56118 | 1.054
70 | 0.0025035 | 0.0006269 | -0.0025032 | -0.00062737 | 2.9178e-07 | -4.669e-07 | 0.0038366 | 0.0038368 | 0.0038368 | 0.97093 | -0.56118 | 0.97081 | -0.56363 | 1.0541
71 | 0.0021187 | 0.00053071 | -0.0021186 | -0.00053079 | 2.9801e-08 | -7.4891e-08 | 0.0032405 | 0.0032405 | 0.0032405 | 0.97285 | -0.52327 | 0.97283 | -0.52357 | 0.89026
72 | 0.0011558 | 0.00028948 | -0.0011558 | -0.00028967 | 1.8919e-08 | -1.8832e-07 | 0.0017678 | 0.0017679 | 0.0017679 | 0.97283 | -0.52357 | 0.97282 | -0.52391 | 0.48568
73 | 0.0011158 | 0.00027938 | -0.0011158 | -0.00027964 | 2.3854e-08 | -2.5827e-07 | 0.0017029 | 0.001703 | 0.001703 | 0.97496 | -0.48165 | 0.97494 | -0.4821 | 0.46785
74 | -0.0016244 | -0.00040659 | 0.0016245 | 0.00040607 | 1.0027e-07 | -5.1709e-07 | 0.0024368 | 0.0024365 | 0.0024368 | 0.99185 | -0.1566 | 0.99192 | -0.1553 | 0.66944
75 | 0.0016244 | 0.00040659 | -0.0016243 | -0.00040708 | 9.5265e-08 | -4.9113e-07 | 0.0024368 | 0.0024369 | 0.0024369 | 0.99185 | -0.1566 | 0.99179 | -0.15783 | 0.66949
76 | 0.013214 | 0.0033123 | -0.013214 | -0.0033122 | 5.4628e-08 | 3.0177e-08 | 0.019823 | 0.019823 | 0.019823 | 0.99192 | -0.1553 | 0.99191 | -0.15538 | 5.4458
77 | -0.014838 | -0.0037183 | 0.014847 | 0.0037233 | 8.7866e-06 | 5.0126e-06 | 0.022259 | 0.022259 | 0.022259 | 0.99192 | -0.1553 | 0.99256 | -0.14287 | 6.1152
78 | 0.0099691 | 0.0024991 | -0.0099671 | -0.0024981 | 2.0082e-06 | 9.7626e-07 | 0.014955 | 0.014956 | 0.014956 | 0.99191 | -0.15538 | 0.99169 | -0.15961 | 4.1087
79 | 0.0065544 | 0.0016428 | -0.006552 | -0.0016421 | 2.4007e-06 | 6.8285e-07 | 0.0098348 | 0.0098351 | 0.0098351 | 0.99169 | -0.15961 | 0.9913 | -0.1673 | 2.702
80 | 0.027946 | 0.007019 | -0.027922 | -0.0070042 | 2.3855e-05 | 1.4799e-05 | 0.041884 | 0.041885 | 0.041885 | 0.99295 | -0.1353 | 0.99202 | -0.15321 | 11.5067
81 | 0.0053411 | 0.0013382 | -0.0053402 | -0.0013381 | 9.3233e-07 | 9.6678e-08 | 0.0080114 | 0.0080116 | 0.0080116 | 0.99202 | -0.15321 | 0.99183 | -0.15687 | 2.201
82 | 0.022581 | 0.005666 | -0.02257 | -0.0056597 | 1.0381e-05 | 6.3322e-06 | 0.033873 | 0.033873 | 0.033873 | 0.99202 | -0.15321 | 0.99152 | -0.16285 | 9.3058
83 | 0.0016404 | 0.00041101 | -0.0016403 | -0.00041111 | 1.9356e-08 | -9.7604e-08 | 0.0024609 | 0.002461 | 0.002461 | 0.99183 | -0.15687 | 0.99182 | -0.15712 | 0.67609
84 | 0.016531 | 0.0041461 | -0.016527 | -0.0041436 | 4.1826e-06 | 2.4432e-06 | 0.024809 | 0.02481 | 0.02481 | 0.99152 | -0.16285 | 0.99125 | -0.16816 | 6.8158
85 | 0.0060396 | 0.0015136 | -0.0060386 | -0.0015134 | 9.1292e-07 | 2.0213e-07 | 0.0090638 | 0.0090639 | 0.0090639 | 0.99152 | -0.16285 | 0.99136 | -0.16603 | 2.4901
86 | 0.0021733 | 0.00054435 | -0.0021732 | -0.00054465 | 1.1301e-07 | -3.0178e-07 | 0.0032422 | 0.0032424 | 0.0032424 | 0.99739 | -0.049318 | 0.99734 | -0.05041 | 0.89076
87 | -0.0046038 | -0.0011535 | 0.0046041 | 0.0011535 | 3.3678e-07 | -3.2946e-08 | 0.0068683 | 0.0068682 | 0.0068683 | 0.99739 | -0.049318 | 0.99747 | -0.047782 | 1.8869
88 | 0.10963 | 0.028165 | -0.10931 | -0.027964 | 0.00031674 | 0.00020108 | 0.16379 | 0.16379 | 0.16379 | 0.99747 | -0.047782 | 0.99432 | -0.10746 | 22.4988
89 | -0.11423 | -0.029318 | 0.11437 | 0.029406 | 0.00013747 | 8.7322e-05 | 0.17066 | 0.17066 | 0.17066 | 0.99747 | -0.047782 | 0.99878 | -0.023016 | 23.4422
90 | 0.0030805 | 0.00077073 | -0.0030804 | -0.00077087 | 1.4221e-07 | -1.4047e-07 | 0.0046095 | 0.0046096 | 0.0046096 | 0.99432 | -0.10746 | 0.99427 | -0.10843 | 1.2664
91 | 0.10623 | 0.027193 | -0.10614 | -0.027137 | 8.8516e-05 | 5.6167e-05 | 0.15918 | 0.15918 | 0.15918 | 0.99432 | -0.10746 | 0.99342 | -0.12468 | 21.8657
92 | 0.0021116 | 0.00052808 | -0.0021116 | -0.00052828 | 7.0749e-08 | -1.9977e-07 | 0.0031598 | 0.0031599 | 0.0031599 | 0.99427 | -0.10843 | 0.99424 | -0.10913 | 0.86811
93 | 0.10025 | 0.025661 | -0.10023 | -0.025648 | 1.9666e-05 | 1.2466e-05 | 0.15036 | 0.15036 | 0.15036 | 0.99342 | -0.12468 | 0.99321 | -0.12873 | 20.6537
94 | 0.001198 | 0.00029951 | -0.0011979 | -0.00029984 | 3.2294e-08 | -3.2681e-07 | 0.0017927 | 0.0017928 | 0.0017928 | 0.99424 | -0.10913 | 0.99421 | -0.1097 | 0.49253
95 | 0.00091359 | 0.00022877 | -0.00091358 | -0.00022896 | 1.0754e-08 | -1.9206e-07 | 0.0013672 | 0.0013673 | 0.0013673 | 0.99424 | -0.10913 | 0.99422 | -0.10938 | 0.37564
96 | 0.00075318 | 0.00018856 | -0.00075317 | -0.00018876 | 7.7645e-09 | -2.0549e-07 | 0.0011283 | 0.0011284 | 0.0011284 | 0.99321 | -0.12873 | 0.99319 | -0.12895 | 0.31
97 | 0.099481 | 0.02546 | -0.099369 | -0.025388 | 0.00011243 | 7.126e-05 | 0.14923 | 0.14923 | 0.14923 | 0.99321 | -0.12873 | 0.99198 | -0.1521 | 20.4987
98 | 0.0011979 | 0.00029984 | -0.0011979 | -0.00030005 | 2.071e-08 | -2.0955e-07 | 0.0017928 | 0.0017929 | 0.0017929 | 0.99421 | -0.1097 | 0.99419 | -0.11006 | 0.49255
99 | 0.00072397 | 0.00018126 | -0.00072396 | -0.00018144 | 6.2151e-09 | -1.7907e-07 | 0.0010835 | 0.0010836 | 0.0010836 | 0.99419 | -0.11006 | 0.99418 | -0.11024 | 0.29769
100 | -0.097746 | -0.024942 | 0.09785 | 0.025008 | 0.00010426 | 6.6061e-05 | 0.14695 | 0.14695 | 0.14695 | 0.99083 | -0.17416 | 0.99198 | -0.1521 | 20.1858
101 | 0.097253 | 0.024818 | -0.097231 | -0.024804 | 2.2022e-05 | 1.3952e-05 | 0.14621 | 0.14621 | 0.14621 | 0.99083 | -0.17416 | 0.99058 | -0.17885 | 20.0842
102 | 0.001107 | 0.00027676 | -0.001107 | -0.00027697 | 1.7508e-08 | -2.0619e-07 | 0.0016627 | 0.0016628 | 0.0016628 | 0.99058 | -0.17885 | 0.99056 | -0.17918 | 0.4568
103 | 0.00065517 | 0.00016372 | -0.00065515 | -0.0001642 | 1.3559e-08 | -4.7193e-07 | 0.00098402 | 0.00098419 | 0.00098419 | 0.99056 | -0.17918 | 0.99054 | -0.17961 | 0.27038
104 | -0.0075541 | -0.0018932 | 0.007555 | 0.0018936 | 8.6196e-07 | 3.2207e-07 | 0.011351 | 0.01135 | 0.011351 | 0.99031 | -0.1864 | 0.99043 | -0.184 | 3.1183
105 | 0.0061643 | 0.0015449 | -0.006164 | -0.0015448 | 3.4697e-07 | 8.331e-08 | 0.0092624 | 0.0092624 | 0.0092624 | 0.99031 | -0.1864 | 0.99025 | -0.18758 | 2.5446
106 | -0.010245 | -0.0025668 | 0.010249 | 0.0025685 | 3.3866e-06 | 1.6767e-06 | 0.015392 | 0.015392 | 0.015392 | 0.99043 | -0.184 | 0.99079 | -0.17706 | 4.2286
107 | 0.0026903 | 0.00067323 | -0.0026903 | -0.00067328 | 2.8991e-08 | -4.2356e-08 | 0.0040415 | 0.0040416 | 0.0040416 | 0.99043 | -0.184 | 0.99042 | -0.18423 | 1.1103
108 | -0.011484 | -0.0028781 | 0.011485 | 0.0028784 | 5.221e-07 | 2.7386e-07 | 0.017247 | 0.017247 | 0.017247 | 0.99079 | -0.17706 | 0.99084 | -0.17611 | 4.7383
109 | 0.0018435 | 0.00046133 | -0.0018434 | -0.00046149 | 4.1222e-08 | -1.5806e-07 | 0.0027694 | 0.0027695 | 0.0027695 | 0.99042 | -0.18423 | 0.9904 | -0.1847 | 0.76084
110 | 0.00084681 | 0.00021195 | -0.0008468 | -0.00021223 | 1.3721e-08 | -2.8215e-07 | 0.0012722 | 0.0012723 | 0.0012723 | 0.99042 | -0.18423 | 0.99041 | -0.18457 | 0.34952
111 | -0.01315 | -0.0032957 | 0.013152 | 0.003297 | 2.4644e-06 | 1.3601e-06 | 0.019748 | 0.019748 | 0.019748 | 0.99084 | -0.17611 | 0.99104 | -0.17218 | 5.4252
112 | 0.0010034 | 0.00025095 | -0.0010033 | -0.00025129 | 2.3873e-08 | -3.4527e-07 | 0.0015073 | 0.0015074 | 0.0015074 | 0.9904 | -0.1847 | 0.99037 | -0.1852 | 0.41413
113 | -0.014231 | -0.0035675 | 0.014234 | 0.0035691 | 2.7236e-06 | 1.5381e-06 | 0.021368 | 0.021368 | 0.021368 | 0.99104 | -0.17218 | 0.99125 | -0.16816 | 5.8704
114 | 0.0010033 | 0.00025129 | -0.0010033 | -0.00025146 | 1.1486e-08 | -1.6608e-07 | 0.0015074 | 0.0015075 | 0.0015075 | 0.99037 | -0.1852 | 0.99036 | -0.18544 | 0.41415
115 | 0.0045648 | 0.001144 | -0.0045648 | -0.001144 | 7.2295e-08 | -6.6783e-09 | 0.0068517 | 0.0068517 | 0.0068517 | 0.99136 | -0.16603 | 0.99134 | -0.16636 | 1.8823

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.25071 | 0.063413

## res_load
| p_mw | q_mvar
0 | 0.0010985 | 0.00027531
1 | 0.0011013 | 0.00027601
2 | 0.0014826 | 0.00037157
3 | 0.001428 | 0.00035788
4 | 0.0020913 | 0.00052412
5 | 0.00070628 | 0.00017701
6 | 0.0022993 | 0.00057626
7 | 0.0014002 | 0.00035093
8 | 0.0010298 | 0.00025809
9 | 0.0017795 | 0.00044599
10 | 0.0023945 | 0.00060011
11 | 0.001208 | 0.00030274
12 | 0.0017096 | 0.00042846
13 | 0.016643 | 0.0041711
14 | 0.0038592 | 0.0009672
15 | 0.0022173 | 0.0005557
16 | 0.0026404 | 0.00066175
17 | 0.0020571 | 0.00051555
18 | 0.001705 | 0.0004273
19 | 0.0014232 | 0.00035669
20 | 0.0018223 | 0.00045671
21 | 0.0013706 | 0.00034349
22 | 0.0048613 | 0.0012184
23 | 0.070914 | 0.017773
24 | 0.0026236 | 0.00065754
25 | 0.0015156 | 0.00037983
26 | 0.0025668 | 0.0006433
27 | 0.0017662 | 0.00044265
28 | 0.0027843 | 0.0006978
29 | 0.0013545 | 0.00033947
30 | 0.0016352 | 0.00040982
31 | 0.0033974 | 0.00085148
32 | 0.00028783 | 7.2137e-05
33 | 0.0018354 | 0.00046001
34 | 0.00024778 | 6.2099e-05
35 | 0.0011074 | 0.00027754
36 | 0.002007 | 0.000503
37 | 0.00079929 | 0.00020032
38 | 0.0037522 | 0.00094038
39 | 0.003308 | 0.00082906
40 | 0.00082077 | 0.0002057
41 | 0.002891 | 0.00072457
42 | 0.0030446 | 0.00076305
43 | 0.002023 | 0.000507
44 | 0.0039727 | 0.00099566
45 | 0.0017633 | 0.00044192
46 | 0.0028312 | 0.00070958
47 | 0.0025032 | 0.00062737
48 | 0.00096283 | 0.00024131
49 | 0.0014282 | 0.00035795
50 | 0.0011158 | 0.00027964
51 | 0.0011558 | 0.00028967
52 | 0.0016243 | 0.00040708
53 | 0.0032446 | 0.00081318
54 | 0.0017276 | 0.00043297
55 | 0.0034127 | 0.0008553
56 | 0.0011148 | 0.00027939
57 | 0.006552 | 0.0016421
58 | 0.0024305 | 0.00060913
59 | 0.0021732 | 0.00054465
60 | 0.0018637 | 0.00046708
61 | 0.00096872 | 0.00024278
62 | 0.0058907 | 0.0014763
63 | 0.00091358 | 0.00022896
64 | 0.00047395 | 0.00011878
65 | 0.00072396 | 0.00018144
66 | 0.00049255 | 0.00012344
67 | 0.001519 | 0.0003807
68 | 0.00045183 | 0.00011324
69 | 0.00075317 | 0.00018876
70 | 0.00065515 | 0.0001642
71 | 0.00048824 | 0.00012237
72 | 0.0013897 | 0.0003483
73 | 0.006164 | 0.0015448
74 | 0.0012354 | 0.00030962
75 | 0.001665 | 0.0004173
76 | 0.00084007 | 0.00021054
77 | 0.0008468 | 0.00021223
78 | 0.0010793 | 0.0002705
79 | 0.0016403 | 0.00041111
80 | 0.0022925 | 0.00057456
81 | 0.0014738 | 0.00036937
82 | 0.0045648 | 0.001144
83 | 0.0010033 | 0.00025146

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1