## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2525-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2525-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2525-3_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2525-3_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2525-3_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2525-3_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2525-3_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2525-3_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2525-3_0_3_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_2525-3_0_3_node_37 | 0.4 | n |  | TRUE
10 | bus_LV_2525-3_0_3_node_34 | 0.4 | n |  | TRUE
11 | bus_LV_2525-3_0_3_node_180 | 0.4 | n |  | TRUE
12 | bus_LV_2525-3_0_3_node_185 | 0.4 | n |  | TRUE
13 | bus_LV_2525-3_0_3_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_2525-3_0_3_node_83 | 0.4 | n |  | TRUE
15 | bus_LV_2525-3_0_3_node_80 | 0.4 | n |  | TRUE
16 | bus_LV_2525-3_0_3_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_2525-3_0_3_node_178 | 0.4 | n |  | TRUE
18 | bus_LV_2525-3_0_3_node_186 | 0.4 | n |  | TRUE
19 | bus_LV_2525-3_0_3_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_2525-3_0_3_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_2525-3_0_3_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2525-3_0_3_node_172 | 0.4 | n |  | TRUE
23 | bus_LV_2525-3_0_3_node_173 | 0.4 | n |  | TRUE
24 | bus_LV_2525-3_0_3_node_200 | 0.4 | n |  | TRUE
25 | bus_LV_2525-3_0_3_node_199 | 0.4 | n |  | TRUE
26 | bus_LV_2525-3_0_3_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_2525-3_0_3_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2525-3_0_3_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_2525-3_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_2525-3_0_3_node_88 | 0.4 | n |  | TRUE
31 | bus_LV_2525-3_0_3_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_2525-3_0_3_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_2525-3_0_3_node_182 | 0.4 | n |  | TRUE
34 | bus_LV_2525-3_0_3_node_230 | 0.4 | n |  | TRUE
35 | bus_LV_2525-3_0_3_node_226 | 0.4 | n |  | TRUE
36 | bus_LV_2525-3_0_3_node_183 | 0.4 | n |  | TRUE
37 | bus_LV_2525-3_0_3_node_184 | 0.4 | n |  | TRUE
38 | bus_LV_2525-3_0_3_node_179 | 0.4 | n |  | TRUE
39 | bus_LV_2525-3_0_3_node_231 | 0.4 | n |  | TRUE
40 | bus_LV_2525-3_0_3_node_225 | 0.4 | n |  | TRUE
41 | bus_LV_2525-3_0_3_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_2525-3_0_3_node_155 | 0.4 | n |  | TRUE
43 | bus_LV_2525-3_0_3_node_143 | 0.4 | n |  | TRUE
44 | bus_LV_2525-3_0_3_node_154 | 0.4 | n |  | TRUE
45 | bus_LV_2525-3_0_3_node_150 | 0.4 | n |  | TRUE
46 | bus_LV_2525-3_0_3_node_151 | 0.4 | n |  | TRUE
47 | bus_LV_2525-3_0_3_node_81 | 0.4 | n |  | TRUE
48 | bus_LV_2525-3_0_3_node_78 | 0.4 | n |  | TRUE
49 | bus_LV_2525-3_0_3_node_137 | 0.4 | n |  | TRUE
50 | bus_LV_2525-3_0_3_node_89 | 0.4 | n |  | TRUE
51 | bus_LV_2525-3_0_3_node_156 | 0.4 | n |  | TRUE
52 | bus_LV_2525-3_0_3_node_136 | 0.4 | n |  | TRUE
53 | bus_LV_2525-3_0_3_node_90 | 0.4 | n |  | TRUE
54 | bus_LV_2525-3_0_3_node_87 | 0.4 | n |  | TRUE
55 | bus_LV_2525-3_0_3_node_82 | 0.4 | n |  | TRUE
56 | bus_LV_2525-3_0_3_node_92 | 0.4 | n |  | TRUE
57 | bus_LV_2525-3_0_3_node_91 | 0.4 | n |  | TRUE
58 | bus_LV_2525-3_0_3_node_84 | 0.4 | n |  | TRUE
59 | bus_LV_2525-3_0_3_node_85 | 0.4 | n |  | TRUE
60 | bus_LV_2525-3_0_3_node_86 | 0.4 | n |  | TRUE
61 | bus_LV_2525-3_0_3_node_99 | 0.4 | n |  | TRUE
62 | bus_LV_2525-3_0_3_node_100 | 0.4 | n |  | TRUE
63 | bus_LV_2525-3_0_3_node_101 | 0.4 | n |  | TRUE
64 | bus_LV_2525-3_0_3_node_102 | 0.4 | n |  | TRUE
65 | bus_LV_2525-3_0_3_node_103 | 0.4 | n |  | TRUE
66 | bus_LV_2525-3_0_3_node_104 | 0.4 | n |  | TRUE
67 | bus_LV_2525-3_0_3_node_162 | 0.4 | n |  | TRUE
68 | bus_LV_2525-3_0_3_node_121 | 0.4 | n |  | TRUE
69 | bus_LV_2525-3_0_3_node_105 | 0.4 | n |  | TRUE
70 | bus_LV_2525-3_0_3_node_174 | 0.4 | n |  | TRUE
71 | bus_LV_2525-3_0_3_node_120 | 0.4 | n |  | TRUE
72 | bus_LV_2525-3_0_3_node_160 | 0.4 | n |  | TRUE
73 | bus_LV_2525-3_0_3_node_161 | 0.4 | n |  | TRUE
74 | bus_LV_2525-3_0_3_node_106 | 0.4 | n |  | TRUE
75 | bus_LV_2525-3_0_3_node_107 | 0.4 | n |  | TRUE
76 | bus_LV_2525-3_0_3_node_170 | 0.4 | n |  | TRUE
77 | bus_LV_2525-3_0_3_node_195 | 0.4 | n |  | TRUE
78 | bus_LV_2525-3_0_3_node_169 | 0.4 | n |  | TRUE
79 | bus_LV_2525-3_0_3_node_196 | 0.4 | n |  | TRUE
80 | bus_LV_2525-3_0_3_node_108 | 0.4 | n |  | TRUE
81 | bus_LV_2525-3_0_3_node_109 | 0.4 | n |  | TRUE
82 | bus_LV_2525-3_0_3_node_110 | 0.4 | n |  | TRUE
83 | bus_LV_2525-3_0_3_node_111 | 0.4 | n |  | TRUE
84 | bus_LV_2525-3_0_3_node_112 | 0.4 | n |  | TRUE
85 | bus_LV_2525-3_0_3_node_113 | 0.4 | n |  | TRUE
86 | bus_LV_2525-3_0_3_node_115 | 0.4 | n |  | TRUE
87 | bus_LV_2525-3_0_3_node_118 | 0.4 | n |  | TRUE
88 | bus_LV_2525-3_0_3_node_116 | 0.4 | n |  | TRUE
89 | bus_LV_2525-3_0_3_node_117 | 0.4 | n |  | TRUE
90 | bus_LV_2525-3_0_3_node_119 | 0.4 | n |  | TRUE
91 | bus_LV_2525-3_0_3_node_157 | 0.4 | n |  | TRUE
92 | bus_LV_2525-3_0_3_node_158 | 0.4 | n |  | TRUE
93 | bus_LV_2525-3_0_3_node_148 | 0.4 | n |  | TRUE
94 | bus_LV_2525-3_0_3_node_149 | 0.4 | n |  | TRUE
95 | bus_LV_2525-3_0_3_node_146 | 0.4 | n |  | TRUE
96 | bus_LV_2525-3_0_3_node_153 | 0.4 | n |  | TRUE
97 | bus_LV_2525-3_0_3_node_138 | 0.4 | n |  | TRUE
98 | bus_LV_2525-3_0_3_node_139 | 0.4 | n |  | TRUE
99 | bus_LV_2525-3_0_3_node_140 | 0.4 | n |  | TRUE
100 | bus_LV_2525-3_0_3_node_141 | 0.4 | n |  | TRUE
101 | bus_LV_2525-3_0_3_node_147 | 0.4 | n |  | TRUE
102 | bus_LV_2525-3_0_3_node_159 | 0.4 | n |  | TRUE
103 | bus_LV_2525-3_0_3_node_142 | 0.4 | n |  | TRUE
104 | bus_LV_2525-3_0_3_node_152 | 0.4 | n |  | TRUE
105 | bus_LV_2525-3_0_3_node_144 | 0.4 | n |  | TRUE
106 | bus_LV_2525-3_0_3_node_163 | 0.4 | n |  | TRUE
107 | bus_LV_2525-3_0_3_node_145 | 0.4 | n |  | TRUE
108 | bus_LV_2525-3_0_3_node_164 | 0.4 | n |  | TRUE
109 | bus_LV_2525-3_0_3_node_165 | 0.4 | n |  | TRUE
110 | bus_LV_2525-3_0_3_node_166 | 0.4 | n |  | TRUE
111 | bus_LV_2525-3_0_3_node_167 | 0.4 | n |  | TRUE
112 | bus_LV_2525-3_0_3_node_171 | 0.4 | n |  | TRUE
113 | bus_LV_2525-3_0_3_node_181 | 0.4 | n |  | TRUE
114 | bus_LV_2525-3_0_3_node_192 | 0.4 | n |  | TRUE
115 | bus_LV_2525-3_0_3_node_168 | 0.4 | n |  | TRUE
116 | bus_LV_2525-3_0_3_node_176 | 0.4 | n |  | TRUE
117 | bus_LV_2525-3_0_3_node_177 | 0.4 | n |  | TRUE
118 | bus_LV_2525-3_0_3_node_193 | 0.4 | n |  | TRUE
119 | bus_LV_2525-3_0_3_node_187 | 0.4 | n |  | TRUE
120 | bus_LV_2525-3_0_3_node_189 | 0.4 | n |  | TRUE
121 | bus_LV_2525-3_0_3_node_188 | 0.4 | n |  | TRUE
122 | bus_LV_2525-3_0_3_node_191 | 0.4 | n |  | TRUE
123 | bus_LV_2525-3_0_3_node_190 | 0.4 | n |  | TRUE
124 | bus_LV_2525-3_0_3_node_220 | 0.4 | n |  | TRUE
125 | bus_LV_2525-3_0_3_node_194 | 0.4 | n |  | TRUE
126 | bus_LV_2525-3_0_3_node_197 | 0.4 | n |  | TRUE
127 | bus_LV_2525-3_0_3_node_198 | 0.4 | n |  | TRUE
128 | bus_LV_2525-3_0_3_node_204 | 0.4 | n |  | TRUE
129 | bus_LV_2525-3_0_3_node_203 | 0.4 | n |  | TRUE
130 | bus_LV_2525-3_0_3_node_201 | 0.4 | n |  | TRUE
131 | bus_LV_2525-3_0_3_node_202 | 0.4 | n |  | TRUE
132 | bus_LV_2525-3_0_3_node_223 | 0.4 | n |  | TRUE
133 | bus_LV_2525-3_0_3_node_222 | 0.4 | n |  | TRUE
134 | bus_LV_2525-3_0_3_node_224 | 0.4 | n |  | TRUE
135 | bus_LV_2525-3_0_3_node_227 | 0.4 | n |  | TRUE
136 | bus_MV_392_1_node_41 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2525-3_0_3_load_0 | 0 | 0.0025756 | 0.00064552 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2525-3_0_3_load_1 | 1 | 0.0018793 | 0.000471 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2525-3_0_3_load_4 | 4 | 0.0020093 | 0.00050357 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2525-3_0_3_load_6 | 6 | 0.0040045 | 0.0010036 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2525-3_0_3_load_7 | 7 | 0.0029778 | 0.0007463 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2525-3_0_3_load_17 | 8 | 0.0053845 | 0.0013495 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2525-3_0_3_load_34 | 10 | 0.0055743 | 0.0013971 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2525-3_0_3_load_180 | 11 | 0.0010124 | 0.00025374 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2525-3_0_3_load_185 | 12 | 0.0022638 | 0.00056736 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2525-3_0_3_load_83 | 14 | 0.0033604 | 0.0008422 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2525-3_0_3_load_80 | 15 | 0.0017789 | 0.00044583 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2525-3_0_3_load_35 | 16 | 0.0026214 | 0.00065699 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2525-3_0_3_load_186 | 18 | 0.0019178 | 0.00048065 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2525-3_0_3_load_8 | 19 | 0.0015731 | 0.00039425 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2525-3_0_3_load_9 | 20 | 0.0017528 | 0.0004393 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2525-3_0_3_load_10 | 21 | 0.003264 | 0.00081803 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2525-3_0_3_load_172 | 22 | 0.0027576 | 0.00069112 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2525-3_0_3_load_200 | 24 | 0.0028965 | 0.00072592 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2525-3_0_3_load_199 | 25 | 0.0020717 | 0.00051921 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2525-3_0_3_load_13 | 26 | 0.00141 | 0.00035339 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2525-3_0_3_load_14 | 27 | 0.0019708 | 0.00049394 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2525-3_0_3_load_15 | 28 | 0.0026321 | 0.00065967 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2525-3_0_3_load_88 | 30 | 0.0017393 | 0.0004359 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2525-3_0_3_load_20 | 31 | 0.0097032 | 0.0024319 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2525-3_0_3_load_230 | 34 | 0.0020767 | 0.00052046 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2525-3_0_3_load_226 | 35 | 0.0044931 | 0.0011261 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2525-3_0_3_load_183 | 36 | 0.0076433 | 0.0019156 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2525-3_0_3_load_184 | 37 | 0.0036675 | 0.00091917 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2525-3_0_3_load_179 | 38 | 0.0023319 | 0.00058444 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2525-3_0_3_load_231 | 39 | 0.0044702 | 0.0011203 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2525-3_0_3_load_225 | 40 | 0.0083243 | 0.0020863 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2525-3_0_3_load_143 | 43 | 0.0031267 | 0.00078363 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2525-3_0_3_load_154 | 44 | 0.0069416 | 0.0017397 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2525-3_0_3_load_150 | 45 | 0.0052861 | 0.0013248 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2525-3_0_3_load_81 | 47 | 0.0051513 | 0.001291 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2525-3_0_3_load_136 | 52 | 0.0015188 | 0.00038065 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2525-3_0_3_load_90 | 53 | 0.0016289 | 0.00040825 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2525-3_0_3_load_87 | 54 | 0.0016453 | 0.00041236 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2525-3_0_3_load_82 | 55 | 0.002661 | 0.00066691 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2525-3_0_3_load_92 | 56 | 0.0041042 | 0.0010286 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2525-3_0_3_load_91 | 57 | 0.002071 | 0.00051905 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2525-3_0_3_load_84 | 58 | 0.0018996 | 0.00047608 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2525-3_0_3_load_85 | 59 | 0.0031257 | 0.00078338 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2525-3_0_3_load_86 | 60 | 0.0016597 | 0.00041596 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2525-3_0_3_load_99 | 61 | 0.0025998 | 0.00065156 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2525-3_0_3_load_100 | 62 | 0.0022772 | 0.00057073 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2525-3_0_3_load_101 | 63 | 0.0031881 | 0.00079902 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2525-3_0_3_load_102 | 64 | 0.002893 | 0.00072505 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2525-3_0_3_load_104 | 66 | 0.00178 | 0.0004461 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2525-3_0_3_load_162 | 67 | 0.0048199 | 0.001208 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2525-3_0_3_load_121 | 68 | 0.0021471 | 0.00053812 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2525-3_0_3_load_174 | 70 | 0.0034431 | 0.00086292 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2525-3_0_3_load_120 | 71 | 0.0090412 | 0.0022659 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2525-3_0_3_load_160 | 72 | 0.0025252 | 0.00063287 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2525-3_0_3_load_161 | 73 | 0.0035775 | 0.0008966 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2525-3_0_3_load_106 | 74 | 0.0019052 | 0.00047748 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2525-3_0_3_load_107 | 75 | 0.0027434 | 0.00068757 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2525-3_0_3_load_170 | 76 | 0.0024252 | 0.00060781 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2525-3_0_3_load_195 | 77 | 0.0017551 | 0.00043986 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2525-3_0_3_load_196 | 79 | 0.0041496 | 0.00104 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2525-3_0_3_load_108 | 80 | 0.0021112 | 0.00052912 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2525-3_0_3_load_109 | 81 | 0.0035991 | 0.00090202 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2525-3_0_3_load_111 | 83 | 0.0034416 | 0.00086254 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2525-3_0_3_load_112 | 84 | 0.0021067 | 0.000528 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2525-3_0_3_load_113 | 85 | 0.0034209 | 0.00085735 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2525-3_0_3_load_118 | 87 | 0.003121 | 0.00078221 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2525-3_0_3_load_116 | 88 | 0.0025643 | 0.00064267 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2525-3_0_3_load_117 | 89 | 0.0047946 | 0.0012016 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2525-3_0_3_load_157 | 91 | 0.002974 | 0.00074536 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2525-3_0_3_load_158 | 92 | 0.0011237 | 0.00028163 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2525-3_0_3_load_149 | 94 | 0.0027033 | 0.00067751 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2525-3_0_3_load_146 | 95 | 0.0034284 | 0.00085924 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2525-3_0_3_load_153 | 96 | 0.0056019 | 0.001404 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2525-3_0_3_load_138 | 97 | 0.0015087 | 0.00037812 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2525-3_0_3_load_139 | 98 | 0.0029671 | 0.00074364 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2525-3_0_3_load_147 | 101 | 0.0034621 | 0.00086768 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2525-3_0_3_load_159 | 102 | 0.001126 | 0.0002822 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2525-3_0_3_load_142 | 103 | 0.0029648 | 0.00074305 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2525-3_0_3_load_144 | 105 | 0.0015036 | 0.00037685 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2525-3_0_3_load_145 | 107 | 0.0029887 | 0.00074904 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2525-3_0_3_load_164 | 108 | 0.0022544 | 0.00056501 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2525-3_0_3_load_165 | 109 | 0.0014415 | 0.00036126 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2525-3_0_3_load_166 | 110 | 0.0027572 | 0.00069103 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2525-3_0_3_load_167 | 111 | 0.0020288 | 0.00050847 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2525-3_0_3_load_171 | 112 | 0.001783 | 0.00044686 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2525-3_0_3_load_192 | 114 | 0.0030814 | 0.00077227 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2525-3_0_3_load_168 | 115 | 0.0014939 | 0.00037442 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2525-3_0_3_load_176 | 116 | 0.0019793 | 0.00049607 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2525-3_0_3_load_177 | 117 | 0.0016936 | 0.00042446 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2525-3_0_3_load_193 | 118 | 0.0040727 | 0.0010207 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2525-3_0_3_load_187 | 119 | 0.0022553 | 0.00056522 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2525-3_0_3_load_189 | 120 | 0.0024309 | 0.00060925 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2525-3_0_3_load_190 | 123 | 0.0076412 | 0.0019151 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2525-3_0_3_load_220 | 124 | 0.0092755 | 0.0023247 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2525-3_0_3_load_194 | 125 | 0.0019418 | 0.00048666 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2525-3_0_3_load_198 | 127 | 0.0034303 | 0.00085972 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2525-3_0_3_load_203 | 129 | 0.0028469 | 0.0007135 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2525-3_0_3_load_201 | 130 | 0.0021967 | 0.00055054 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2525-3_0_3_load_202 | 131 | 0.0034343 | 0.00086073 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2525-3_0_3_load_223 | 132 | 0.0025411 | 0.00063686 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2525-3_0_3_load_222 | 133 | 0.0081572 | 0.0020444 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2525-3_0_3_load_224 | 134 | 0.0031466 | 0.0007886 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2525-3_0_3_load_227 | 135 | 0.002434 | 0.00061002 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 105 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2525-3_0_3_line_0 |  | 0 | 1 | 0.021727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2525-3_0_3_line_1 |  | 1 | 2 | 0.011894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2525-3_0_3_line_2 |  | 2 | 6 | 0.01107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2525-3_0_3_line_3 |  | 2 | 7 | 0.011769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2525-3_0_3_line_4 |  | 3 | 4 | 0.01897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2525-3_0_3_line_5 |  | 3 | 5 | 0.015492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2525-3_0_3_line_6 |  | 4 | 8 | 0.0049626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2525-3_0_3_line_7 |  | 5 | 9 | 0.028625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2525-3_0_3_line_8 |  | 5 | 10 | 0.013847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2525-3_0_3_line_9 |  | 6 | 11 | 0.0096468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2525-3_0_3_line_10 |  | 7 | 12 | 0.011645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2525-3_0_3_line_11 |  | 8 | 13 | 0.031594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2525-3_0_3_line_12 |  | 9 | 14 | 0.025662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2525-3_0_3_line_13 |  | 9 | 15 | 0.0057015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2525-3_0_3_line_14 |  | 10 | 16 | 0.015655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2525-3_0_3_line_15 |  | 11 | 17 | 0.0041252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2525-3_0_3_line_16 |  | 12 | 18 | 0.0058626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2525-3_0_3_line_17 |  | 13 | 31 | 0.018781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2525-3_0_3_line_18 |  | 14 | 29 | 0.042845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2525-3_0_3_line_19 |  | 15 | 47 | 0.0003882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2525-3_0_3_line_20 |  | 16 | 41 | 0.0029741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2525-3_0_3_line_21 |  | 17 | 113 | 0.014436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2525-3_0_3_line_22 |  | 17 | 116 | 0.016644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2525-3_0_3_line_23 |  | 19 | 20 | 0.017358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2525-3_0_3_line_24 |  | 20 | 21 | 0.039336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2525-3_0_3_line_25 |  | 21 | 22 | 0.025564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2525-3_0_3_line_26 |  | 22 | 23 | 0.038617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2525-3_0_3_line_27 |  | 23 | 70 | 0.019683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2525-3_0_3_line_28 |  | 24 | 25 | 0.021557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2525-3_0_3_line_29 |  | 25 | 127 | 0.022682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2525-3_0_3_line_30 |  | 26 | 27 | 0.021386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2525-3_0_3_line_31 |  | 26 | 28 | 0.014888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2525-3_0_3_line_32 |  | 28 | 29 | 0.019991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2525-3_0_3_line_33 |  | 29 | 30 | 0.011427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2525-3_0_3_line_34 |  | 31 | 35 | 0.0018678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2525-3_0_3_line_35 |  | 32 | 33 | 0.03876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2525-3_0_3_line_36 |  | 32 | 34 | 0.023155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2525-3_0_3_line_37 |  | 33 | 36 | 0.015445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2525-3_0_3_line_38 |  | 33 | 37 | 0.017438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2525-3_0_3_line_39 |  | 33 | 38 | 0.012177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2525-3_0_3_line_40 |  | 34 | 39 | 0.0040494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2525-3_0_3_line_41 |  | 35 | 40 | 0.0019772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2525-3_0_3_line_42 |  | 36 | 119 | 0.0083935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2525-3_0_3_line_43 |  | 37 | 120 | 0.019689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2525-3_0_3_line_44 |  | 38 | 117 | 0.023152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2525-3_0_3_line_45 |  | 40 | 135 | 0.012703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2525-3_0_3_line_46 |  | 41 | 42 | 0.023244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2525-3_0_3_line_47 |  | 42 | 43 | 0.0101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2525-3_0_3_line_48 |  | 42 | 44 | 0.013061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2525-3_0_3_line_49 |  | 43 | 99 | 0.014772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2525-3_0_3_line_50 |  | 44 | 46 | 0.036013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2525-3_0_3_line_51 |  | 45 | 46 | 0.018689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2525-3_0_3_line_52 |  | 46 | 104 | 0.004831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2525-3_0_3_line_53 |  | 47 | 55 | 0.0090425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2525-3_0_3_line_54 |  | 48 | 49 | 0.040514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2525-3_0_3_line_55 |  | 48 | 50 | 0.015069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2525-3_0_3_line_56 |  | 49 | 51 | 0.013387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2525-3_0_3_line_57 |  | 49 | 52 | 0.036509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2525-3_0_3_line_58 |  | 50 | 53 | 0.01801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2525-3_0_3_line_59 |  | 50 | 54 | 0.01632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2525-3_0_3_line_60 |  | 51 | 96 | 0.021136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2525-3_0_3_line_61 |  | 53 | 57 | 0.030795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2525-3_0_3_line_62 |  | 54 | 59 | 0.011637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2525-3_0_3_line_63 |  | 55 | 56 | 0.022602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2525-3_0_3_line_64 |  | 56 | 57 | 0.026352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2525-3_0_3_line_65 |  | 58 | 59 | 0.0020373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2525-3_0_3_line_66 |  | 58 | 60 | 0.0072476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2525-3_0_3_line_67 |  | 61 | 62 | 0.02786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2525-3_0_3_line_68 |  | 61 | 63 | 0.027321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2525-3_0_3_line_69 |  | 62 | 64 | 0.013733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2525-3_0_3_line_70 |  | 63 | 65 | 0.016101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2525-3_0_3_line_71 |  | 64 | 66 | 0.02172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2525-3_0_3_line_72 |  | 65 | 67 | 0.019531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2525-3_0_3_line_73 |  | 65 | 68 | 0.013732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2525-3_0_3_line_74 |  | 66 | 69 | 0.020464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2525-3_0_3_line_75 |  | 67 | 70 | 0.0056739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2525-3_0_3_line_76 |  | 68 | 71 | 0.021126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2525-3_0_3_line_77 |  | 69 | 74 | 0.020393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2525-3_0_3_line_78 |  | 69 | 75 | 0.0069115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2525-3_0_3_line_79 |  | 72 | 73 | 0.0015972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2525-3_0_3_line_80 |  | 73 | 90 | 0.017318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2525-3_0_3_line_81 |  | 74 | 76 | 0.0083226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2525-3_0_3_line_82 |  | 75 | 77 | 0.016281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2525-3_0_3_line_83 |  | 76 | 78 | 0.018061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2525-3_0_3_line_84 |  | 77 | 79 | 0.018414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2525-3_0_3_line_85 |  | 78 | 112 | 0.015778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_2525-3_0_3_line_86 |  | 78 | 115 | 0.019888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2525-3_0_3_line_87 |  | 79 | 130 | 0.0065404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2525-3_0_3_line_88 |  | 80 | 81 | 0.00090954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2525-3_0_3_line_89 |  | 80 | 82 | 0.012488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2525-3_0_3_line_90 |  | 81 | 83 | 0.02841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2525-3_0_3_line_91 |  | 82 | 84 | 0.0151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2525-3_0_3_line_92 |  | 82 | 85 | 0.017566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2525-3_0_3_line_93 |  | 84 | 86 | 0.020934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2525-3_0_3_line_94 |  | 85 | 87 | 0.018339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2525-3_0_3_line_95 |  | 86 | 88 | 0.0094094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2525-3_0_3_line_96 |  | 86 | 89 | 0.021404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2525-3_0_3_line_97 |  | 87 | 90 | 0.0053629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2525-3_0_3_line_98 |  | 88 | 91 | 0.0027545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2525-3_0_3_line_99 |  | 91 | 92 | 0.0062009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2525-3_0_3_line_100 |  | 92 | 102 | 0.022096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2525-3_0_3_line_101 |  | 93 | 94 | 0.0066727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_2525-3_0_3_line_102 |  | 93 | 95 | 0.016866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_2525-3_0_3_line_103 |  | 94 | 110 | 0.010348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_2525-3_0_3_line_104 |  | 95 | 107 | 0.020857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_2525-3_0_3_line_105 |  | 97 | 98 | 0.003299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2525-3_0_3_line_106 |  | 97 | 99 | 0.01744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2525-3_0_3_line_107 |  | 98 | 100 | 0.016491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2525-3_0_3_line_108 |  | 100 | 101 | 0.01687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
109 | LV_2525-3_0_3_line_109 |  | 100 | 102 | 0.016824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2525-3_0_3_line_110 |  | 101 | 107 | 0.0020513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_2525-3_0_3_line_111 |  | 103 | 104 | 0.0071683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2525-3_0_3_line_112 |  | 105 | 106 | 0.022082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_2525-3_0_3_line_113 |  | 106 | 108 | 0.021596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
114 | LV_2525-3_0_3_line_114 |  | 106 | 109 | 0.01379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2525-3_0_3_line_115 |  | 108 | 112 | 0.0083257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_2525-3_0_3_line_116 |  | 109 | 113 | 0.023203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2525-3_0_3_line_117 |  | 110 | 111 | 0.013546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_2525-3_0_3_line_118 |  | 111 | 115 | 0.010722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_2525-3_0_3_line_119 |  | 113 | 114 | 0.039846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2525-3_0_3_line_120 |  | 114 | 118 | 0.03494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2525-3_0_3_line_121 |  | 116 | 117 | 0.012254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2525-3_0_3_line_122 |  | 118 | 125 | 0.020619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2525-3_0_3_line_123 |  | 119 | 121 | 0.012303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2525-3_0_3_line_124 |  | 121 | 122 | 0.014043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2525-3_0_3_line_125 |  | 121 | 123 | 0.042311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2525-3_0_3_line_126 |  | 122 | 124 | 0.054462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2525-3_0_3_line_127 |  | 125 | 126 | 0.030413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2525-3_0_3_line_128 |  | 125 | 127 | 0.024375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2525-3_0_3_line_129 |  | 126 | 128 | 0.011889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2525-3_0_3_line_130 |  | 126 | 129 | 0.037152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2525-3_0_3_line_131 |  | 128 | 132 | 0.024364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2525-3_0_3_line_132 |  | 130 | 131 | 0.0039819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2525-3_0_3_line_133 |  | 132 | 133 | 0.032569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2525-3_0_3_line_134 |  | 133 | 134 | 0.00071053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2525-3_0_3_trafo_144 | 0.63 MVA 20/0.4 kV | 136 | 105 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2612051.2974 | 1225555.9053 | 2612070.9086 | 1225565.2565
1 | 2612081.6448 | 1225570.3759 | 2612070.9086 | 1225565.2565
2 | 2612081.6448 | 1225570.3759 | 2612091.6504 | 1225575.1125
3 | 2612081.6448 | 1225570.3759 | 2612072.0235 | 1225577.1542
4 | 2612022.5698 | 1225542.207 | 2612021.1308 | 1225545.3615 | 2612014.6922 | 1225559.4641
5 | 2612008.4612 | 1225535.7193 | 2612022.5698 | 1225542.207
6 | 2612014.6922 | 1225559.4641 | 2612012.6312 | 1225563.9785
7 | 2612008.4612 | 1225535.7193 | 2611986.918 | 1225524.6919 | 2611982.9198 | 1225522.6493
8 | 2612008.4612 | 1225535.7193 | 2612009.8622 | 1225532.6092 | 2612019.5968 | 1225528.8485
9 | 2612091.6504 | 1225575.1125 | 2612100.3695 | 1225579.2402
10 | 2612062.5037 | 1225583.861 | 2612072.0235 | 1225577.1542
11 | 2612003.221 | 1225593.5205 | 2612002.7164 | 1225588.1496 | 2612004.0613 | 1225582.7492 | 2612012.6312 | 1225563.9785
12 | 2611982.9198 | 1225522.6493 | 2611977.9582 | 1225532.3451 | 2611972.42 | 1225542.3065 | 2611970.6941 | 1225545.2043
13 | 2611982.9198 | 1225522.6493 | 2611985.3854 | 1225517.5085
14 | 2612019.5968 | 1225528.8485 | 2612034.2001 | 1225523.2071
15 | 2612104.0981 | 1225581.0053 | 2612100.3695 | 1225579.2402
16 | 2612057.711 | 1225587.2375 | 2612062.5037 | 1225583.861
17 | 2612003.221 | 1225593.5205 | 2611985.3744 | 1225599.3713
18 | 2611946.8439 | 1225580.7335 | 2611956.7162 | 1225567.79 | 2611962.989 | 1225558.1414 | 2611970.6941 | 1225545.2043
19 | 2611985.3854 | 1225517.5085 | 2611985.5533 | 1225517.1585
20 | 2612036.9744 | 1225522.1353 | 2612034.2001 | 1225523.2071
21 | 2612117.2675 | 1225587.0021 | 2612104.0981 | 1225581.0053
22 | 2612104.0981 | 1225581.0053 | 2612096.1954 | 1225595.6536
23 | 2612270.1581 | 1225534.356 | 2612272.4286 | 1225550.7527 | 2612272.5101 | 1225551.5535
24 | 2612268.8038 | 1225495.1734 | 2612268.7801 | 1225496.5801 | 2612267.9653 | 1225509.4749 | 2612268.4325 | 1225521.8942 | 2612270.1581 | 1225534.356
25 | 2612268.3596 | 1225469.6535 | 2612269.1167 | 1225476.6024 | 2612268.8038 | 1225495.1734
26 | 2612265.0029 | 1225431.2118 | 2612265.1437 | 1225440.1395 | 2612268.3596 | 1225469.6535
27 | 2612265.0029 | 1225431.2118 | 2612245.4214 | 1225433.2046
28 | 2612246.1919 | 1225647.6058 | 2612256.4388 | 1225652.3017 | 2612265.6028 | 1225656.9724
29 | 2612246.1919 | 1225647.6058 | 2612225.5724 | 1225638.1562
30 | 2611930.07 | 1225550.167 | 2611920.854 | 1225530.8683
31 | 2611937.0146 | 1225563.3263 | 2611932.7343 | 1225555.7462 | 2611930.07 | 1225550.167
32 | 2611946.8439 | 1225580.7335 | 2611937.0146 | 1225563.3263
33 | 2611946.8439 | 1225580.7335 | 2611943.7658 | 1225584.8297 | 2611939.6945 | 1225589.641
34 | 2611983.5996 | 1225599.9531 | 2611985.3744 | 1225599.3713
35 | 2612038.3715 | 1225618.8282 | 2612072.7023 | 1225637.008
36 | 2612038.3715 | 1225618.8282 | 2612016.7675 | 1225627.1593
37 | 2612072.7023 | 1225637.008 | 2612066.8751 | 1225651.3114
38 | 2612072.7023 | 1225637.008 | 2612088.1496 | 1225645.0994
39 | 2612072.7023 | 1225637.008 | 2612079.0379 | 1225626.6088
40 | 2612012.9893 | 1225628.6162 | 2612016.7675 | 1225627.1593
41 | 2611981.7208 | 1225600.5691 | 2611983.5996 | 1225599.9531
42 | 2612066.8751 | 1225651.3114 | 2612063.7084 | 1225659.0846
43 | 2612087.4922 | 1225659.8125 | 2612093.7749 | 1225648.046 | 2612088.1496 | 1225645.0994
44 | 2612079.0379 | 1225626.6088 | 2612084.7033 | 1225617.3096 | 2612089.1017 | 1225608.8024 | 2612090.3771 | 1225606.4383
45 | 2611969.65 | 1225604.5263 | 2611981.7208 | 1225600.5691
46 | 2612058.7083 | 1225513.7297 | 2612036.9744 | 1225522.1353
47 | 2612058.7083 | 1225513.7297 | 2612068.1288 | 1225510.0872
48 | 2612058.7083 | 1225513.7297 | 2612059.0802 | 1225509.6947 | 2612060.2949 | 1225508.7744 | 2612062.0886 | 1225501.508
49 | 2612081.9063 | 1225504.7601 | 2612068.1288 | 1225510.0872
50 | 2612052.0346 | 1225470.1907 | 2612056.2823 | 1225476.2806 | 2612063.1233 | 1225485.711 | 2612065.3008 | 1225488.4948 | 2612062.0886 | 1225501.508
51 | 2612052.0346 | 1225470.1907 | 2612035.281 | 1225478.4729
52 | 2612052.0346 | 1225470.1907 | 2612056.3748 | 1225468.0426
53 | 2611985.5533 | 1225517.1585 | 2611988.8115 | 1225510.365 | 2611989.3787 | 1225508.9677
54 | 2612004.1964 | 1225398.408 | 2612008.1458 | 1225398.3714 | 2612044.8273 | 1225397.9894
55 | 2612004.7195 | 1225413.4623 | 2612004.4398 | 1225409.326 | 2612004.1964 | 1225398.408
56 | 2612046.127 | 1225411.3109 | 2612044.8273 | 1225397.9894
57 | 2612044.8273 | 1225397.9894 | 2612056.0789 | 1225396.7558 | 2612066.8117 | 1225393.3866 | 2612075.4098 | 1225388.6011 | 2612078.5218 | 1225385.9311
58 | 2612004.7195 | 1225413.4623 | 2612005.4011 | 1225428.9061 | 2612005.3773 | 1225431.4571
59 | 2612004.7195 | 1225413.4623 | 2611988.406 | 1225412.9979
60 | 2612046.127 | 1225411.3109 | 2612041.7814 | 1225416.1161 | 2612043.1613 | 1225430.708
61 | 2612005.3773 | 1225431.4571 | 2612005.3045 | 1225439.2564 | 2612004.8534 | 1225448.7388 | 2612003.9782 | 1225457.9869 | 2612003.2849 | 1225462.1425
62 | 2611977.4511 | 1225410.4943 | 2611979.1317 | 1225411.9768 | 2611982.0332 | 1225412.8165 | 2611988.406 | 1225412.9979
63 | 2611996.9346 | 1225487.6849 | 2611995.3268 | 1225493.2236 | 2611992.4146 | 1225501.4893 | 2611989.3787 | 1225508.9677
64 | 2611996.9346 | 1225487.6849 | 2611997.7846 | 1225484.7569 | 2612000.1805 | 1225476.9349 | 2612002.3594 | 1225467.6894 | 2612003.2849 | 1225462.1425
65 | 2611975.9234 | 1225409.1465 | 2611977.4511 | 1225410.4943
66 | 2611972.2822 | 1225402.88 | 2611975.9234 | 1225409.1465 | 2611975.9234 | 1225409.1465
67 | 2612224.2185 | 1225479.0061 | 2612226.7029 | 1225506.7546
68 | 2612224.2185 | 1225479.0061 | 2612221.7821 | 1225451.7934
69 | 2612227.9276 | 1225520.4332 | 2612226.7029 | 1225506.7546
70 | 2612220.3462 | 1225435.7564 | 2612221.7821 | 1225451.7934
71 | 2612227.9276 | 1225520.4332 | 2612228.8465 | 1225530.6961 | 2612228.5986 | 1225536.9993 | 2612226.8183 | 1225541.7866
72 | 2612220.3462 | 1225435.7564 | 2612239.7766 | 1225433.779
73 | 2612220.3462 | 1225435.7564 | 2612219.1745 | 1225422.0747
74 | 2612211.8943 | 1225554.531 | 2612217.1587 | 1225552.6518 | 2612221.4021 | 1225549.6031 | 2612225.748 | 1225544.6647 | 2612226.8183 | 1225541.7866
75 | 2612245.4214 | 1225433.2046 | 2612239.7766 | 1225433.779
76 | 2612221.1747 | 1225401.1883 | 2612219.3402 | 1225408.7607 | 2612218.9025 | 1225418.8991 | 2612219.1745 | 1225422.0747
77 | 2612211.8943 | 1225554.531 | 2612205.8683 | 1225554.4631 | 2612199.7022 | 1225552.4939 | 2612192.5818 | 1225549.0855
78 | 2612211.8943 | 1225554.531 | 2612217.4994 | 1225558.5746
79 | 2612181.6008 | 1225439.4631 | 2612180.0108 | 1225439.6152
80 | 2612162.7711 | 1225441.2645 | 2612180.0108 | 1225439.6152
81 | 2612185.0749 | 1225545.4922 | 2612192.5818 | 1225549.0855
82 | 2612217.4994 | 1225558.5746 | 2612230.7029 | 1225568.0997 | 2612230.7029 | 1225568.0997
83 | 2612169.0493 | 1225537.1891 | 2612173.8947 | 1225540.0451 | 2612180.5055 | 1225543.3049 | 2612185.0749 | 1225545.4922
84 | 2612230.7029 | 1225568.0997 | 2612241.2647 | 1225583.1836
85 | 2612169.0493 | 1225537.1891 | 2612163.1278 | 1225537.9442 | 2612157.6977 | 1225539.3006 | 2612153.7848 | 1225540.8593
86 | 2612169.0493 | 1225537.1891 | 2612170.6528 | 1225531.4779 | 2612169.4249 | 1225517.5764
87 | 2612245.0161 | 1225588.5413 | 2612241.2647 | 1225583.1836
88 | 2612144.0138 | 1225397.6624 | 2612144.1292 | 1225396.7602
89 | 2612142.4286 | 1225410.0493 | 2612144.0138 | 1225397.6624
90 | 2612144.1292 | 1225396.7602 | 2612147.7353 | 1225368.5801
91 | 2612142.4286 | 1225410.0493 | 2612136.9405 | 1225410.1049 | 2612130.3728 | 1225411.6814 | 2612127.8463 | 1225413.0151
92 | 2612142.4286 | 1225410.0493 | 2612149.1938 | 1225412.0309 | 2612154.5539 | 1225415.3215 | 2612157.2038 | 1225418.6147
93 | 2612111.0155 | 1225425.3835 | 2612124.6664 | 1225414.6938 | 2612127.8463 | 1225413.0151
94 | 2612157.2038 | 1225418.6147 | 2612158.5234 | 1225420.2547 | 2612160.8163 | 1225425.896 | 2612161.881 | 1225431.6793 | 2612162.2752 | 1225435.9246
95 | 2612111.0155 | 1225425.3835 | 2612107.676 | 1225431.2135 | 2612107.0601 | 1225433.8328
96 | 2612096.2428 | 1225409.8557 | 2612111.0155 | 1225425.3835
97 | 2612162.7711 | 1225441.2645 | 2612162.2752 | 1225435.9246
98 | 2612107.0601 | 1225433.8328 | 2612106.4297 | 1225436.5141
99 | 2612106.4297 | 1225436.5141 | 2612106.4297 | 1225436.5141 | 2612106.4482 | 1225442.3287 | 2612106.4853 | 1225442.7132
100 | 2612108.6095 | 1225464.7067 | 2612106.4853 | 1225442.7132
101 | 2612165.7922 | 1225476.4469 | 2612166.3793 | 1225483.0937
102 | 2612165.7922 | 1225476.4469 | 2612148.9927 | 1225477.9421
103 | 2612167.2897 | 1225493.4018 | 2612166.3793 | 1225483.0937
104 | 2612128.2174 | 1225479.7912 | 2612148.9927 | 1225477.9421
105 | 2612097.3708 | 1225496.6978 | 2612099.9698 | 1225494.6657
106 | 2612081.9063 | 1225504.7601 | 2612097.3708 | 1225496.6978
107 | 2612109.3707 | 1225481.4687 | 2612106.9793 | 1225487.0337 | 2612102.7461 | 1225492.4951 | 2612099.9698 | 1225494.6657
108 | 2612109.3707 | 1225481.4687 | 2612126.1741 | 1225479.9731
109 | 2612109.3707 | 1225481.4687 | 2612109.7001 | 1225475.9995 | 2612108.6095 | 1225464.7067
110 | 2612126.1741 | 1225479.9731 | 2612128.2174 | 1225479.7912
111 | 2612056.3748 | 1225468.0426 | 2612060.4671 | 1225473.928
112 | 2612125.9874 | 1225551.9325 | 2612109.6282 | 1225541.471 | 2612107.6437 | 1225539.6946
113 | 2612125.9874 | 1225551.9325 | 2612146.0502 | 1225543.9404
114 | 2612125.9874 | 1225551.9325 | 2612126.6426 | 1225561.5173 | 2612126.1118 | 1225565.6667
115 | 2612146.0502 | 1225543.9404 | 2612153.7848 | 1225540.8593
116 | 2612117.2675 | 1225587.0021 | 2612123.9886 | 1225573.241 | 2612125.9032 | 1225567.2969 | 2612126.1118 | 1225565.6667
117 | 2612167.2897 | 1225493.4018 | 2612168.4816 | 1225506.8956
118 | 2612168.4816 | 1225506.8956 | 2612169.4249 | 1225517.5764
119 | 2612117.2675 | 1225587.0021 | 2612153.247 | 1225604.1256
120 | 2612153.247 | 1225604.1256 | 2612184.7963 | 1225619.1407
121 | 2612096.1954 | 1225595.6536 | 2612090.3771 | 1225606.4383
122 | 2612203.4138 | 1225628.0013 | 2612184.7963 | 1225619.1407
123 | 2612059.0667 | 1225670.4779 | 2612063.7084 | 1225659.0846
124 | 2612059.0667 | 1225670.4779 | 2612053.7649 | 1225683.486
125 | 2612059.0667 | 1225670.4779 | 2612039.6917 | 1225659.6214 | 2612032.8026 | 1225662.8539 | 2612021.7101 | 1225657.1093
126 | 2612053.7649 | 1225683.486 | 2612107.7136 | 1225690.9472
127 | 2612187.7536 | 1225654.0958 | 2612203.4138 | 1225628.0013
128 | 2612203.4138 | 1225628.0013 | 2612225.5724 | 1225638.1562
129 | 2612181.6385 | 1225664.3004 | 2612187.7536 | 1225654.0958
130 | 2612187.7536 | 1225654.0958 | 2612181.0021 | 1225656.7058 | 2612173.2985 | 1225654.1886 | 2612154.958 | 1225660.1993 | 2612152.6597 | 1225661.2044
131 | 2612181.6385 | 1225664.3004 | 2612190.2753 | 1225677.5814 | 2612198.6889 | 1225678.9364
132 | 2612247.3001 | 1225591.8031 | 2612245.0161 | 1225588.5413
133 | 2612221.5273 | 1225668.3624 | 2612219.9349 | 1225677.7642 | 2612215.7959 | 1225681.6914 | 2612198.6889 | 1225678.9364
134 | 2612221.6459 | 1225667.6618 | 2612221.5273 | 1225668.3624

## bus_geodata
| x | y | coords
0 | 2612051.2974 | 1225555.9053
1 | 2612070.9086 | 1225565.2565
2 | 2612081.6448 | 1225570.3759
3 | 2612022.5698 | 1225542.207
4 | 2612014.6922 | 1225559.4641
5 | 2612008.4612 | 1225535.7193
6 | 2612091.6504 | 1225575.1125
7 | 2612072.0235 | 1225577.1542
8 | 2612012.6312 | 1225563.9785
9 | 2611982.9198 | 1225522.6493
10 | 2612019.5968 | 1225528.8485
11 | 2612100.3695 | 1225579.2402
12 | 2612062.5037 | 1225583.861
13 | 2612003.221 | 1225593.5205
14 | 2611970.6941 | 1225545.2043
15 | 2611985.3854 | 1225517.5085
16 | 2612034.2001 | 1225523.2071
17 | 2612104.0981 | 1225581.0053
18 | 2612057.711 | 1225587.2375
19 | 2612272.5101 | 1225551.5535
20 | 2612270.1581 | 1225534.356
21 | 2612268.8038 | 1225495.1734
22 | 2612268.3596 | 1225469.6535
23 | 2612265.0029 | 1225431.2118
24 | 2612265.6028 | 1225656.9724
25 | 2612246.1919 | 1225647.6058
26 | 2611930.07 | 1225550.167
27 | 2611920.854 | 1225530.8683
28 | 2611937.0146 | 1225563.3263
29 | 2611946.8439 | 1225580.7335
30 | 2611939.6945 | 1225589.641
31 | 2611985.3744 | 1225599.3713
32 | 2612038.3715 | 1225618.8282
33 | 2612072.7023 | 1225637.008
34 | 2612016.7675 | 1225627.1593
35 | 2611983.5996 | 1225599.9531
36 | 2612066.8751 | 1225651.3114
37 | 2612088.1496 | 1225645.0994
38 | 2612079.0379 | 1225626.6088
39 | 2612012.9893 | 1225628.6162
40 | 2611981.7208 | 1225600.5691
41 | 2612036.9744 | 1225522.1353
42 | 2612058.7083 | 1225513.7297
43 | 2612068.1288 | 1225510.0872
44 | 2612062.0886 | 1225501.508
45 | 2612035.281 | 1225478.4729
46 | 2612052.0346 | 1225470.1907
47 | 2611985.5533 | 1225517.1585
48 | 2612004.1964 | 1225398.408
49 | 2612044.8273 | 1225397.9894
50 | 2612004.7195 | 1225413.4623
51 | 2612046.127 | 1225411.3109
52 | 2612078.5218 | 1225385.9311
53 | 2612005.3773 | 1225431.4571
54 | 2611988.406 | 1225412.9979
55 | 2611989.3787 | 1225508.9677
56 | 2611996.9346 | 1225487.6849
57 | 2612003.2849 | 1225462.1425
58 | 2611975.9234 | 1225409.1465
59 | 2611977.4511 | 1225410.4943
60 | 2611972.2822 | 1225402.88
61 | 2612224.2185 | 1225479.0061
62 | 2612226.7029 | 1225506.7546
63 | 2612221.7821 | 1225451.7934
64 | 2612227.9276 | 1225520.4332
65 | 2612220.3462 | 1225435.7564
66 | 2612226.8183 | 1225541.7866
67 | 2612239.7766 | 1225433.779
68 | 2612219.1745 | 1225422.0747
69 | 2612211.8943 | 1225554.531
70 | 2612245.4214 | 1225433.2046
71 | 2612221.1747 | 1225401.1883
72 | 2612181.6008 | 1225439.4631
73 | 2612180.0108 | 1225439.6152
74 | 2612192.5818 | 1225549.0855
75 | 2612217.4994 | 1225558.5746
76 | 2612185.0749 | 1225545.4922
77 | 2612230.7029 | 1225568.0997
78 | 2612169.0493 | 1225537.1891
79 | 2612241.2647 | 1225583.1836
80 | 2612144.0138 | 1225397.6624
81 | 2612144.1292 | 1225396.7602
82 | 2612142.4286 | 1225410.0493
83 | 2612147.7353 | 1225368.5801
84 | 2612127.8463 | 1225413.0151
85 | 2612157.2038 | 1225418.6147
86 | 2612111.0155 | 1225425.3835
87 | 2612162.2752 | 1225435.9246
88 | 2612107.0601 | 1225433.8328
89 | 2612096.2428 | 1225409.8557
90 | 2612162.7711 | 1225441.2645
91 | 2612106.4297 | 1225436.5141
92 | 2612106.4853 | 1225442.7132
93 | 2612165.7922 | 1225476.4469
94 | 2612166.3793 | 1225483.0937
95 | 2612148.9927 | 1225477.9421
96 | 2612043.1613 | 1225430.708
97 | 2612097.3708 | 1225496.6978
98 | 2612099.9698 | 1225494.6657
99 | 2612081.9063 | 1225504.7601
100 | 2612109.3707 | 1225481.4687
101 | 2612126.1742 | 1225479.9731
102 | 2612108.6095 | 1225464.7067
103 | 2612060.4671 | 1225473.928
104 | 2612056.3748 | 1225468.0426
105 | 2612107.6437 | 1225539.6946
106 | 2612125.9874 | 1225551.9325
107 | 2612128.2174 | 1225479.7912
108 | 2612146.0502 | 1225543.9404
109 | 2612126.1118 | 1225565.6667
110 | 2612167.2897 | 1225493.4018
111 | 2612168.4816 | 1225506.8956
112 | 2612153.7848 | 1225540.8593
113 | 2612117.2675 | 1225587.0021
114 | 2612153.247 | 1225604.1256
115 | 2612169.4249 | 1225517.5764
116 | 2612096.1954 | 1225595.6536
117 | 2612090.3771 | 1225606.4383
118 | 2612184.7963 | 1225619.1407
119 | 2612063.7084 | 1225659.0846
120 | 2612087.4922 | 1225659.8125
121 | 2612059.0667 | 1225670.478
122 | 2612053.7649 | 1225683.486
123 | 2612021.7101 | 1225657.1093
124 | 2612107.7136 | 1225690.9472
125 | 2612203.4138 | 1225628.0013
126 | 2612187.7536 | 1225654.0958
127 | 2612225.5724 | 1225638.1562
128 | 2612181.6385 | 1225664.3004
129 | 2612152.6597 | 1225661.2044
130 | 2612245.0161 | 1225588.5413
131 | 2612247.3001 | 1225591.8031
132 | 2612198.6889 | 1225678.9364
133 | 2612221.5273 | 1225668.3624
134 | 2612221.6459 | 1225667.6618
135 | 2611969.65 | 1225604.5263
136 | 2612125.9874 | 1225551.9325

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99329 | -0.12855 | 0.0025756 | 0.00064552
1 | 0.99334 | -0.12756 | 0.0018793 | 0.000471
2 | 0.99339 | -0.12662 | 0 | 0
3 | 0.97798 | -0.42389 | 0 | 0
4 | 0.97741 | -0.43508 | 0.0020093 | 0.00050357
5 | 0.97844 | -0.41477 | 0 | 0
6 | 0.9935 | -0.12435 | 0.0040045 | 0.0010036
7 | 0.99331 | -0.12811 | 0.0029778 | 0.0007463
8 | 0.97727 | -0.43783 | 0.0053845 | 0.0013495
9 | 0.97727 | -0.43771 | 0 | 0
10 | 0.97943 | -0.39554 | 0.0055743 | 0.0013971
11 | 0.99364 | -0.12169 | 0.0010124 | 0.00025374
12 | 0.99327 | -0.12897 | 0.0022638 | 0.00056736
13 | 0.97654 | -0.45223 | 0 | 0
14 | 0.97701 | -0.44292 | 0.0033604 | 0.0008422
15 | 0.9771 | -0.44113 | 0.0017789 | 0.00044583
16 | 0.98062 | -0.37228 | 0.0026214 | 0.00065699
17 | 0.9937 | -0.12048 | 0 | 0
18 | 0.99326 | -0.12917 | 0.0019178 | 0.00048065
19 | 0.98682 | -0.25318 | 0.0015731 | 0.00039425
20 | 0.98685 | -0.25269 | 0.0017528 | 0.0004393
21 | 0.98697 | -0.25035 | 0.003264 | 0.00081803
22 | 0.98712 | -0.24734 | 0.0027576 | 0.00069112
23 | 0.98746 | -0.24088 | 0 | 0
24 | 0.99143 | -0.16454 | 0.0028965 | 0.00072592
25 | 0.99148 | -0.16343 | 0.0020717 | 0.00051921
26 | 0.97654 | -0.4521 | 0.00141 | 0.00035339
27 | 0.9765 | -0.45287 | 0.0019708 | 0.00049394
28 | 0.97659 | -0.45118 | 0.0026321 | 0.00065967
29 | 0.9767 | -0.44899 | 0 | 0
30 | 0.97668 | -0.44935 | 0.0017393 | 0.0004359
31 | 0.9761 | -0.4608 | 0.0097032 | 0.0024319
32 | 0.99097 | -0.17344 | 0 | 0
33 | 0.9912 | -0.16893 | 0 | 0
34 | 0.99083 | -0.17613 | 0.0020767 | 0.00052046
35 | 0.97607 | -0.46132 | 0.0044931 | 0.0011261
36 | 0.99082 | -0.17629 | 0.0076433 | 0.0019156
37 | 0.9911 | -0.17082 | 0.0036675 | 0.00091917
38 | 0.99164 | -0.16041 | 0.0023319 | 0.00058444
39 | 0.99081 | -0.17645 | 0.0044702 | 0.0011203
40 | 0.97605 | -0.46171 | 0.0083243 | 0.0020863
41 | 0.98085 | -0.36772 | 0 | 0
42 | 0.98267 | -0.33219 | 0 | 0
43 | 0.98361 | -0.31403 | 0.0031267 | 0.00078363
44 | 0.98249 | -0.33578 | 0.0069416 | 0.0017397
45 | 0.98213 | -0.34293 | 0.0052861 | 0.0013248
46 | 0.98222 | -0.34114 | 0 | 0
47 | 0.97709 | -0.44135 | 0.0051513 | 0.001291
48 | 0.97507 | -0.48117 | 0 | 0
49 | 0.9748 | -0.48647 | 0 | 0
50 | 0.97517 | -0.47921 | 0 | 0
51 | 0.97473 | -0.48784 | 0 | 0
52 | 0.97475 | -0.48748 | 0.0015188 | 0.00038065
53 | 0.97542 | -0.47411 | 0.0016289 | 0.00040825
54 | 0.97504 | -0.4817 | 0.0016453 | 0.00041236
55 | 0.97687 | -0.44563 | 0.002661 | 0.00066691
56 | 0.97638 | -0.45524 | 0.0041042 | 0.0010286
57 | 0.97591 | -0.46447 | 0.002071 | 0.00051905
58 | 0.97496 | -0.48326 | 0.0018996 | 0.00047608
59 | 0.97497 | -0.48313 | 0.0031257 | 0.00078338
60 | 0.97495 | -0.48348 | 0.0016597 | 0.00041596
61 | 0.98924 | -0.20629 | 0.0025998 | 0.00065156
62 | 0.99012 | -0.18914 | 0.0022772 | 0.00057073
63 | 0.98843 | -0.22187 | 0.0031881 | 0.00079902
64 | 0.99058 | -0.18014 | 0.002893 | 0.00072505
65 | 0.98801 | -0.23015 | 0 | 0
66 | 0.99138 | -0.16481 | 0.00178 | 0.0004461
67 | 0.98769 | -0.23629 | 0.0048199 | 0.001208
68 | 0.98787 | -0.23289 | 0.0021471 | 0.00053812
69 | 0.99216 | -0.14974 | 0 | 0
70 | 0.98762 | -0.23759 | 0.0034431 | 0.00086292
71 | 0.98769 | -0.2363 | 0.0090412 | 0.0022659
72 | 0.98559 | -0.27628 | 0.0025252 | 0.00063287
73 | 0.98559 | -0.27621 | 0.0035775 | 0.0008966
74 | 0.9932 | -0.1296 | 0.0019052 | 0.00047748
75 | 0.99207 | -0.15149 | 0.0027434 | 0.00068757
76 | 0.99364 | -0.12112 | 0.0024252 | 0.00060781
77 | 0.9919 | -0.15482 | 0.0017551 | 0.00043986
78 | 0.99464 | -0.10196 | 0 | 0
79 | 0.99173 | -0.15801 | 0.0041496 | 0.00104
80 | 0.98597 | -0.26876 | 0.0021112 | 0.00052912
81 | 0.98597 | -0.26887 | 0.0035991 | 0.00090202
82 | 0.98608 | -0.26671 | 0 | 0
83 | 0.98588 | -0.27063 | 0.0034416 | 0.00086254
84 | 0.98638 | -0.26081 | 0.0021067 | 0.000528
85 | 0.98587 | -0.27069 | 0.0034209 | 0.00085735
86 | 0.98684 | -0.25185 | 0 | 0
87 | 0.98572 | -0.27373 | 0.003121 | 0.00078221
88 | 0.98709 | -0.24702 | 0.0025643 | 0.00064267
89 | 0.98674 | -0.25369 | 0.0047946 | 0.0012016
90 | 0.98569 | -0.27431 | 0 | 0
91 | 0.98717 | -0.24548 | 0.002974 | 0.00074536
92 | 0.98736 | -0.24168 | 0.0011237 | 0.00028163
93 | 0.99163 | -0.15947 | 0 | 0
94 | 0.99194 | -0.15341 | 0.0027033 | 0.00067751
95 | 0.99083 | -0.1748 | 0.0034284 | 0.00085924
96 | 0.97462 | -0.49001 | 0.0056019 | 0.001404
97 | 0.98668 | -0.25454 | 0.0015087 | 0.00037812
98 | 0.987 | -0.24838 | 0.0029671 | 0.00074364
99 | 0.98502 | -0.2867 | 0 | 0
100 | 0.98864 | -0.21676 | 0 | 0
101 | 0.98977 | -0.19516 | 0.0034621 | 0.00086768
102 | 0.98808 | -0.22772 | 0.001126 | 0.0002822
103 | 0.98218 | -0.34179 | 0.0029648 | 0.00074305
104 | 0.9822 | -0.3414 | 0 | 0
105 | 1 | 0 | -0.3304 | -0.083994
106 | 0.9978 | -0.04174 | 0 | 0
107 | 0.98986 | -0.19337 | 0.0029887 | 0.00074904
108 | 0.99629 | -0.070377 | 0.0022544 | 0.00056501
109 | 0.99657 | -0.065368 | 0.0014415 | 0.00036126
110 | 0.99244 | -0.14386 | 0.0027572 | 0.00069103
111 | 0.99311 | -0.13115 | 0.0020288 | 0.00050847
112 | 0.99572 | -0.08133 | 0.001783 | 0.00044686
113 | 0.99452 | -0.10467 | 0 | 0
114 | 0.99328 | -0.12871 | 0.0030814 | 0.00077227
115 | 0.99364 | -0.12098 | 0.0014939 | 0.00037442
116 | 0.99301 | -0.13385 | 0.0019793 | 0.00049607
117 | 0.99252 | -0.14327 | 0.0016936 | 0.00042446
118 | 0.99228 | -0.14793 | 0.0040727 | 0.0010207
119 | 0.99067 | -0.17914 | 0.0022553 | 0.00056522
120 | 0.99106 | -0.17167 | 0.0024309 | 0.00060925
121 | 0.99048 | -0.18284 | 0 | 0
122 | 0.99036 | -0.18516 | 0 | 0
123 | 0.99019 | -0.18859 | 0.0076412 | 0.0019151
124 | 0.9899 | -0.19414 | 0.0092755 | 0.0023247
125 | 0.99177 | -0.1578 | 0.0019418 | 0.00048666
126 | 0.99131 | -0.16681 | 0 | 0
127 | 0.99159 | -0.16143 | 0.0034303 | 0.00085972
128 | 0.99116 | -0.16973 | 0 | 0
129 | 0.99121 | -0.16868 | 0.0028469 | 0.0007135
130 | 0.9917 | -0.15866 | 0.0021967 | 0.00055054
131 | 0.99168 | -0.1589 | 0.0034343 | 0.00086073
132 | 0.99085 | -0.17571 | 0.0025411 | 0.00063686
133 | 0.99051 | -0.18225 | 0.0081572 | 0.0020444
134 | 0.99051 | -0.18229 | 0.0031466 | 0.0007886
135 | 0.97603 | -0.46228 | 0.002434 | 0.00061002
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0025756 | -0.00064552 | 0.0025758 | 0.00064531 | 1.213e-07 | -2.0361e-07 | 0.0038585 | 0.0038584 | 0.0038585 | 0.99329 | -0.12855 | 0.99334 | -0.12756 | 1.06
1 | -0.0044551 | -0.0011163 | 0.0044553 | 0.0011163 | 1.9865e-07 | -2.6844e-08 | 0.0066736 | 0.0066736 | 0.0066736 | 0.99334 | -0.12756 | 0.99339 | -0.12662 | 1.8334
2 | -0.011615 | -0.0029107 | 0.011617 | 0.0029113 | 1.2567e-06 | 6.6093e-07 | 0.017399 | 0.017399 | 0.017399 | 0.99339 | -0.12662 | 0.9935 | -0.12435 | 4.7799
3 | 0.0071601 | 0.0017944 | -0.0071596 | -0.0017942 | 5.0769e-07 | 1.7256e-07 | 0.010725 | 0.010725 | 0.010725 | 0.99339 | -0.12662 | 0.99331 | -0.12811 | 2.9465
4 | 0.032398 | 0.0081376 | -0.03238 | -0.0081268 | 1.729e-05 | 1.0828e-05 | 0.0493 | 0.0493 | 0.0493 | 0.97798 | -0.42389 | 0.97741 | -0.43508 | 13.544
5 | -0.032398 | -0.0081376 | 0.032412 | 0.0081465 | 1.412e-05 | 8.8423e-06 | 0.0493 | 0.0493 | 0.0493 | 0.97798 | -0.42389 | 0.97844 | -0.41477 | 13.544
6 | 0.030371 | 0.0076232 | -0.030367 | -0.0076208 | 3.9792e-06 | 2.4845e-06 | 0.046241 | 0.046241 | 0.046241 | 0.97741 | -0.43508 | 0.97727 | -0.43783 | 12.7037
7 | 0.04406 | 0.011076 | -0.044012 | -0.011046 | 4.8213e-05 | 3.0497e-05 | 0.067018 | 0.067018 | 0.067018 | 0.97844 | -0.41477 | 0.97727 | -0.43771 | 18.4116
8 | -0.076471 | -0.019223 | 0.076542 | 0.019267 | 7.0255e-05 | 4.4789e-05 | 0.11632 | 0.11632 | 0.11632 | 0.97844 | -0.41477 | 0.97943 | -0.39554 | 31.9556
9 | -0.015621 | -0.0039149 | 0.015623 | 0.0039161 | 1.9802e-06 | 1.1424e-06 | 0.023396 | 0.023396 | 0.023396 | 0.9935 | -0.12435 | 0.99364 | -0.12169 | 6.4276
10 | 0.0041818 | 0.0010479 | -0.0041816 | -0.0010479 | 1.7137e-07 | -4.1052e-08 | 0.0062644 | 0.0062645 | 0.0062645 | 0.99331 | -0.12811 | 0.99327 | -0.12897 | 1.721
11 | 0.024983 | 0.0062713 | -0.024965 | -0.0062607 | 1.7147e-05 | 1.0578e-05 | 0.038043 | 0.038043 | 0.038043 | 0.97727 | -0.43783 | 0.97654 | -0.45223 | 10.4514
12 | 0.011119 | 0.0027872 | -0.011116 | -0.0027857 | 2.7581e-06 | 1.4437e-06 | 0.01693 | 0.01693 | 0.01693 | 0.97727 | -0.43771 | 0.97701 | -0.44292 | 4.651
13 | 0.032893 | 0.0082585 | -0.032888 | -0.0082551 | 5.3641e-06 | 3.3616e-06 | 0.050089 | 0.050089 | 0.050089 | 0.97727 | -0.43771 | 0.9771 | -0.44113 | 13.7607
14 | -0.082116 | -0.020664 | 0.082208 | 0.020723 | 9.1417e-05 | 5.8309e-05 | 0.12479 | 0.12479 | 0.12479 | 0.97943 | -0.39554 | 0.98062 | -0.37228 | 34.2822
15 | -0.016636 | -0.0041698 | 0.016636 | 0.0041704 | 9.601e-07 | 5.6103e-07 | 0.024913 | 0.024913 | 0.024913 | 0.99364 | -0.12169 | 0.9937 | -0.12048 | 6.8441
16 | 0.0019178 | 0.00048059 | -0.0019178 | -0.00048065 | 1.8148e-08 | -6.4266e-08 | 0.0028731 | 0.0028731 | 0.0028731 | 0.99327 | -0.12897 | 0.99326 | -0.12917 | 0.78932
17 | 0.024965 | 0.0062607 | -0.024955 | -0.0062544 | 1.0193e-05 | 6.2887e-06 | 0.038043 | 0.038043 | 0.038043 | 0.97654 | -0.45223 | 0.9761 | -0.4608 | 10.4514
18 | 0.0077554 | 0.0019435 | -0.0077531 | -0.0019426 | 2.2416e-06 | 8.9824e-07 | 0.011812 | 0.011812 | 0.011812 | 0.97701 | -0.44292 | 0.9767 | -0.44899 | 3.245
19 | 0.031109 | 0.0078093 | -0.031108 | -0.0078091 | 3.2679e-07 | 2.0428e-07 | 0.04738 | 0.04738 | 0.04738 | 0.9771 | -0.44113 | 0.97709 | -0.44135 | 13.0164
20 | -0.084829 | -0.02138 | 0.084847 | 0.021392 | 1.8492e-05 | 1.1797e-05 | 0.12876 | 0.12876 | 0.12876 | 0.98062 | -0.37228 | 0.98085 | -0.36772 | 35.375
21 | -0.062226 | -0.01564 | 0.062273 | 0.01567 | 4.7019e-05 | 2.9905e-05 | 0.093196 | 0.093196 | 0.093196 | 0.9937 | -0.12048 | 0.99452 | -0.10467 | 25.6032
22 | 0.045589 | 0.01147 | -0.04556 | -0.011452 | 2.9102e-05 | 1.841e-05 | 0.068283 | 0.068283 | 0.068283 | 0.9937 | -0.12048 | 0.99301 | -0.13385 | 18.7591
23 | -0.0015731 | -0.00039425 | 0.0015731 | 0.00039405 | 3.6624e-08 | -1.9833e-07 | 0.002372 | 0.002372 | 0.002372 | 0.98682 | -0.25318 | 0.98685 | -0.25269 | 0.65166
24 | -0.003326 | -0.00083336 | 0.0033263 | 0.00083309 | 3.7097e-07 | -2.6522e-07 | 0.005015 | 0.0050148 | 0.005015 | 0.98685 | -0.25269 | 0.98697 | -0.25035 | 1.3777
25 | -0.0065903 | -0.0016511 | 0.0065913 | 0.0016514 | 9.4635e-07 | 2.7892e-07 | 0.0099358 | 0.0099357 | 0.0099358 | 0.98697 | -0.25035 | 0.98712 | -0.24734 | 2.7296
26 | -0.0093489 | -0.0023425 | 0.0093518 | 0.0023439 | 2.876e-06 | 1.3468e-06 | 0.014093 | 0.014092 | 0.014093 | 0.98712 | -0.24734 | 0.98746 | -0.24088 | 3.8716
27 | -0.0093518 | -0.0023439 | 0.0093532 | 0.0023446 | 1.4658e-06 | 6.863e-07 | 0.014092 | 0.014092 | 0.014092 | 0.98746 | -0.24088 | 0.98762 | -0.23759 | 3.8715
28 | -0.0028965 | -0.00072592 | 0.0028966 | 0.00072574 | 1.5277e-07 | -1.8023e-07 | 0.0043473 | 0.0043472 | 0.0043473 | 0.99143 | -0.16454 | 0.99148 | -0.16343 | 1.1943
29 | -0.0049683 | -0.001245 | 0.0049688 | 0.001245 | 4.7288e-07 | 1.0091e-08 | 0.0074563 | 0.0074562 | 0.0074563 | 0.99148 | -0.16343 | 0.99159 | -0.16143 | 2.0484
30 | 0.0019709 | 0.00049372 | -0.0019708 | -0.00049394 | 7.233e-08 | -2.2126e-07 | 0.0030031 | 0.0030032 | 0.0030032 | 0.97654 | -0.4521 | 0.9765 | -0.45287 | 0.82505
31 | -0.0033809 | -0.0008471 | 0.0033811 | 0.00084701 | 1.4817e-07 | -9.1445e-08 | 0.0051516 | 0.0051516 | 0.0051516 | 0.97654 | -0.4521 | 0.97659 | -0.45118 | 1.4153
32 | -0.0060132 | -0.0015067 | 0.0060138 | 0.0015068 | 6.2928e-07 | 1.5258e-07 | 0.0091621 | 0.009162 | 0.0091621 | 0.97659 | -0.45118 | 0.9767 | -0.44899 | 2.5171
33 | 0.0017393 | 0.00043578 | -0.0017393 | -0.0004359 | 3.0087e-08 | -1.2375e-07 | 0.0026498 | 0.0026498 | 0.0026498 | 0.9767 | -0.44899 | 0.97668 | -0.44935 | 0.72798
34 | 0.015252 | 0.0038226 | -0.015252 | -0.0038223 | 3.7865e-07 | 2.1899e-07 | 0.023251 | 0.023251 | 0.023251 | 0.9761 | -0.4608 | 0.97607 | -0.46132 | 6.3876
35 | -0.0065477 | -0.001641 | 0.0065491 | 0.0016414 | 1.405e-06 | 3.9975e-07 | 0.009832 | 0.0098318 | 0.009832 | 0.99097 | -0.17344 | 0.9912 | -0.16893 | 2.7011
36 | 0.0065477 | 0.001641 | -0.0065469 | -0.0016408 | 8.3937e-07 | 2.3893e-07 | 0.009832 | 0.0098321 | 0.0098321 | 0.99097 | -0.17344 | 0.99083 | -0.17613 | 2.7011
37 | 0.026837 | 0.0067328 | -0.026828 | -0.006727 | 9.4024e-06 | 5.8185e-06 | 0.040291 | 0.040291 | 0.040291 | 0.9912 | -0.16893 | 0.99082 | -0.17629 | 11.0691
38 | 0.0060991 | 0.0015284 | -0.0060986 | -0.0015282 | 5.4822e-07 | 1.2612e-07 | 0.0091561 | 0.0091562 | 0.0091562 | 0.9912 | -0.16893 | 0.9911 | -0.17082 | 2.5154
39 | -0.039486 | -0.0099025 | 0.039502 | 0.0099127 | 1.6047e-05 | 1.0113e-05 | 0.059279 | 0.059279 | 0.059279 | 0.9912 | -0.16893 | 0.99164 | -0.16041 | 16.2855
40 | 0.0044702 | 0.0011203 | -0.0044702 | -0.0011203 | 6.8439e-08 | -8.3534e-09 | 0.0067134 | 0.0067134 | 0.0067134 | 0.99083 | -0.17613 | 0.99081 | -0.17645 | 1.8443
41 | 0.010759 | 0.0026963 | -0.010758 | -0.0026962 | 1.9945e-07 | 1.0294e-07 | 0.016401 | 0.016401 | 0.016401 | 0.97607 | -0.46132 | 0.97605 | -0.46171 | 4.5058
42 | 0.019185 | 0.0048114 | -0.019182 | -0.0048098 | 2.613e-06 | 1.5642e-06 | 0.028813 | 0.028813 | 0.028813 | 0.99082 | -0.17629 | 0.99067 | -0.17914 | 7.9156
43 | 0.002431 | 0.00060906 | -0.0024309 | -0.00060925 | 9.8359e-08 | -1.9077e-07 | 0.0036498 | 0.0036499 | 0.0036499 | 0.9911 | -0.17082 | 0.99106 | -0.17167 | 1.0027
44 | -0.041834 | -0.010497 | 0.041868 | 0.010519 | 3.4217e-05 | 2.16e-05 | 0.062778 | 0.062778 | 0.062778 | 0.99164 | -0.16041 | 0.99252 | -0.14327 | 17.2468
45 | 0.0024341 | 0.00060991 | -0.002434 | -0.00061002 | 6.5595e-08 | -1.1678e-07 | 0.0037108 | 0.0037108 | 0.0037108 | 0.97605 | -0.46171 | 0.97603 | -0.46228 | 1.0195
46 | -0.084847 | -0.021392 | 0.084992 | 0.021484 | 0.00014452 | 9.2201e-05 | 0.12876 | 0.12876 | 0.12876 | 0.98085 | -0.36772 | 0.98267 | -0.33219 | 35.375
47 | -0.10019 | -0.025294 | 0.10028 | 0.025349 | 8.7253e-05 | 5.5714e-05 | 0.15178 | 0.15178 | 0.15178 | 0.98267 | -0.33219 | 0.98361 | -0.31403 | 41.6973
48 | 0.015198 | 0.00381 | -0.015195 | -0.0038085 | 2.594e-06 | 1.4947e-06 | 0.023014 | 0.023014 | 0.023014 | 0.98267 | -0.33219 | 0.98249 | -0.33578 | 6.3224
49 | -0.1034 | -0.026133 | 0.10354 | 0.02622 | 0.00013569 | 8.6651e-05 | 0.15651 | 0.15651 | 0.15651 | 0.98361 | -0.31403 | 0.98502 | -0.2867 | 42.9968
50 | 0.0082536 | 0.0020687 | -0.0082515 | -0.0020678 | 2.1103e-06 | 8.9466e-07 | 0.0125 | 0.012501 | 0.012501 | 0.98249 | -0.33578 | 0.98222 | -0.34114 | 3.4342
51 | -0.0052861 | -0.0013248 | 0.0052865 | 0.0013249 | 4.4954e-07 | 5.1181e-08 | 0.0080089 | 0.0080089 | 0.0080089 | 0.98213 | -0.34293 | 0.98222 | -0.34114 | 2.2003
52 | 0.0029649 | 0.00074296 | -0.0029649 | -0.000743 | 3.655e-08 | -3.7752e-08 | 0.0044917 | 0.0044917 | 0.0044917 | 0.98222 | -0.34114 | 0.9822 | -0.3414 | 1.234
53 | 0.025957 | 0.0065181 | -0.025952 | -0.0065148 | 5.3e-06 | 3.2788e-06 | 0.039535 | 0.039535 | 0.039535 | 0.97709 | -0.44135 | 0.97687 | -0.44563 | 10.8612
54 | 0.0071235 | 0.001785 | -0.0071217 | -0.0017844 | 1.7954e-06 | 6.4387e-07 | 0.010871 | 0.010871 | 0.010871 | 0.97507 | -0.48117 | 0.9748 | -0.48647 | 2.9865
55 | -0.0071235 | -0.001785 | 0.0071242 | 0.0017853 | 6.6779e-07 | 2.394e-07 | 0.010871 | 0.010871 | 0.010871 | 0.97507 | -0.48117 | 0.97517 | -0.47921 | 2.9865
56 | 0.0056028 | 0.0014041 | -0.0056024 | -0.0014041 | 3.6721e-07 | 6.8139e-08 | 0.0085526 | 0.0085527 | 0.0085527 | 0.9748 | -0.48647 | 0.97473 | -0.48784 | 2.3496
57 | 0.0015189 | 0.00038024 | -0.0015188 | -0.00038065 | 7.3593e-08 | -4.0801e-07 | 0.0023184 | 0.0023186 | 0.0023186 | 0.9748 | -0.48647 | 0.97475 | -0.48748 | 0.63697
58 | -0.015456 | -0.0038735 | 0.01546 | 0.0038757 | 3.7566e-06 | 2.1795e-06 | 0.023584 | 0.023584 | 0.023584 | 0.97517 | -0.47921 | 0.97542 | -0.47411 | 6.4792
59 | 0.0083318 | 0.0020883 | -0.0083308 | -0.0020878 | 9.8923e-07 | 4.2953e-07 | 0.012714 | 0.012714 | 0.012714 | 0.97517 | -0.47921 | 0.97504 | -0.4817 | 3.4928
60 | 0.0056024 | 0.0014041 | -0.0056019 | -0.001404 | 5.7977e-07 | 1.0763e-07 | 0.0085527 | 0.0085528 | 0.0085528 | 0.97473 | -0.48784 | 0.97462 | -0.49001 | 2.3497
61 | -0.017089 | -0.0042839 | 0.017096 | 0.0042886 | 7.8482e-06 | 4.6382e-06 | 0.026069 | 0.026069 | 0.026069 | 0.97542 | -0.47411 | 0.97591 | -0.46447 | 7.1619
62 | 0.0066855 | 0.0016755 | -0.006685 | -0.0016753 | 4.5426e-07 | 1.4559e-07 | 0.010203 | 0.010203 | 0.010203 | 0.97504 | -0.4817 | 0.97497 | -0.48313 | 2.803
63 | 0.023291 | 0.0058479 | -0.02328 | -0.0058413 | 1.0671e-05 | 6.5463e-06 | 0.035481 | 0.035482 | 0.035482 | 0.97687 | -0.44563 | 0.97638 | -0.45524 | 9.7477
64 | 0.019176 | 0.0048127 | -0.019168 | -0.0048076 | 8.4413e-06 | 5.073e-06 | 0.029227 | 0.029227 | 0.029227 | 0.97638 | -0.45524 | 0.97591 | -0.46447 | 8.0294
65 | -0.0035593 | -0.00089195 | 0.0035593 | 0.00089194 | 2.2545e-08 | -1.0978e-08 | 0.0054322 | 0.0054322 | 0.0054322 | 0.97496 | -0.48326 | 0.97497 | -0.48313 | 1.4924
66 | 0.0016597 | 0.00041588 | -0.0016597 | -0.00041596 | 1.7439e-08 | -7.9219e-08 | 0.0025331 | 0.0025331 | 0.0025331 | 0.97496 | -0.48326 | 0.97495 | -0.48348 | 0.69591
67 | -0.034636 | -0.008697 | 0.034665 | 0.0087148 | 2.8365e-05 | 1.7796e-05 | 0.052106 | 0.052106 | 0.052106 | 0.98924 | -0.20629 | 0.99012 | -0.18914 | 14.3149
68 | 0.032037 | 0.0080454 | -0.032013 | -0.0080305 | 2.3799e-05 | 1.4881e-05 | 0.048196 | 0.048196 | 0.048196 | 0.98924 | -0.20629 | 0.98843 | -0.22187 | 13.2406
69 | -0.036942 | -0.0092855 | 0.036958 | 0.0092955 | 1.588e-05 | 9.9862e-06 | 0.055528 | 0.055528 | 0.055528 | 0.99012 | -0.18914 | 0.99058 | -0.18014 | 15.2551
70 | 0.028825 | 0.0072315 | -0.028813 | -0.0072244 | 1.1371e-05 | 7.0711e-06 | 0.043396 | 0.043396 | 0.043396 | 0.98843 | -0.22187 | 0.98801 | -0.23015 | 11.9221
71 | -0.039851 | -0.010021 | 0.03988 | 0.010039 | 2.9199e-05 | 1.8407e-05 | 0.059874 | 0.059874 | 0.059874 | 0.99058 | -0.18014 | 0.99138 | -0.16481 | 16.4489
72 | 0.017622 | 0.004419 | -0.017617 | -0.0044159 | 5.1593e-06 | 3.0519e-06 | 0.026541 | 0.026541 | 0.026541 | 0.98801 | -0.23015 | 0.98769 | -0.23629 | 7.2916
73 | 0.011191 | 0.0028055 | -0.01119 | -0.0028047 | 1.4629e-06 | 7.6044e-07 | 0.016855 | 0.016855 | 0.016855 | 0.98801 | -0.23015 | 0.98787 | -0.23289 | 4.6305
74 | -0.04166 | -0.010485 | 0.04169 | 0.010504 | 3.002e-05 | 1.8949e-05 | 0.062546 | 0.062546 | 0.062546 | 0.99138 | -0.16481 | 0.99216 | -0.14974 | 17.1829
75 | 0.012797 | 0.0032079 | -0.012796 | -0.0032075 | 7.909e-07 | 4.3356e-07 | 0.01928 | 0.01928 | 0.01928 | 0.98769 | -0.23629 | 0.98762 | -0.23759 | 5.2967
76 | 0.0090426 | 0.0022666 | -0.0090412 | -0.0022659 | 1.4699e-06 | 6.7028e-07 | 0.013621 | 0.013621 | 0.013621 | 0.98787 | -0.23289 | 0.98769 | -0.2363 | 3.7421
77 | -0.055974 | -0.014085 | 0.056028 | 0.014119 | 5.3921e-05 | 3.4246e-05 | 0.083969 | 0.083969 | 0.083969 | 0.99216 | -0.14974 | 0.9932 | -0.1296 | 23.0683
78 | 0.014284 | 0.003581 | -0.014283 | -0.0035804 | 1.1895e-06 | 6.7203e-07 | 0.021423 | 0.021423 | 0.021423 | 0.99216 | -0.14974 | 0.99207 | -0.15149 | 5.8855
79 | -0.0025252 | -0.00063287 | 0.0025252 | 0.00063285 | 8.7056e-09 | -1.4783e-08 | 0.0038124 | 0.0038124 | 0.0038124 | 0.98559 | -0.27628 | 0.98559 | -0.27621 | 1.0474
80 | -0.0061027 | -0.0015295 | 0.0061032 | 0.0015296 | 5.5132e-07 | 1.3212e-07 | 0.0092137 | 0.0092136 | 0.0092137 | 0.98559 | -0.27621 | 0.98569 | -0.27431 | 2.5312
81 | -0.057933 | -0.014597 | 0.057957 | 0.014612 | 2.3527e-05 | 1.4949e-05 | 0.086823 | 0.086823 | 0.086823 | 0.9932 | -0.1296 | 0.99364 | -0.12112 | 23.8524
82 | 0.011539 | 0.0028928 | -0.011537 | -0.0028918 | 1.829e-06 | 9.6036e-07 | 0.017308 | 0.017308 | 0.017308 | 0.99207 | -0.15149 | 0.9919 | -0.15482 | 4.755
83 | -0.060382 | -0.01522 | 0.060437 | 0.015255 | 5.5416e-05 | 3.5232e-05 | 0.090455 | 0.090455 | 0.090455 | 0.99364 | -0.12112 | 0.99464 | -0.10196 | 24.8502
84 | 0.0097823 | 0.002452 | -0.0097809 | -0.0024513 | 1.4872e-06 | 7.1415e-07 | 0.014675 | 0.014675 | 0.014675 | 0.9919 | -0.15482 | 0.99173 | -0.15801 | 4.0317
85 | -0.2251 | -0.057291 | 0.22532 | 0.057434 | 0.00022408 | 0.0001428 | 0.33707 | 0.33707 | 0.33707 | 0.99464 | -0.10196 | 0.99572 | -0.08133 | 30.867
86 | 0.16466 | 0.042036 | -0.16451 | -0.04194 | 0.00015119 | 9.5989e-05 | 0.24661 | 0.24661 | 0.24661 | 0.99464 | -0.10196 | 0.99364 | -0.12098 | 22.5837
87 | 0.0056312 | 0.0014113 | -0.0056311 | -0.0014112 | 1.7509e-07 | 2.7671e-08 | 0.0084492 | 0.0084493 | 0.0084493 | 0.99173 | -0.15801 | 0.9917 | -0.15866 | 2.3212
88 | 0.007041 | 0.0017644 | -0.007041 | -0.0017644 | 3.8513e-08 | 1.3048e-08 | 0.010626 | 0.010626 | 0.010626 | 0.98597 | -0.26876 | 0.98597 | -0.26887 | 2.9193
89 | -0.0091522 | -0.0022935 | 0.0091531 | 0.0022939 | 8.9342e-07 | 4.125e-07 | 0.013812 | 0.013812 | 0.013812 | 0.98597 | -0.26876 | 0.98608 | -0.26671 | 3.7946
90 | 0.0034419 | 0.00086236 | -0.0034416 | -0.00086254 | 2.8746e-07 | -1.7832e-07 | 0.0051944 | 0.0051945 | 0.0051945 | 0.98597 | -0.26887 | 0.98588 | -0.27063 | 1.4271
91 | -0.021802 | -0.005465 | 0.021808 | 0.0054688 | 6.1291e-06 | 3.73e-06 | 0.0329 | 0.0329 | 0.0329 | 0.98608 | -0.26671 | 0.98638 | -0.26081 | 9.0386
92 | 0.012649 | 0.0031711 | -0.012647 | -0.0031698 | 2.4001e-06 | 1.312e-06 | 0.019088 | 0.019088 | 0.019088 | 0.98608 | -0.26671 | 0.98587 | -0.27069 | 5.244
93 | -0.023915 | -0.0059968 | 0.023925 | 0.006003 | 1.0218e-05 | 6.2724e-06 | 0.036078 | 0.036078 | 0.036078 | 0.98638 | -0.26081 | 0.98684 | -0.25185 | 9.9117
94 | 0.0092258 | 0.0023125 | -0.0092244 | -0.0023118 | 1.3335e-06 | 6.1962e-07 | 0.013925 | 0.013925 | 0.013925 | 0.98587 | -0.27069 | 0.98572 | -0.27373 | 3.8256
95 | -0.02872 | -0.0072047 | 0.028727 | 0.0072088 | 6.6182e-06 | 4.1154e-06 | 0.043309 | 0.043308 | 0.043309 | 0.98684 | -0.25185 | 0.98709 | -0.24702 | 11.8979
96 | 0.004795 | 0.0012016 | -0.0047946 | -0.0012016 | 4.196e-07 | -4.8955e-09 | 0.0072302 | 0.0072303 | 0.0072303 | 0.98684 | -0.25185 | 0.98674 | -0.25369 | 1.9863
97 | 0.0061034 | 0.0015296 | -0.0061032 | -0.0015296 | 1.7072e-07 | 4.0901e-08 | 0.0092135 | 0.0092136 | 0.0092136 | 0.98572 | -0.27373 | 0.98569 | -0.27431 | 2.5312
98 | -0.031291 | -0.0078515 | 0.031293 | 0.0078529 | 2.2987e-06 | 1.4359e-06 | 0.047174 | 0.047174 | 0.047174 | 0.98709 | -0.24702 | 0.98717 | -0.24548 | 12.9599
99 | -0.034267 | -0.0085983 | 0.034274 | 0.0086021 | 6.205e-06 | 3.8919e-06 | 0.051657 | 0.051657 | 0.051657 | 0.98717 | -0.24548 | 0.98736 | -0.24168 | 14.1915
100 | -0.035397 | -0.0088838 | 0.035421 | 0.0088986 | 2.3584e-05 | 1.4811e-05 | 0.05335 | 0.05335 | 0.05335 | 0.98736 | -0.24168 | 0.98808 | -0.22772 | 14.6567
101 | -0.15523 | -0.039501 | 0.15528 | 0.039529 | 4.534e-05 | 2.8759e-05 | 0.23315 | 0.23315 | 0.23315 | 0.99163 | -0.15947 | 0.99194 | -0.15341 | 21.3506
102 | 0.15523 | 0.039501 | -0.15512 | -0.039428 | 0.0001146 | 7.2692e-05 | 0.23315 | 0.23315 | 0.23315 | 0.99163 | -0.15947 | 0.99083 | -0.1748 | 21.3506
103 | -0.15798 | -0.040207 | 0.15805 | 0.040253 | 7.2781e-05 | 4.6179e-05 | 0.2372 | 0.2372 | 0.2372 | 0.99194 | -0.15341 | 0.99244 | -0.14386 | 21.7219
104 | 0.15169 | 0.038569 | -0.15155 | -0.038483 | 0.00013553 | 8.5935e-05 | 0.228 | 0.228 | 0.228 | 0.99083 | -0.1748 | 0.98986 | -0.19337 | 20.8791
105 | -0.10521 | -0.0267 | 0.10524 | 0.02672 | 3.1191e-05 | 1.992e-05 | 0.15878 | 0.15878 | 0.15878 | 0.98668 | -0.25454 | 0.987 | -0.24838 | 43.6218
106 | 0.1037 | 0.026322 | -0.10354 | -0.02622 | 0.0001602 | 0.0001023 | 0.15651 | 0.15651 | 0.15651 | 0.98668 | -0.25454 | 0.98502 | -0.2867 | 42.9968
107 | -0.10821 | -0.027464 | 0.10837 | 0.027569 | 0.00016483 | 0.00010528 | 0.16326 | 0.16326 | 0.16326 | 0.987 | -0.24838 | 0.98864 | -0.21676 | 44.8508
108 | -0.14494 | -0.036762 | 0.14509 | 0.036858 | 0.00015074 | 9.6041e-05 | 0.2183 | 0.2183 | 0.2183 | 0.98864 | -0.21676 | 0.98977 | -0.19516 | 29.9866
109 | 0.036566 | 0.0091928 | -0.036547 | -0.0091808 | 1.9117e-05 | 1.2019e-05 | 0.055046 | 0.055046 | 0.055046 | 0.98864 | -0.21676 | 0.98808 | -0.22772 | 15.1225
110 | -0.14855 | -0.037725 | 0.14856 | 0.037734 | 1.2809e-05 | 8.1187e-06 | 0.22351 | 0.22351 | 0.22351 | 0.98977 | -0.19516 | 0.98986 | -0.19337 | 20.4677
111 | -0.0029648 | -0.00074305 | 0.0029649 | 0.000743 | 5.4234e-08 | -5.6014e-08 | 0.0044917 | 0.0044917 | 0.0044917 | 0.98218 | -0.34179 | 0.9822 | -0.3414 | 1.234
112 | 0.32875 | 0.083994 | -0.32809 | -0.083571 | 0.00066207 | 0.00042286 | 0.48976 | 0.48976 | 0.48976 | 1 | 0 | 0.9978 | -0.04174 | 44.8496
113 | 0.2298 | 0.058725 | -0.22948 | -0.058522 | 0.00031778 | 0.00020253 | 0.3431 | 0.3431 | 0.3431 | 0.9978 | -0.04174 | 0.99629 | -0.070377 | 31.4193
114 | 0.098293 | 0.024846 | -0.098182 | -0.024775 | 0.00011123 | 7.1008e-05 | 0.14666 | 0.14666 | 0.14666 | 0.9978 | -0.04174 | 0.99657 | -0.065368 | 40.2909
115 | 0.22723 | 0.057957 | -0.22711 | -0.057881 | 0.00012012 | 7.655e-05 | 0.33973 | 0.33973 | 0.33973 | 0.99629 | -0.070377 | 0.99572 | -0.08133 | 31.111
116 | 0.09674 | 0.024414 | -0.096559 | -0.024298 | 0.0001817 | 0.00011599 | 0.14451 | 0.14451 | 0.14451 | 0.99657 | -0.065368 | 0.99452 | -0.10467 | 39.6996
117 | -0.16081 | -0.040944 | 0.16091 | 0.041007 | 9.8623e-05 | 6.2593e-05 | 0.24134 | 0.24134 | 0.24134 | 0.99244 | -0.14386 | 0.99311 | -0.13115 | 22.1005
118 | -0.16294 | -0.041515 | 0.16302 | 0.041566 | 8.0043e-05 | 5.0811e-05 | 0.24438 | 0.24438 | 0.24438 | 0.99311 | -0.13115 | 0.99364 | -0.12098 | 22.3788
119 | 0.034286 | 0.0086277 | -0.034246 | -0.008603 | 3.9341e-05 | 2.4662e-05 | 0.051311 | 0.051311 | 0.051311 | 0.99452 | -0.10467 | 0.99328 | -0.12871 | 14.0965
120 | 0.031165 | 0.0078308 | -0.031136 | -0.0078129 | 2.8569e-05 | 1.7832e-05 | 0.046695 | 0.046695 | 0.046695 | 0.99328 | -0.12871 | 0.99228 | -0.14793 | 12.8283
121 | 0.043581 | 0.010956 | -0.043561 | -0.010943 | 1.9605e-05 | 1.2389e-05 | 0.065317 | 0.065317 | 0.065317 | 0.99301 | -0.13385 | 0.99252 | -0.14327 | 17.9443
122 | 0.027064 | 0.0067922 | -0.027051 | -0.0067843 | 1.2737e-05 | 7.8857e-06 | 0.040588 | 0.040588 | 0.040588 | 0.99228 | -0.14793 | 0.99177 | -0.1578 | 11.1505
123 | 0.016927 | 0.0042446 | -0.016924 | -0.0042428 | 2.9824e-06 | 1.7503e-06 | 0.025425 | 0.025425 | 0.025425 | 0.99067 | -0.17914 | 0.99048 | -0.18284 | 6.985
124 | 0.0092805 | 0.002327 | -0.0092795 | -0.0023265 | 1.0237e-06 | 4.7446e-07 | 0.013943 | 0.013943 | 0.013943 | 0.99048 | -0.18284 | 0.99036 | -0.18516 | 3.8304
125 | 0.0076433 | 0.0019159 | -0.0076412 | -0.0019151 | 2.0921e-06 | 7.9453e-07 | 0.011483 | 0.011483 | 0.011483 | 0.99048 | -0.18284 | 0.99019 | -0.18859 | 3.1546
126 | 0.0092795 | 0.0023265 | -0.0092755 | -0.0023247 | 3.9703e-06 | 1.8405e-06 | 0.013943 | 0.013943 | 0.013943 | 0.99036 | -0.18516 | 0.9899 | -0.19414 | 3.8305
127 | 0.016709 | 0.0041924 | -0.016702 | -0.0041882 | 7.1685e-06 | 4.1955e-06 | 0.025071 | 0.025071 | 0.025071 | 0.99177 | -0.1578 | 0.99131 | -0.16681 | 6.8876
128 | 0.0084005 | 0.0021053 | -0.0083991 | -0.0021047 | 1.452e-06 | 6.1482e-07 | 0.012604 | 0.012604 | 0.012604 | 0.99177 | -0.1578 | 0.99159 | -0.16143 | 3.4626
129 | 0.013854 | 0.003475 | -0.013852 | -0.0034739 | 1.9284e-06 | 1.0809e-06 | 0.020797 | 0.020797 | 0.020797 | 0.99131 | -0.16681 | 0.99116 | -0.16973 | 5.7135
130 | 0.0028472 | 0.00071319 | -0.0028469 | -0.0007135 | 2.5446e-07 | -3.1607e-07 | 0.0042736 | 0.0042738 | 0.0042738 | 0.99131 | -0.16681 | 0.99121 | -0.16868 | 1.1741
131 | 0.013852 | 0.0034739 | -0.013848 | -0.0034717 | 3.9518e-06 | 2.2153e-06 | 0.020797 | 0.020797 | 0.020797 | 0.99116 | -0.16973 | 0.99085 | -0.17571 | 5.7136
132 | 0.0034344 | 0.0008607 | -0.0034343 | -0.00086073 | 3.9653e-08 | -2.5997e-08 | 0.0051532 | 0.0051532 | 0.0051532 | 0.9917 | -0.15866 | 0.99168 | -0.1589 | 1.4157
133 | 0.011307 | 0.0028348 | -0.011304 | -0.002833 | 3.5219e-06 | 1.8346e-06 | 0.016981 | 0.016981 | 0.016981 | 0.99085 | -0.17571 | 0.99051 | -0.18225 | 4.6652
134 | 0.0031466 | 0.0007886 | -0.0031466 | -0.0007886 | 5.9539e-09 | -5.3353e-09 | 0.004727 | 0.004727 | 0.004727 | 0.99051 | -0.18225 | 0.99051 | -0.18229 | 1.2986

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33191 | 0.084371

## res_load
| p_mw | q_mvar
0 | 0.0025756 | 0.00064552
1 | 0.0018793 | 0.000471
2 | 0.0020093 | 0.00050357
3 | 0.0040045 | 0.0010036
4 | 0.0029778 | 0.0007463
5 | 0.0053845 | 0.0013495
6 | 0.0055743 | 0.0013971
7 | 0.0010124 | 0.00025374
8 | 0.0022638 | 0.00056736
9 | 0.0033604 | 0.0008422
10 | 0.0017789 | 0.00044583
11 | 0.0026214 | 0.00065699
12 | 0.0019178 | 0.00048065
13 | 0.0015731 | 0.00039425
14 | 0.0017528 | 0.0004393
15 | 0.003264 | 0.00081803
16 | 0.0027576 | 0.00069112
17 | 0.0028965 | 0.00072592
18 | 0.0020717 | 0.00051921
19 | 0.00141 | 0.00035339
20 | 0.0019708 | 0.00049394
21 | 0.0026321 | 0.00065967
22 | 0.0017393 | 0.0004359
23 | 0.0097032 | 0.0024319
24 | 0.0020767 | 0.00052046
25 | 0.0044931 | 0.0011261
26 | 0.0076433 | 0.0019156
27 | 0.0036675 | 0.00091917
28 | 0.0023319 | 0.00058444
29 | 0.0044702 | 0.0011203
30 | 0.0083243 | 0.0020863
31 | 0.0031267 | 0.00078363
32 | 0.0069416 | 0.0017397
33 | 0.0052861 | 0.0013248
34 | 0.0051513 | 0.001291
35 | 0.0015188 | 0.00038065
36 | 0.0016289 | 0.00040825
37 | 0.0016453 | 0.00041236
38 | 0.002661 | 0.00066691
39 | 0.0041042 | 0.0010286
40 | 0.002071 | 0.00051905
41 | 0.0018996 | 0.00047608
42 | 0.0031257 | 0.00078338
43 | 0.0016597 | 0.00041596
44 | 0.0025998 | 0.00065156
45 | 0.0022772 | 0.00057073
46 | 0.0031881 | 0.00079902
47 | 0.002893 | 0.00072505
48 | 0.00178 | 0.0004461
49 | 0.0048199 | 0.001208
50 | 0.0021471 | 0.00053812
51 | 0.0034431 | 0.00086292
52 | 0.0090412 | 0.0022659
53 | 0.0025252 | 0.00063287
54 | 0.0035775 | 0.0008966
55 | 0.0019052 | 0.00047748
56 | 0.0027434 | 0.00068757
57 | 0.0024252 | 0.00060781
58 | 0.0017551 | 0.00043986
59 | 0.0041496 | 0.00104
60 | 0.0021112 | 0.00052912
61 | 0.0035991 | 0.00090202
62 | 0.0034416 | 0.00086254
63 | 0.0021067 | 0.000528
64 | 0.0034209 | 0.00085735
65 | 0.003121 | 0.00078221
66 | 0.0025643 | 0.00064267
67 | 0.0047946 | 0.0012016
68 | 0.002974 | 0.00074536
69 | 0.0011237 | 0.00028163
70 | 0.0027033 | 0.00067751
71 | 0.0034284 | 0.00085924
72 | 0.0056019 | 0.001404
73 | 0.0015087 | 0.00037812
74 | 0.0029671 | 0.00074364
75 | 0.0034621 | 0.00086768
76 | 0.001126 | 0.0002822
77 | 0.0029648 | 0.00074305
78 | 0.0015036 | 0.00037685
79 | 0.0029887 | 0.00074904
80 | 0.0022544 | 0.00056501
81 | 0.0014415 | 0.00036126
82 | 0.0027572 | 0.00069103
83 | 0.0020288 | 0.00050847
84 | 0.001783 | 0.00044686
85 | 0.0030814 | 0.00077227
86 | 0.0014939 | 0.00037442
87 | 0.0019793 | 0.00049607
88 | 0.0016936 | 0.00042446
89 | 0.0040727 | 0.0010207
90 | 0.0022553 | 0.00056522
91 | 0.0024309 | 0.00060925
92 | 0.0076412 | 0.0019151
93 | 0.0092755 | 0.0023247
94 | 0.0019418 | 0.00048666
95 | 0.0034303 | 0.00085972
96 | 0.0028469 | 0.0007135
97 | 0.0021967 | 0.00055054
98 | 0.0034343 | 0.00086073
99 | 0.0025411 | 0.00063686
100 | 0.0081572 | 0.0020444
101 | 0.0031466 | 0.0007886
102 | 0.002434 | 0.00061002

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1