## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2525-3_1_3_node_21 | 0.4 | n |  | TRUE
1 | bus_LV_2525-3_1_3_node_22 | 0.4 | n |  | TRUE
2 | bus_LV_2525-3_1_3_node_23 | 0.4 | n |  | TRUE
3 | bus_LV_2525-3_1_3_node_24 | 0.4 | n |  | TRUE
4 | bus_LV_2525-3_1_3_node_25 | 0.4 | n |  | TRUE
5 | bus_LV_2525-3_1_3_node_98 | 0.4 | n |  | TRUE
6 | bus_LV_2525-3_1_3_node_41 | 0.4 | n |  | TRUE
7 | bus_LV_2525-3_1_3_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_2525-3_1_3_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_2525-3_1_3_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_2525-3_1_3_node_46 | 0.4 | n |  | TRUE
11 | bus_LV_2525-3_1_3_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_2525-3_1_3_node_49 | 0.4 | n |  | TRUE
13 | bus_LV_2525-3_1_3_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_2525-3_1_3_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_2525-3_1_3_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_2525-3_1_3_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_2525-3_1_3_node_39 | 0.4 | n |  | TRUE
18 | bus_LV_2525-3_1_3_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_2525-3_1_3_node_134 | 0.4 | n |  | TRUE
20 | bus_LV_2525-3_1_3_node_205 | 0.4 | n |  | TRUE
21 | bus_LV_2525-3_1_3_node_42 | 0.4 | n |  | TRUE
22 | bus_LV_2525-3_1_3_node_71 | 0.4 | n |  | TRUE
23 | bus_LV_2525-3_1_3_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_2525-3_1_3_node_44 | 0.4 | n |  | TRUE
25 | bus_LV_2525-3_1_3_node_45 | 0.4 | n |  | TRUE
26 | bus_LV_2525-3_1_3_node_54 | 0.4 | n |  | TRUE
27 | bus_LV_2525-3_1_3_node_50 | 0.4 | n |  | TRUE
28 | bus_LV_2525-3_1_3_node_47 | 0.4 | n |  | TRUE
29 | bus_LV_2525-3_1_3_node_48 | 0.4 | n |  | TRUE
30 | bus_LV_2525-3_1_3_node_56 | 0.4 | n |  | TRUE
31 | bus_LV_2525-3_1_3_node_61 | 0.4 | n |  | TRUE
32 | bus_LV_2525-3_1_3_node_51 | 0.4 | n |  | TRUE
33 | bus_LV_2525-3_1_3_node_52 | 0.4 | n |  | TRUE
34 | bus_LV_2525-3_1_3_node_53 | 0.4 | n |  | TRUE
35 | bus_LV_2525-3_1_3_node_55 | 0.4 | n |  | TRUE
36 | bus_LV_2525-3_1_3_node_62 | 0.4 | n |  | TRUE
37 | bus_LV_2525-3_1_3_node_57 | 0.4 | n |  | TRUE
38 | bus_LV_2525-3_1_3_node_58 | 0.4 | n |  | TRUE
39 | bus_LV_2525-3_1_3_node_59 | 0.4 | n |  | TRUE
40 | bus_LV_2525-3_1_3_node_65 | 0.4 | n |  | TRUE
41 | bus_LV_2525-3_1_3_node_63 | 0.4 | n |  | TRUE
42 | bus_LV_2525-3_1_3_node_60 | 0.4 | n |  | TRUE
43 | bus_LV_2525-3_1_3_node_64 | 0.4 | n |  | TRUE
44 | bus_LV_2525-3_1_3_node_66 | 0.4 | n |  | TRUE
45 | bus_LV_2525-3_1_3_node_67 | 0.4 | n |  | TRUE
46 | bus_LV_2525-3_1_3_node_68 | 0.4 | n |  | TRUE
47 | bus_LV_2525-3_1_3_node_69 | 0.4 | n |  | TRUE
48 | bus_LV_2525-3_1_3_node_70 | 0.4 | n |  | TRUE
49 | bus_LV_2525-3_1_3_node_79 | 0.4 | n |  | TRUE
50 | bus_LV_2525-3_1_3_node_76 | 0.4 | n |  | TRUE
51 | bus_LV_2525-3_1_3_node_75 | 0.4 | n |  | TRUE
52 | bus_LV_2525-3_1_3_node_72 | 0.4 | n |  | TRUE
53 | bus_LV_2525-3_1_3_node_73 | 0.4 | n |  | TRUE
54 | bus_LV_2525-3_1_3_node_74 | 0.4 | n |  | TRUE
55 | bus_LV_2525-3_1_3_node_77 | 0.4 | n |  | TRUE
56 | bus_LV_2525-3_1_3_node_124 | 0.4 | n |  | TRUE
57 | bus_LV_2525-3_1_3_node_93 | 0.4 | n |  | TRUE
58 | bus_LV_2525-3_1_3_node_94 | 0.4 | n |  | TRUE
59 | bus_LV_2525-3_1_3_node_95 | 0.4 | n |  | TRUE
60 | bus_LV_2525-3_1_3_node_232 | 0.4 | n |  | TRUE
61 | bus_LV_2525-3_1_3_node_96 | 0.4 | n |  | TRUE
62 | bus_LV_2525-3_1_3_node_97 | 0.4 | n |  | TRUE
63 | bus_LV_2525-3_1_3_node_209 | 0.4 | n |  | TRUE
64 | bus_LV_2525-3_1_3_node_215 | 0.4 | n |  | TRUE
65 | bus_LV_2525-3_1_3_node_228 | 0.4 | n |  | TRUE
66 | bus_LV_2525-3_1_3_node_114 | 0.4 | n |  | TRUE
67 | bus_LV_2525-3_1_3_node_122 | 0.4 | n |  | TRUE
68 | bus_LV_2525-3_1_3_node_123 | 0.4 | n |  | TRUE
69 | bus_LV_2525-3_1_3_node_135 | 0.4 | n |  | TRUE
70 | bus_LV_2525-3_1_3_node_125 | 0.4 | n |  | TRUE
71 | bus_LV_2525-3_1_3_node_126 | 0.4 | n |  | TRUE
72 | bus_LV_2525-3_1_3_node_127 | 0.4 | n |  | TRUE
73 | bus_LV_2525-3_1_3_node_128 | 0.4 | n |  | TRUE
74 | bus_LV_2525-3_1_3_node_129 | 0.4 | n |  | TRUE
75 | bus_LV_2525-3_1_3_node_130 | 0.4 | n |  | TRUE
76 | bus_LV_2525-3_1_3_node_131 | 0.4 | n |  | TRUE
77 | bus_LV_2525-3_1_3_node_132 | 0.4 | n |  | TRUE
78 | bus_LV_2525-3_1_3_node_133 | 0.4 | n |  | TRUE
79 | bus_LV_2525-3_1_3_node_206 | 0.4 | n |  | TRUE
80 | bus_LV_2525-3_1_3_node_219 | 0.4 | n |  | TRUE
81 | bus_LV_2525-3_1_3_node_211 | 0.4 | n |  | TRUE
82 | bus_LV_2525-3_1_3_node_207 | 0.4 | n |  | TRUE
83 | bus_LV_2525-3_1_3_node_208 | 0.4 | n |  | TRUE
84 | bus_LV_2525-3_1_3_node_210 | 0.4 | n |  | TRUE
85 | bus_LV_2525-3_1_3_node_212 | 0.4 | n |  | TRUE
86 | bus_LV_2525-3_1_3_node_213 | 0.4 | n |  | TRUE
87 | bus_LV_2525-3_1_3_node_214 | 0.4 | n |  | TRUE
88 | bus_LV_2525-3_1_3_node_216 | 0.4 | n |  | TRUE
89 | bus_LV_2525-3_1_3_node_217 | 0.4 | n |  | TRUE
90 | bus_LV_2525-3_1_3_node_218 | 0.4 | n |  | TRUE
91 | bus_LV_2525-3_1_3_node_229 | 0.4 | n |  | TRUE
92 | bus_MV_392_1_node_44 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2525-3_1_3_load_21 | 0 | 0.0080157 | 0.0020089 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2525-3_1_3_load_22 | 1 | 0.0045449 | 0.0011391 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2525-3_1_3_load_23 | 2 | 0.0030195 | 0.00075676 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2525-3_1_3_load_24 | 3 | 0.010634 | 0.0026652 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2525-3_1_3_load_25 | 4 | 0.0018538 | 0.0004646 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2525-3_1_3_load_41 | 6 | 0.00083733 | 0.00020985 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2525-3_1_3_load_26 | 7 | 0.015481 | 0.00388 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2525-3_1_3_load_27 | 8 | 0.0094336 | 0.0023643 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2525-3_1_3_load_28 | 9 | 0.015448 | 0.0038716 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2525-3_1_3_load_30 | 11 | 0.015444 | 0.0038705 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2525-3_1_3_load_49 | 12 | 0.0023212 | 0.00058174 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2525-3_1_3_load_31 | 13 | 0.005288 | 0.0013253 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2525-3_1_3_load_32 | 14 | 0.0029529 | 0.00074006 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2525-3_1_3_load_33 | 15 | 0.0016339 | 0.00040949 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2525-3_1_3_load_38 | 16 | 0.002622 | 0.00065713 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2525-3_1_3_load_39 | 17 | 0.0035322 | 0.00088527 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2525-3_1_3_load_205 | 20 | 0.0022209 | 0.00055661 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2525-3_1_3_load_42 | 21 | 0.0022536 | 0.0005648 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2525-3_1_3_load_43 | 23 | 0.0030447 | 0.00076308 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2525-3_1_3_load_54 | 26 | 0.0018074 | 0.00045297 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2525-3_1_3_load_50 | 27 | 0.0021109 | 0.00052905 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2525-3_1_3_load_47 | 28 | 0.0024023 | 0.00060207 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2525-3_1_3_load_48 | 29 | 0.0024145 | 0.00060513 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2525-3_1_3_load_56 | 30 | 0.0040702 | 0.0010201 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2525-3_1_3_load_61 | 31 | 0.0023825 | 0.00059712 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2525-3_1_3_load_51 | 32 | 0.0023765 | 0.0005956 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2525-3_1_3_load_52 | 33 | 0.0017542 | 0.00043964 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2525-3_1_3_load_53 | 34 | 0.0023833 | 0.00059732 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2525-3_1_3_load_55 | 35 | 0.0028899 | 0.00072427 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2525-3_1_3_load_62 | 36 | 0.0023725 | 0.0005946 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2525-3_1_3_load_57 | 37 | 0.0034368 | 0.00086135 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2525-3_1_3_load_58 | 38 | 0.0037955 | 0.00095125 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2525-3_1_3_load_65 | 40 | 0.003576 | 0.00089624 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2525-3_1_3_load_63 | 41 | 0.0027751 | 0.0006955 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2525-3_1_3_load_60 | 42 | 0.0027394 | 0.00068656 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2525-3_1_3_load_66 | 44 | 0.0069319 | 0.0017373 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2525-3_1_3_load_67 | 45 | 0.0031297 | 0.00078436 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2525-3_1_3_load_68 | 46 | 0.00092119 | 0.00023087 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2525-3_1_3_load_69 | 47 | 0.0028133 | 0.00070508 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2525-3_1_3_load_79 | 49 | 0.0013913 | 0.00034868 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2525-3_1_3_load_76 | 50 | 0.0011477 | 0.00028764 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2525-3_1_3_load_75 | 51 | 0.0083872 | 0.002102 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2525-3_1_3_load_72 | 52 | 0.0034596 | 0.00086706 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2525-3_1_3_load_73 | 53 | 0.0041397 | 0.0010375 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2525-3_1_3_load_74 | 54 | 0.0032265 | 0.00080863 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2525-3_1_3_load_77 | 55 | 0.0024261 | 0.00060805 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2525-3_1_3_load_124 | 56 | 0.0014083 | 0.00035295 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2525-3_1_3_load_93 | 57 | 0.0022618 | 0.00056685 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2525-3_1_3_load_232 | 60 | 0.0052901 | 0.0013258 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2525-3_1_3_load_97 | 62 | 0.0027322 | 0.00068475 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2525-3_1_3_load_215 | 64 | 0.0018271 | 0.00045793 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2525-3_1_3_load_228 | 65 | 0.00192 | 0.00048121 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2525-3_1_3_load_114 | 66 | 0.0022827 | 0.0005721 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2525-3_1_3_load_122 | 67 | 0.0032011 | 0.00080226 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2525-3_1_3_load_123 | 68 | 0.0036261 | 0.00090878 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2525-3_1_3_load_125 | 70 | 0.0016124 | 0.0004041 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2525-3_1_3_load_126 | 71 | 0.0040764 | 0.0010216 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2525-3_1_3_load_127 | 72 | 0.0037938 | 0.00095082 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2525-3_1_3_load_128 | 73 | 0.0018314 | 0.000459 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2525-3_1_3_load_130 | 75 | 0.0010752 | 0.00026948 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2525-3_1_3_load_131 | 76 | 0.0018818 | 0.00047163 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2525-3_1_3_load_133 | 78 | 0.0028857 | 0.00072323 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2525-3_1_3_load_206 | 79 | 0.0026674 | 0.0006685 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2525-3_1_3_load_219 | 80 | 0.0018331 | 0.00045943 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2525-3_1_3_load_211 | 81 | 0.0032348 | 0.00081071 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2525-3_1_3_load_207 | 82 | 0.0029652 | 0.00074314 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2525-3_1_3_load_208 | 83 | 0.0025556 | 0.00064048 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2525-3_1_3_load_210 | 84 | 0.0012463 | 0.00031235 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2525-3_1_3_load_212 | 85 | 0.0018502 | 0.0004637 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2525-3_1_3_load_213 | 86 | 0.0028865 | 0.00072341 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2525-3_1_3_load_214 | 87 | 0.0017492 | 0.0004384 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2525-3_1_3_load_216 | 88 | 0.0035686 | 0.00089437 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2525-3_1_3_load_217 | 89 | 0.0016418 | 0.00041148 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2525-3_1_3_load_218 | 90 | 0.0040125 | 0.0010056 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2525-3_1_3_load_229 | 91 | 0.0010686 | 0.00026782 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2525-3_1_3_line_0 |  | 0 | 1 | 0.0043234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2525-3_1_3_line_1 |  | 0 | 2 | 0.035019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2525-3_1_3_line_2 |  | 1 | 3 | 0.052524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2525-3_1_3_line_3 |  | 2 | 4 | 0.0008522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2525-3_1_3_line_4 |  | 3 | 5 | 0.025201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2525-3_1_3_line_5 |  | 4 | 6 | 0.0098172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2525-3_1_3_line_6 |  | 5 | 40 | 0.015293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2525-3_1_3_line_7 |  | 6 | 21 | 0.044731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2525-3_1_3_line_8 |  | 7 | 8 | 0.050543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2525-3_1_3_line_9 |  | 8 | 9 | 0.014512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2525-3_1_3_line_10 |  | 9 | 10 | 0.049779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2525-3_1_3_line_11 |  | 10 | 28 | 0.0089385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2525-3_1_3_line_12 |  | 10 | 29 | 0.0059916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2525-3_1_3_line_13 |  | 11 | 12 | 0.046405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2525-3_1_3_line_14 |  | 12 | 27 | 0.019087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2525-3_1_3_line_15 |  | 13 | 14 | 0.0022516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2525-3_1_3_line_16 |  | 14 | 15 | 0.0089719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2525-3_1_3_line_17 |  | 15 | 16 | 0.014386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2525-3_1_3_line_18 |  | 16 | 17 | 0.0025737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2525-3_1_3_line_19 |  | 17 | 18 | 0.018679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2525-3_1_3_line_20 |  | 18 | 19 | 0.030807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2525-3_1_3_line_21 |  | 18 | 20 | 0.0026542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2525-3_1_3_line_22 |  | 19 | 80 | 0.014997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2525-3_1_3_line_23 |  | 19 | 77 | 0.011033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2525-3_1_3_line_24 |  | 20 | 81 | 0.02917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2525-3_1_3_line_25 |  | 21 | 22 | 0.0030808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2525-3_1_3_line_26 |  | 22 | 51 | 0.023045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2525-3_1_3_line_27 |  | 22 | 47 | 0.018508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2525-3_1_3_line_28 |  | 23 | 24 | 0.053769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2525-3_1_3_line_29 |  | 24 | 25 | 0.04961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2525-3_1_3_line_30 |  | 25 | 26 | 0.0040972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2525-3_1_3_line_31 |  | 25 | 27 | 0.01574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2525-3_1_3_line_32 |  | 26 | 33 | 0.0058306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2525-3_1_3_line_33 |  | 28 | 30 | 0.0054493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2525-3_1_3_line_34 |  | 29 | 31 | 0.014265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2525-3_1_3_line_35 |  | 30 | 37 | 0.010244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2525-3_1_3_line_36 |  | 31 | 42 | 0.0016419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2525-3_1_3_line_37 |  | 32 | 33 | 0.014459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2525-3_1_3_line_38 |  | 32 | 34 | 0.0059158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2525-3_1_3_line_39 |  | 34 | 35 | 0.00062327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2525-3_1_3_line_40 |  | 35 | 36 | 0.012982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2525-3_1_3_line_41 |  | 36 | 42 | 0.0042671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2525-3_1_3_line_42 |  | 37 | 38 | 0.019198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2525-3_1_3_line_43 |  | 38 | 39 | 0.0039167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2525-3_1_3_line_44 |  | 39 | 40 | 0.027137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2525-3_1_3_line_45 |  | 39 | 41 | 0.016101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2525-3_1_3_line_46 |  | 41 | 43 | 0.011612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2525-3_1_3_line_47 |  | 43 | 44 | 0.006026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2525-3_1_3_line_48 |  | 43 | 45 | 0.006791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2525-3_1_3_line_49 |  | 46 | 47 | 0.0178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2525-3_1_3_line_50 |  | 47 | 48 | 0.026125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2525-3_1_3_line_51 |  | 48 | 49 | 0.019343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2525-3_1_3_line_52 |  | 48 | 50 | 0.0073375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2525-3_1_3_line_53 |  | 49 | 56 | 0.0066109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2525-3_1_3_line_54 |  | 50 | 55 | 0.028747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2525-3_1_3_line_55 |  | 51 | 53 | 0.0031929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2525-3_1_3_line_56 |  | 52 | 53 | 0.028953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2525-3_1_3_line_57 |  | 52 | 54 | 0.010113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2525-3_1_3_line_58 |  | 56 | 70 | 0.024301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2525-3_1_3_line_59 |  | 57 | 58 | 0.023598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2525-3_1_3_line_60 |  | 57 | 59 | 0.011494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2525-3_1_3_line_61 |  | 58 | 60 | 0.034683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2525-3_1_3_line_62 |  | 59 | 61 | 0.032141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2525-3_1_3_line_63 |  | 59 | 62 | 0.018927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2525-3_1_3_line_64 |  | 61 | 63 | 0.028396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2525-3_1_3_line_65 |  | 61 | 64 | 0.019728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2525-3_1_3_line_66 |  | 62 | 65 | 0.013787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2525-3_1_3_line_67 |  | 63 | 81 | 0.0019812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2525-3_1_3_line_68 |  | 63 | 82 | 0.013279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2525-3_1_3_line_69 |  | 64 | 86 | 0.0011312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2525-3_1_3_line_70 |  | 65 | 91 | 0.017153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2525-3_1_3_line_71 |  | 66 | 67 | 0.024773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2525-3_1_3_line_72 |  | 67 | 68 | 0.0018658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2525-3_1_3_line_73 |  | 68 | 69 | 0.016065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2525-3_1_3_line_74 |  | 69 | 71 | 0.035677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2525-3_1_3_line_75 |  | 69 | 76 | 0.016121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2525-3_1_3_line_76 |  | 70 | 71 | 0.008955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2525-3_1_3_line_77 |  | 72 | 73 | 0.018161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2525-3_1_3_line_78 |  | 72 | 74 | 0.018237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2525-3_1_3_line_79 |  | 74 | 75 | 0.01533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2525-3_1_3_line_80 |  | 74 | 76 | 0.010857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2525-3_1_3_line_81 |  | 75 | 77 | 0.010416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2525-3_1_3_line_82 |  | 77 | 78 | 0.018706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2525-3_1_3_line_83 |  | 78 | 79 | 0.017074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2525-3_1_3_line_84 |  | 80 | 89 | 0.02384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2525-3_1_3_line_85 |  | 82 | 83 | 0.00013372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2525-3_1_3_line_86 |  | 83 | 84 | 0.024522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2525-3_1_3_line_87 |  | 84 | 85 | 0.00041761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2525-3_1_3_line_88 |  | 86 | 87 | 0.014246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2525-3_1_3_line_89 |  | 87 | 88 | 0.0014073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2525-3_1_3_line_90 |  | 89 | 90 | 0.00022865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2525-3_1_3_trafo_21 | 0.63 MVA 20/0.4 kV | 92 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2612024.2113 | 1225202.5741 | 2612025.045 | 1225198.3319
1 | 2612018.1073 | 1225237.0551 | 2612022.7756 | 1225209.8792 | 2612024.2113 | 1225202.5741
2 | 2612036.4355 | 1225147.0713 | 2612036.1048 | 1225148.2922 | 2612031.5272 | 1225166.5826 | 2612027.8841 | 1225183.8854 | 2612025.045 | 1225198.3319
3 | 2612018.1073 | 1225237.0551 | 2612017.963 | 1225237.8949
4 | 2612043.0242 | 1225122.7467 | 2612036.4355 | 1225147.0713
5 | 2612017.963 | 1225237.8949 | 2612016.3009 | 1225247.5705
6 | 2612043.0242 | 1225122.7467 | 2612037.4903 | 1225122.7911 | 2612027.7316 | 1225122.8656
7 | 2612009.2639 | 1225291.7396 | 2612011.8686 | 1225273.3723 | 2612016.3009 | 1225247.5705
8 | 2611951.0249 | 1225188.3204 | 2611949.842 | 1225229.7892 | 2611948.4673 | 1225238.7414
9 | 2611951.4387 | 1225173.814 | 2611951.0249 | 1225188.3204
10 | 2611952.8581 | 1225124.0555 | 2611951.4387 | 1225173.814
11 | 2611952.8581 | 1225124.0555 | 2611961.7947 | 1225123.8715
12 | 2611952.8581 | 1225124.0555 | 2611946.868 | 1225124.1881
13 | 2611887.4997 | 1225206.7008 | 2611885.3692 | 1225173.1498 | 2611884.68 | 1225160.3823
14 | 2611883.6512 | 1225141.3232 | 2611884.68 | 1225160.3823
15 | 2612155.967 | 1225254.5358 | 2612158.2041 | 1225254.7915
16 | 2612155.967 | 1225254.5358 | 2612147.0531 | 1225253.5171
17 | 2612132.7597 | 1225251.8836 | 2612147.0531 | 1225253.5171
18 | 2612132.7597 | 1225251.8836 | 2612130.2027 | 1225251.5914
19 | 2612111.6447 | 1225249.4706 | 2612130.2027 | 1225251.5914
20 | 2612111.6447 | 1225249.4706 | 2612107.6486 | 1225280.0137
21 | 2612111.6447 | 1225249.4706 | 2612111.981 | 1225246.8378
22 | 2612107.6486 | 1225280.0137 | 2612092.6719 | 1225279.2251
23 | 2612107.6486 | 1225280.0137 | 2612106.2089 | 1225290.9505
24 | 2612111.981 | 1225246.8378 | 2612115.6764 | 1225217.9026
25 | 2612008.8314 | 1225294.7899 | 2612009.2639 | 1225291.7396
26 | 2612008.8314 | 1225294.7899 | 2611985.9831 | 1225291.7865
27 | 2612008.8314 | 1225294.7899 | 2612006.9296 | 1225313.1968
28 | 2611835.1976 | 1225113.7156 | 2611831.5069 | 1225117.0436 | 2611823.4547 | 1225121.6526 | 2611814.4334 | 1225125.7371 | 2611808.0852 | 1225127.3811 | 2611801.3522 | 1225128.1127 | 2611795.0462 | 1225127.5778 | 2611788.9703 | 1225125.6758 | 2611785.7897 | 1225124.0053
29 | 2611882.8029 | 1225125.6058 | 2611870.5083 | 1225125.0255 | 2611860.2017 | 1225123.5042 | 2611846.9277 | 1225119.9091 | 2611835.1976 | 1225113.7156
30 | 2611882.8029 | 1225125.6058 | 2611886.899 | 1225125.5151
31 | 2611882.8029 | 1225125.6058 | 2611883.6512 | 1225141.3232
32 | 2611886.899 | 1225125.5151 | 2611892.7282 | 1225125.3861
33 | 2611961.7947 | 1225123.8715 | 2611967.2429 | 1225123.7594
34 | 2611946.868 | 1225124.1881 | 2611932.6066 | 1225124.5037
35 | 2611977.4849 | 1225123.5485 | 2611967.2429 | 1225123.7594
36 | 2611930.9651 | 1225124.54 | 2611932.6066 | 1225124.5037
37 | 2611907.1832 | 1225125.0663 | 2611892.7282 | 1225125.3861
38 | 2611907.1832 | 1225125.0663 | 2611913.0975 | 1225124.9354
39 | 2611913.0975 | 1225124.9354 | 2611913.7207 | 1225124.9216
40 | 2611913.7207 | 1225124.9216 | 2611926.699 | 1225124.6344
41 | 2611930.9651 | 1225124.54 | 2611926.699 | 1225124.6344
42 | 2611977.4849 | 1225123.5485 | 2611996.6791 | 1225123.1534
43 | 2612000.595 | 1225123.0727 | 2611996.6791 | 1225123.1534
44 | 2612000.595 | 1225123.0727 | 2612027.7316 | 1225122.8656
45 | 2612000.595 | 1225123.0727 | 2611999.3869 | 1225139.1279
46 | 2611998.5156 | 1225150.707 | 2611999.3869 | 1225139.1279
47 | 2611998.5156 | 1225150.707 | 2612004.38 | 1225152.164
48 | 2611998.5156 | 1225150.707 | 2611996.5846 | 1225157.218
49 | 2612006.9296 | 1225313.1968 | 2611989.1369 | 1225312.6955
50 | 2612006.9296 | 1225313.1968 | 2612005.4181 | 1225329.7924 | 2612004.8155 | 1225339.2301
51 | 2612004.8155 | 1225339.2301 | 2612008.9695 | 1225339.2384 | 2612011.3042 | 1225339.2542 | 2612024.1585 | 1225339.2882
52 | 2612004.8155 | 1225339.2301 | 2612004.4946 | 1225346.5605
53 | 2612030.7694 | 1225339.3057 | 2612024.1585 | 1225339.2882
54 | 2612004.4946 | 1225346.5605 | 2612004.1561 | 1225354.2932 | 2612003.8155 | 1225372.9367 | 2612003.8508 | 1225375.2965
55 | 2611982.8174 | 1225291.3704 | 2611985.9831 | 1225291.7865
56 | 2611969.7727 | 1225272.253 | 2611971.7277 | 1225289.9127 | 2611982.8174 | 1225291.3704
57 | 2611968.66 | 1225262.2014 | 2611969.7727 | 1225272.253
58 | 2612030.7694 | 1225339.3057 | 2612055.07 | 1225339.37
59 | 2612128.2712 | 1225121.1179 | 2612125.0072 | 1225144.4894
60 | 2612123.4174 | 1225155.8729 | 2612125.0072 | 1225144.4894
61 | 2612128.2712 | 1225121.1179 | 2612134.2534 | 1225086.9545
62 | 2612119.517 | 1225187.7726 | 2612123.4174 | 1225155.8729
63 | 2612123.4174 | 1225155.8729 | 2612142.1925 | 1225158.2652
64 | 2612119.517 | 1225187.7726 | 2612115.9274 | 1225215.9374
65 | 2612119.517 | 1225187.7726 | 2612139.0939 | 1225190.2091
66 | 2612155.8689 | 1225160.0078 | 2612155.8689 | 1225160.0078 | 2612142.1925 | 1225158.2652
67 | 2612115.9274 | 1225215.9374 | 2612115.6764 | 1225217.9026
68 | 2612115.9274 | 1225215.9374 | 2612102.8056 | 1225213.8976
69 | 2612140.2164 | 1225190.3488 | 2612139.0939 | 1225190.2091
70 | 2612155.8689 | 1225160.0078 | 2612153.969 | 1225177.0552
71 | 2612141.8758 | 1225348.4724 | 2612117.2893 | 1225345.4402
72 | 2612115.4376 | 1225345.2118 | 2612117.2893 | 1225345.4402
73 | 2612099.493 | 1225343.2454 | 2612115.4376 | 1225345.2118
74 | 2612064.025 | 1225339.3937 | 2612099.493 | 1225343.2454
75 | 2612099.493 | 1225343.2454 | 2612101.5185 | 1225327.2521
76 | 2612064.025 | 1225339.3937 | 2612055.07 | 1225339.37
77 | 2612139.0657 | 1225319.1114 | 2612130.999 | 1225319.751 | 2612120.9979 | 1225318.5878
78 | 2612102.8825 | 1225316.481 | 2612120.9979 | 1225318.5878
79 | 2612102.8825 | 1225316.481 | 2612104.8632 | 1225301.2796
80 | 2612102.8825 | 1225316.481 | 2612101.5185 | 1225327.2521
81 | 2612106.2089 | 1225290.9505 | 2612104.8632 | 1225301.2796
82 | 2612106.2089 | 1225290.9505 | 2612124.8035 | 1225292.9877
83 | 2612141.7757 | 1225294.8471 | 2612124.8035 | 1225292.9877
84 | 2612068.8648 | 1225277.9715 | 2612092.6719 | 1225279.2251
85 | 2612102.6734 | 1225213.8771 | 2612102.8056 | 1225213.8976
86 | 2612102.6734 | 1225213.8771 | 2612078.442 | 1225210.1103
87 | 2612078.0294 | 1225210.0462 | 2612078.442 | 1225210.1103
88 | 2612140.2164 | 1225190.3488 | 2612154.3536 | 1225192.1083
89 | 2612155.7502 | 1225192.2821 | 2612154.3536 | 1225192.1083
90 | 2612068.6365 | 1225277.9594 | 2612068.8648 | 1225277.9715

## bus_geodata
| x | y | coords
0 | 2612024.2113 | 1225202.5741
1 | 2612025.045 | 1225198.3319
2 | 2612018.1073 | 1225237.0551
3 | 2612036.4355 | 1225147.0713
4 | 2612017.963 | 1225237.8949
5 | 2612043.0242 | 1225122.7467
6 | 2612016.3009 | 1225247.5705
7 | 2611948.4673 | 1225238.7414
8 | 2611951.0249 | 1225188.3204
9 | 2611951.4387 | 1225173.814
10 | 2611952.8581 | 1225124.0555
11 | 2611887.4997 | 1225206.7008
12 | 2611884.68 | 1225160.3823
13 | 2612158.2041 | 1225254.7915
14 | 2612155.967 | 1225254.5358
15 | 2612147.0531 | 1225253.5171
16 | 2612132.7597 | 1225251.8836
17 | 2612130.2027 | 1225251.5914
18 | 2612111.6447 | 1225249.4706
19 | 2612107.6486 | 1225280.0137
20 | 2612111.981 | 1225246.8378
21 | 2612009.2639 | 1225291.7396
22 | 2612008.8314 | 1225294.7899
23 | 2611785.7897 | 1225124.0053
24 | 2611835.1976 | 1225113.7156
25 | 2611882.8029 | 1225125.6058
26 | 2611886.899 | 1225125.5151
27 | 2611883.6512 | 1225141.3232
28 | 2611961.7947 | 1225123.8715
29 | 2611946.868 | 1225124.1881
30 | 2611967.2429 | 1225123.7594
31 | 2611932.6066 | 1225124.5037
32 | 2611907.1832 | 1225125.0663
33 | 2611892.7282 | 1225125.3862
34 | 2611913.0975 | 1225124.9354
35 | 2611913.7207 | 1225124.9216
36 | 2611926.699 | 1225124.6344
37 | 2611977.4849 | 1225123.5485
38 | 2611996.6791 | 1225123.1534
39 | 2612000.595 | 1225123.0727
40 | 2612027.7316 | 1225122.8656
41 | 2611999.3869 | 1225139.1279
42 | 2611930.9651 | 1225124.54
43 | 2611998.5156 | 1225150.707
44 | 2612004.38 | 1225152.164
45 | 2611996.5846 | 1225157.218
46 | 2611989.1369 | 1225312.6955
47 | 2612006.9296 | 1225313.1968
48 | 2612004.8155 | 1225339.2301
49 | 2612024.1585 | 1225339.2882
50 | 2612004.4946 | 1225346.5605
51 | 2611985.9831 | 1225291.7865
52 | 2611969.7727 | 1225272.253
53 | 2611982.8174 | 1225291.3704
54 | 2611968.66 | 1225262.2014
55 | 2612003.8508 | 1225375.2965
56 | 2612030.7694 | 1225339.3057
57 | 2612125.0072 | 1225144.4894
58 | 2612128.2712 | 1225121.1179
59 | 2612123.4174 | 1225155.8729
60 | 2612134.2534 | 1225086.9545
61 | 2612119.517 | 1225187.7726
62 | 2612142.1925 | 1225158.2652
63 | 2612115.9274 | 1225215.9374
64 | 2612139.0939 | 1225190.2091
65 | 2612155.8689 | 1225160.0078
66 | 2612141.8758 | 1225348.4724
67 | 2612117.2893 | 1225345.4402
68 | 2612115.4376 | 1225345.2118
69 | 2612099.493 | 1225343.2454
70 | 2612055.07 | 1225339.37
71 | 2612064.025 | 1225339.3937
72 | 2612120.9979 | 1225318.5878
73 | 2612139.0657 | 1225319.1114
74 | 2612102.8825 | 1225316.481
75 | 2612104.8632 | 1225301.2796
76 | 2612101.5185 | 1225327.2521
77 | 2612106.2089 | 1225290.9505
78 | 2612124.8035 | 1225292.9877
79 | 2612141.7757 | 1225294.8471
80 | 2612092.6719 | 1225279.2251
81 | 2612115.6764 | 1225217.9026
82 | 2612102.8056 | 1225213.8976
83 | 2612102.6734 | 1225213.8771
84 | 2612078.442 | 1225210.1103
85 | 2612078.0294 | 1225210.0462
86 | 2612140.2164 | 1225190.3488
87 | 2612154.3536 | 1225192.1083
88 | 2612155.7502 | 1225192.2821
89 | 2612068.8648 | 1225277.9715
90 | 2612068.6365 | 1225277.9594
91 | 2612153.969 | 1225177.0552
92 | 2612043.0242 | 1225122.7467

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.26294 | -0.06721
1 | 0.99948 | -0.0097799 | 0.0045449 | 0.0011391
2 | 0.99794 | -0.038881 | 0.0030195 | 0.00075676
3 | 0.99341 | -0.12519 | 0.010634 | 0.0026652
4 | 0.99784 | -0.040733 | 0.0018538 | 0.0004646
5 | 0.99074 | -0.17631 | 0 | 0
6 | 0.99672 | -0.061768 | 0.00083733 | 0.00020985
7 | 0.97939 | -0.39671 | 0.015481 | 0.00388
8 | 0.98011 | -0.3825 | 0.0094336 | 0.0023643
9 | 0.98045 | -0.37594 | 0.015448 | 0.0038716
10 | 0.98231 | -0.33958 | 0 | 0
11 | 0.97888 | -0.40667 | 0.015444 | 0.0038705
12 | 0.97955 | -0.39364 | 0.0023212 | 0.00058174
13 | 0.97333 | -0.51347 | 0.005288 | 0.0013253
14 | 0.97335 | -0.51325 | 0.0029529 | 0.00074006
15 | 0.97341 | -0.51189 | 0.0016339 | 0.00040949
16 | 0.97355 | -0.50928 | 0.002622 | 0.00065713
17 | 0.97358 | -0.50869 | 0.0035322 | 0.00088527
18 | 0.97386 | -0.50319 | 0 | 0
19 | 0.97539 | -0.47299 | 0 | 0
20 | 0.97376 | -0.50501 | 0.0022209 | 0.00055661
21 | 0.99168 | -0.15755 | 0.0022536 | 0.0005648
22 | 0.99134 | -0.16406 | 0 | 0
23 | 0.97986 | -0.38752 | 0.0030447 | 0.00076308
24 | 0.98001 | -0.38455 | 0 | 0
25 | 0.98015 | -0.38181 | 0 | 0
26 | 0.98024 | -0.3801 | 0.0018074 | 0.00045297
27 | 0.97986 | -0.38749 | 0.0021109 | 0.00052905
28 | 0.98301 | -0.32596 | 0.0024023 | 0.00060207
29 | 0.98206 | -0.34435 | 0.0024145 | 0.00060513
30 | 0.98344 | -0.31743 | 0.0040702 | 0.0010201
31 | 0.98151 | -0.35509 | 0.0023825 | 0.00059712
32 | 0.98072 | -0.37055 | 0.0023765 | 0.0005956
33 | 0.98037 | -0.37749 | 0.0017542 | 0.00043964
34 | 0.98088 | -0.36745 | 0.0023833 | 0.00059732
35 | 0.9809 | -0.3671 | 0.0028899 | 0.00072427
36 | 0.98131 | -0.35907 | 0.0023725 | 0.0005946
37 | 0.9843 | -0.30067 | 0.0034368 | 0.00086135
38 | 0.98598 | -0.26815 | 0.0037955 | 0.00095125
39 | 0.98634 | -0.26126 | 0 | 0
40 | 0.98912 | -0.20746 | 0.003576 | 0.00089624
41 | 0.98615 | -0.26496 | 0.0027751 | 0.0006955
42 | 0.98145 | -0.35625 | 0.0027394 | 0.00068656
43 | 0.98604 | -0.26706 | 0 | 0
44 | 0.986 | -0.2678 | 0.0069319 | 0.0017373
45 | 0.98602 | -0.26744 | 0.0031297 | 0.00078436
46 | 0.98961 | -0.19722 | 0.00092119 | 0.00023087
47 | 0.98962 | -0.19692 | 0.0028133 | 0.00070508
48 | 0.98728 | -0.24177 | 0 | 0
49 | 0.98562 | -0.27387 | 0.0013913 | 0.00034868
50 | 0.98726 | -0.24224 | 0.0011477 | 0.00028764
51 | 0.99094 | -0.17191 | 0.0083872 | 0.002102
52 | 0.99073 | -0.17596 | 0.0034596 | 0.00086706
53 | 0.99091 | -0.17253 | 0.0041397 | 0.0010375
54 | 0.9907 | -0.17654 | 0.0032265 | 0.00080863
55 | 0.9872 | -0.24349 | 0.0024261 | 0.00060805
56 | 0.98506 | -0.2847 | 0.0014083 | 0.00035295
57 | 0.97165 | -0.54672 | 0.0022618 | 0.00056685
58 | 0.97153 | -0.54903 | 0 | 0
59 | 0.97173 | -0.54512 | 0 | 0
60 | 0.97136 | -0.55242 | 0.0052901 | 0.0013258
61 | 0.97213 | -0.53725 | 0 | 0
62 | 0.97163 | -0.54712 | 0.0027322 | 0.00068475
63 | 0.97275 | -0.52505 | 0 | 0
64 | 0.97195 | -0.5409 | 0.0018271 | 0.00045793
65 | 0.97159 | -0.54788 | 0.00192 | 0.00048121
66 | 0.97929 | -0.39652 | 0.0022827 | 0.0005721
67 | 0.97935 | -0.3955 | 0.0032011 | 0.00080226
68 | 0.97936 | -0.39531 | 0.0036261 | 0.00090878
69 | 0.97949 | -0.39265 | 0 | 0
70 | 0.98302 | -0.324 | 0.0016124 | 0.0004041
71 | 0.98229 | -0.33826 | 0.0040764 | 0.0010216
72 | 0.97753 | -0.431 | 0.0037938 | 0.00095082
73 | 0.9775 | -0.43161 | 0.0018314 | 0.000459
74 | 0.97763 | -0.42913 | 0 | 0
75 | 0.97666 | -0.44803 | 0.0010752 | 0.00026948
76 | 0.97837 | -0.41465 | 0.0018818 | 0.00047163
77 | 0.97602 | -0.46069 | 0 | 0
78 | 0.97592 | -0.46259 | 0.0028857 | 0.00072323
79 | 0.97588 | -0.46342 | 0.0026674 | 0.0006685
80 | 0.97529 | -0.47505 | 0.0018331 | 0.00045943
81 | 0.97281 | -0.52388 | 0.0032348 | 0.00081071
82 | 0.97264 | -0.52716 | 0.0029652 | 0.00074314
83 | 0.97264 | -0.52717 | 0.0025556 | 0.00064048
84 | 0.97257 | -0.52857 | 0.0012463 | 0.00031235
85 | 0.97257 | -0.52858 | 0.0018502 | 0.0004637
86 | 0.97194 | -0.54107 | 0.0028865 | 0.00072341
87 | 0.97187 | -0.54247 | 0.0017492 | 0.0004384
88 | 0.97186 | -0.54256 | 0.0035686 | 0.00089437
89 | 0.97516 | -0.47752 | 0.0016418 | 0.00041148
90 | 0.97516 | -0.47753 | 0.0040125 | 0.0010056
91 | 0.97158 | -0.54822 | 0.0010686 | 0.00026782
92 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.13174 | 0.033806 | -0.13168 | -0.033766 | 6.2483e-05 | 3.9932e-05 | 0.19631 | 0.19631 | 0.19631 | 1 | 0 | 0.99948 | -0.0097799 | 53.9325
1 | 0.12955 | 0.033405 | -0.1293 | -0.033249 | 0.00024484 | 0.00015578 | 0.1931 | 0.1931 | 0.1931 | 1 | 0 | 0.99794 | -0.038881 | 26.5254
2 | 0.12714 | 0.032627 | -0.12643 | -0.032175 | 0.00070767 | 0.00045223 | 0.18955 | 0.18955 | 0.18955 | 0.99948 | -0.0097799 | 0.99341 | -0.12519 | 52.0737
3 | 0.12628 | 0.032492 | -0.12627 | -0.032485 | 1.1367e-05 | 7.2641e-06 | 0.1886 | 0.1886 | 0.1886 | 0.99794 | -0.038881 | 0.99784 | -0.040733 | 51.8138
4 | 0.11579 | 0.029509 | -0.11551 | -0.029327 | 0.00028487 | 0.00018199 | 0.17362 | 0.17362 | 0.17362 | 0.99341 | -0.12519 | 0.99074 | -0.17631 | 47.6978
5 | 0.12442 | 0.03202 | -0.12429 | -0.031939 | 0.00012714 | 8.1243e-05 | 0.18584 | 0.18584 | 0.18584 | 0.99784 | -0.040733 | 0.99672 | -0.061768 | 51.0544
6 | 0.11551 | 0.029327 | -0.11534 | -0.029217 | 0.00017287 | 0.00011044 | 0.17362 | 0.17362 | 0.17362 | 0.99074 | -0.17631 | 0.98912 | -0.20746 | 47.6978
7 | 0.12346 | 0.031729 | -0.12288 | -0.031364 | 0.00057154 | 0.00036521 | 0.18459 | 0.18459 | 0.18459 | 0.99672 | -0.061768 | 0.99168 | -0.15755 | 50.7111
8 | -0.015481 | -0.00388 | 0.015492 | 0.003886 | 1.0486e-05 | 6.0744e-06 | 0.023521 | 0.023521 | 0.023521 | 0.97939 | -0.39671 | 0.98011 | -0.3825 | 6.4618
9 | -0.024925 | -0.0062503 | 0.024933 | 0.0062551 | 7.7936e-06 | 4.8049e-06 | 0.037843 | 0.037843 | 0.037843 | 0.98011 | -0.3825 | 0.98045 | -0.37594 | 10.3964
10 | -0.040381 | -0.010127 | 0.040451 | 0.010171 | 7.0117e-05 | 4.4246e-05 | 0.061288 | 0.061288 | 0.061288 | 0.98045 | -0.37594 | 0.98231 | -0.33958 | 16.8373
11 | -0.084583 | -0.021264 | 0.084638 | 0.021299 | 5.5047e-05 | 3.5117e-05 | 0.12815 | 0.12815 | 0.12815 | 0.98231 | -0.33958 | 0.98301 | -0.32596 | 35.2062
12 | 0.044132 | 0.011093 | -0.044122 | -0.011086 | 1.0045e-05 | 6.3529e-06 | 0.066863 | 0.066863 | 0.066863 | 0.98231 | -0.33958 | 0.98206 | -0.34435 | 18.369
13 | -0.015444 | -0.0038705 | 0.015453 | 0.0038761 | 9.5905e-06 | 5.5542e-06 | 0.023476 | 0.023476 | 0.023476 | 0.97888 | -0.40667 | 0.97955 | -0.39364 | 6.4495
14 | -0.017774 | -0.0044578 | 0.01778 | 0.0044609 | 5.2186e-06 | 3.0996e-06 | 0.027002 | 0.027002 | 0.027002 | 0.97955 | -0.39364 | 0.97986 | -0.38749 | 7.4181
15 | -0.005288 | -0.0013253 | 0.0052881 | 0.0013253 | 5.5183e-08 | 7.3314e-09 | 0.0080842 | 0.0080842 | 0.0080842 | 0.97333 | -0.51347 | 0.97335 | -0.51325 | 2.2209
16 | -0.008241 | -0.0020654 | 0.0082415 | 0.0020656 | 5.3402e-07 | 2.3025e-07 | 0.012599 | 0.012598 | 0.012599 | 0.97335 | -0.51325 | 0.97341 | -0.51189 | 3.4611
17 | -0.0098754 | -0.0024751 | 0.0098766 | 0.0024757 | 1.2295e-06 | 6.0799e-07 | 0.015096 | 0.015096 | 0.015096 | 0.97341 | -0.51189 | 0.97355 | -0.50928 | 4.1473
18 | -0.012499 | -0.0031328 | 0.012499 | 0.003133 | 3.5222e-07 | 1.9342e-07 | 0.019104 | 0.019104 | 0.019104 | 0.97355 | -0.50928 | 0.97358 | -0.50869 | 5.2482
19 | -0.016031 | -0.0040183 | 0.016035 | 0.0040208 | 4.2052e-06 | 2.459e-06 | 0.024502 | 0.024502 | 0.024502 | 0.97358 | -0.50869 | 0.97386 | -0.50319 | 6.7314
20 | -0.053474 | -0.013424 | 0.053551 | 0.013473 | 7.7138e-05 | 4.8985e-05 | 0.081714 | 0.081714 | 0.081714 | 0.97386 | -0.50319 | 0.97539 | -0.47299 | 22.4489
21 | 0.037438 | 0.0094032 | -0.037435 | -0.0094011 | 3.2579e-06 | 2.052e-06 | 0.057212 | 0.057212 | 0.057212 | 0.97386 | -0.50319 | 0.97376 | -0.50501 | 15.7175
22 | 0.0074889 | 0.001877 | -0.0074882 | -0.0018767 | 7.3409e-07 | 2.8264e-07 | 0.011425 | 0.011425 | 0.011425 | 0.97539 | -0.47299 | 0.97529 | -0.47505 | 3.1387
23 | -0.06104 | -0.01535 | 0.061076 | 0.015373 | 3.5891e-05 | 2.2832e-05 | 0.093138 | 0.093138 | 0.093138 | 0.97539 | -0.47299 | 0.97602 | -0.46069 | 25.5875
24 | 0.035214 | 0.0088445 | -0.035182 | -0.0088246 | 3.1683e-05 | 1.9915e-05 | 0.053818 | 0.053818 | 0.053818 | 0.97376 | -0.50501 | 0.97281 | -0.52388 | 14.7852
25 | 0.12063 | 0.030799 | -0.12059 | -0.030775 | 3.7935e-05 | 2.4239e-05 | 0.18121 | 0.18121 | 0.18121 | 0.99168 | -0.15755 | 0.99134 | -0.16406 | 49.7821
26 | 0.019222 | 0.00482 | -0.019215 | -0.0048157 | 7.1942e-06 | 4.3073e-06 | 0.028853 | 0.028853 | 0.028853 | 0.99134 | -0.16406 | 0.99094 | -0.17191 | 7.9266
27 | 0.10137 | 0.025955 | -0.10121 | -0.025852 | 0.0001611 | 0.00010287 | 0.15235 | 0.15235 | 0.15235 | 0.99134 | -0.16406 | 0.98962 | -0.19692 | 41.8556
28 | -0.0030447 | -0.00076308 | 0.0030452 | 0.00076268 | 4.3105e-07 | -4.0151e-07 | 0.0046237 | 0.0046235 | 0.0046237 | 0.97986 | -0.38752 | 0.98001 | -0.38455 | 1.2703
29 | -0.0030452 | -0.00076268 | 0.0030456 | 0.00076231 | 3.9767e-07 | -3.7067e-07 | 0.0046235 | 0.0046233 | 0.0046235 | 0.98001 | -0.38455 | 0.98015 | -0.38181 | 1.2702
30 | -0.022942 | -0.0057555 | 0.022943 | 0.0057567 | 1.864e-06 | 1.1413e-06 | 0.034831 | 0.034831 | 0.034831 | 0.98015 | -0.38181 | 0.98024 | -0.3801 | 9.5689
31 | 0.019896 | 0.0049932 | -0.019891 | -0.00499 | 5.3861e-06 | 3.2488e-06 | 0.030208 | 0.030208 | 0.030208 | 0.98015 | -0.38181 | 0.97986 | -0.38749 | 8.2988
32 | -0.024751 | -0.0062097 | 0.024754 | 0.0062116 | 3.0869e-06 | 1.9021e-06 | 0.037574 | 0.037574 | 0.037574 | 0.98024 | -0.3801 | 0.98037 | -0.37749 | 10.3226
33 | -0.08704 | -0.021901 | 0.087075 | 0.021923 | 3.5491e-05 | 2.2645e-05 | 0.13179 | 0.13179 | 0.13179 | 0.98301 | -0.32596 | 0.98344 | -0.31743 | 36.2052
34 | 0.041707 | 0.010481 | -0.041686 | -0.010468 | 2.137e-05 | 1.3496e-05 | 0.063205 | 0.063205 | 0.063205 | 0.98206 | -0.34435 | 0.98151 | -0.35509 | 17.3639
35 | -0.091146 | -0.022944 | 0.091219 | 0.02299 | 7.3101e-05 | 4.6655e-05 | 0.13795 | 0.13795 | 0.13795 | 0.98344 | -0.31743 | 0.9843 | -0.30067 | 37.8971
36 | 0.039303 | 0.0098706 | -0.039301 | -0.0098693 | 2.1866e-06 | 1.3787e-06 | 0.059593 | 0.059593 | 0.059593 | 0.98151 | -0.35509 | 0.98145 | -0.35625 | 16.3716
37 | 0.026517 | 0.0066566 | -0.026508 | -0.0066512 | 8.7781e-06 | 5.4356e-06 | 0.040237 | 0.040237 | 0.040237 | 0.98072 | -0.37055 | 0.98037 | -0.37749 | 11.0541
38 | -0.028893 | -0.0072522 | 0.028898 | 0.0072549 | 4.2642e-06 | 2.6544e-06 | 0.043843 | 0.043843 | 0.043843 | 0.98072 | -0.37055 | 0.98088 | -0.36745 | 12.0447
39 | -0.031281 | -0.0078522 | 0.031281 | 0.0078525 | 5.2642e-07 | 3.2904e-07 | 0.047458 | 0.047458 | 0.047458 | 0.98088 | -0.36745 | 0.9809 | -0.3671 | 13.0379
40 | -0.034171 | -0.0085768 | 0.034184 | 0.008585 | 1.3083e-05 | 8.2094e-06 | 0.051842 | 0.051842 | 0.051842 | 0.9809 | -0.3671 | 0.98131 | -0.35907 | 14.2423
41 | -0.036557 | -0.0091796 | 0.036562 | 0.0091827 | 4.9181e-06 | 3.0937e-06 | 0.055439 | 0.055439 | 0.055439 | 0.98131 | -0.35907 | 0.98145 | -0.35625 | 15.2306
42 | -0.094656 | -0.023852 | 0.094803 | 0.023946 | 0.00014751 | 9.4162e-05 | 0.14314 | 0.14314 | 0.14314 | 0.9843 | -0.30067 | 0.98598 | -0.26815 | 39.3244
43 | -0.098599 | -0.024897 | 0.098631 | 0.024918 | 3.2551e-05 | 2.0783e-05 | 0.14887 | 0.14887 | 0.14887 | 0.98598 | -0.26815 | 0.98634 | -0.26126 | 40.898
44 | -0.11147 | -0.028137 | 0.11176 | 0.028321 | 0.00028804 | 0.000184 | 0.16824 | 0.16824 | 0.16824 | 0.98634 | -0.26126 | 0.98912 | -0.20746 | 46.2199
45 | 0.01284 | 0.0032189 | -0.012838 | -0.0032177 | 2.2657e-06 | 1.2446e-06 | 0.019371 | 0.019372 | 0.019372 | 0.98634 | -0.26126 | 0.98615 | -0.26496 | 5.3218
46 | 0.010063 | 0.0025222 | -0.010062 | -0.0025217 | 1.004e-06 | 4.944e-07 | 0.015184 | 0.015184 | 0.015184 | 0.98615 | -0.26496 | 0.98604 | -0.26706 | 4.1715
47 | 0.0069321 | 0.0017374 | -0.0069319 | -0.0017373 | 2.473e-07 | 8.1411e-08 | 0.010461 | 0.010461 | 0.010461 | 0.98604 | -0.26706 | 0.986 | -0.2678 | 2.874
48 | 0.0031297 | 0.00078431 | -0.0031297 | -0.00078436 | 5.6807e-08 | -5.0265e-08 | 0.004723 | 0.004723 | 0.004723 | 0.98604 | -0.26706 | 0.98602 | -0.26744 | 1.2975
49 | -0.00092119 | -0.00023087 | 0.0009212 | 0.00023065 | 1.2806e-08 | -2.205e-07 | 0.0013851 | 0.0013851 | 0.0013851 | 0.98961 | -0.19722 | 0.98962 | -0.19692 | 0.38053
50 | 0.097475 | 0.024916 | -0.097264 | -0.024782 | 0.00021095 | 0.00013467 | 0.14674 | 0.14674 | 0.14674 | 0.98962 | -0.19692 | 0.98728 | -0.24177 | 40.313
51 | 0.09369 | 0.023886 | -0.093545 | -0.023794 | 0.00014493 | 9.251e-05 | 0.14135 | 0.14135 | 0.14135 | 0.98728 | -0.24177 | 0.98562 | -0.27387 | 38.8332
52 | 0.0035741 | 0.00089537 | -0.003574 | -0.00089541 | 7.9839e-08 | -4.2731e-08 | 0.0053866 | 0.0053867 | 0.0053867 | 0.98728 | -0.24177 | 0.98726 | -0.24224 | 1.4799
53 | 0.092154 | 0.023445 | -0.092106 | -0.023414 | 4.8073e-05 | 3.0682e-05 | 0.13925 | 0.13925 | 0.13925 | 0.98562 | -0.27387 | 0.98506 | -0.2847 | 38.2562
54 | 0.0024263 | 0.00060777 | -0.0024261 | -0.00060805 | 1.4416e-07 | -2.753e-07 | 0.0036568 | 0.003657 | 0.003657 | 0.98726 | -0.24224 | 0.9872 | -0.24349 | 1.0047
55 | 0.010827 | 0.0027136 | -0.010827 | -0.0027135 | 3.165e-07 | 1.6143e-07 | 0.016259 | 0.016259 | 0.016259 | 0.99094 | -0.17191 | 0.99091 | -0.17253 | 4.4666
56 | -0.0066862 | -0.0016756 | 0.0066873 | 0.0016759 | 1.0949e-06 | 3.2784e-07 | 0.010042 | 0.010042 | 0.010042 | 0.99073 | -0.17596 | 0.99091 | -0.17253 | 2.7588
57 | 0.0032266 | 0.00080856 | -0.0032265 | -0.00080863 | 8.9063e-08 | -7.3223e-08 | 0.0048461 | 0.0048461 | 0.0048461 | 0.99073 | -0.17596 | 0.9907 | -0.17654 | 1.3314
58 | 0.090697 | 0.023061 | -0.090526 | -0.022952 | 0.00017135 | 0.00010936 | 0.13713 | 0.13713 | 0.13713 | 0.98506 | -0.2847 | 0.98302 | -0.324 | 37.6718
59 | 0.0052916 | 0.001326 | -0.005291 | -0.0013259 | 5.8113e-07 | 7.9669e-08 | 0.0081036 | 0.0081037 | 0.0081037 | 0.97165 | -0.54672 | 0.97153 | -0.54903 | 2.2263
60 | -0.0075533 | -0.0018929 | 0.0075539 | 0.0018931 | 5.7672e-07 | 2.2672e-07 | 0.011567 | 0.011567 | 0.011567 | 0.97165 | -0.54672 | 0.97173 | -0.54512 | 3.1778
61 | 0.005291 | 0.0013259 | -0.0052901 | -0.0013258 | 8.5413e-07 | 1.1724e-07 | 0.0081037 | 0.0081038 | 0.0081038 | 0.97153 | -0.54903 | 0.97136 | -0.55242 | 2.2263
62 | -0.013275 | -0.0033267 | 0.01328 | 0.0033295 | 4.9808e-06 | 2.7894e-06 | 0.020329 | 0.020328 | 0.020329 | 0.97173 | -0.54512 | 0.97213 | -0.53725 | 5.5848
63 | 0.0057215 | 0.0014336 | -0.005721 | -0.0014335 | 5.4482e-07 | 1.1424e-07 | 0.0087613 | 0.0087614 | 0.0087614 | 0.97173 | -0.54512 | 0.97163 | -0.54712 | 2.407
64 | -0.023314 | -0.0058445 | 0.023328 | 0.0058529 | 1.3561e-05 | 8.327e-06 | 0.035687 | 0.035687 | 0.035687 | 0.97213 | -0.53725 | 0.97275 | -0.52505 | 9.8041
65 | 0.010034 | 0.0025151 | -0.010032 | -0.0025142 | 1.745e-06 | 8.7228e-07 | 0.015358 | 0.015358 | 0.015358 | 0.97213 | -0.53725 | 0.97195 | -0.5409 | 4.2194
66 | 0.0029888 | 0.00074873 | -0.0029887 | -0.00074883 | 1.0831e-07 | -1.0143e-07 | 0.0045771 | 0.0045772 | 0.0045772 | 0.97163 | -0.54712 | 0.97159 | -0.54788 | 1.2575
67 | -0.031946 | -0.0080128 | 0.031948 | 0.0080139 | 1.7744e-06 | 1.111e-06 | 0.04887 | 0.04887 | 0.04887 | 0.97275 | -0.52505 | 0.97281 | -0.52388 | 13.4258
68 | 0.0086183 | 0.0021599 | -0.0086174 | -0.0021595 | 8.655e-07 | 3.8909e-07 | 0.013183 | 0.013183 | 0.013183 | 0.97275 | -0.52505 | 0.97264 | -0.52716 | 3.6218
69 | 0.0082047 | 0.0020563 | -0.0082047 | -0.0020562 | 6.6931e-08 | 2.8817e-08 | 0.012561 | 0.012561 | 0.012561 | 0.97195 | -0.5409 | 0.97194 | -0.54107 | 3.4509
70 | 0.0010686 | 0.00026762 | -0.0010686 | -0.00026782 | 1.7229e-08 | -2.014e-07 | 0.0016366 | 0.0016366 | 0.0016366 | 0.97159 | -0.54788 | 0.97158 | -0.54822 | 0.44963
71 | -0.0022827 | -0.0005721 | 0.0022828 | 0.00057186 | 1.1176e-07 | -2.4017e-07 | 0.0034685 | 0.0034684 | 0.0034685 | 0.97929 | -0.39652 | 0.97935 | -0.3955 | 0.95289
72 | -0.0054839 | -0.0013741 | 0.0054839 | 0.0013741 | 4.8573e-08 | 7.6096e-09 | 0.0083321 | 0.0083321 | 0.0083321 | 0.97935 | -0.3955 | 0.97936 | -0.39531 | 2.289
73 | -0.00911 | -0.0022829 | 0.0091112 | 0.0022834 | 1.1542e-06 | 5.3651e-07 | 0.013841 | 0.013841 | 0.013841 | 0.97936 | -0.39531 | 0.97949 | -0.39265 | 3.8026
74 | -0.084555 | -0.021346 | 0.084776 | 0.021487 | 0.00022095 | 0.00014095 | 0.12851 | 0.12851 | 0.12851 | 0.97949 | -0.39265 | 0.98229 | -0.33826 | 35.3048
75 | 0.075444 | 0.019063 | -0.075365 | -0.019012 | 7.949e-05 | 5.0671e-05 | 0.11467 | 0.11467 | 0.11467 | 0.97949 | -0.39265 | 0.97837 | -0.41465 | 31.5023
76 | 0.088914 | 0.022548 | -0.088853 | -0.022509 | 6.0916e-05 | 3.8873e-05 | 0.13468 | 0.13468 | 0.13468 | 0.98302 | -0.324 | 0.98229 | -0.33826 | 37.0013
77 | 0.0018315 | 0.00045881 | -0.0018314 | -0.000459 | 5.2931e-08 | -1.9378e-07 | 0.0027878 | 0.0027879 | 0.0027879 | 0.97753 | -0.431 | 0.9775 | -0.43161 | 0.76591
78 | -0.0056253 | -0.0014096 | 0.0056258 | 0.0014097 | 5.0145e-07 | 9.2278e-08 | 0.0085629 | 0.0085628 | 0.0085629 | 0.97753 | -0.431 | 0.97763 | -0.42913 | 2.3524
79 | 0.067806 | 0.017099 | -0.067745 | -0.01706 | 6.1277e-05 | 3.9025e-05 | 0.10324 | 0.10324 | 0.10324 | 0.97763 | -0.42913 | 0.97666 | -0.44803 | 28.3636
80 | -0.073432 | -0.018508 | 0.073483 | 0.018541 | 5.0895e-05 | 3.2437e-05 | 0.11181 | 0.11181 | 0.11181 | 0.97763 | -0.42913 | 0.97837 | -0.41465 | 30.716
81 | 0.06667 | 0.01679 | -0.066629 | -0.016764 | 4.0325e-05 | 2.5678e-05 | 0.10161 | 0.10161 | 0.10161 | 0.97666 | -0.44803 | 0.97602 | -0.46069 | 27.9136
82 | 0.0055537 | 0.0013917 | -0.0055532 | -0.0013916 | 5.0289e-07 | 8.8094e-08 | 0.008467 | 0.0084671 | 0.0084671 | 0.97602 | -0.46069 | 0.97592 | -0.46259 | 2.3261
83 | 0.0026675 | 0.00066836 | -0.0026674 | -0.0006685 | 1.0591e-07 | -1.4555e-07 | 0.0040671 | 0.0040672 | 0.0040672 | 0.97592 | -0.46259 | 0.97588 | -0.46342 | 1.1174
84 | 0.005655 | 0.0014172 | -0.0056543 | -0.0014171 | 6.6552e-07 | 1.2848e-07 | 0.008628 | 0.0086281 | 0.0086281 | 0.97529 | -0.47505 | 0.97516 | -0.47752 | 2.3703
85 | 0.0056522 | 0.0014164 | -0.0056522 | -0.0014164 | 3.7501e-09 | 7.4003e-10 | 0.0086471 | 0.0086471 | 0.0086471 | 0.97264 | -0.52716 | 0.97264 | -0.52717 | 2.3756
86 | 0.0030967 | 0.00077587 | -0.0030965 | -0.00077604 | 2.0639e-07 | -1.7224e-07 | 0.0047374 | 0.0047376 | 0.0047376 | 0.97264 | -0.52717 | 0.97257 | -0.52857 | 1.3015
87 | 0.0018502 | 0.0004637 | -0.0018502 | -0.0004637 | 1.2549e-09 | -4.3792e-09 | 0.0028308 | 0.0028308 | 0.0028308 | 0.97257 | -0.52857 | 0.97257 | -0.52858 | 0.77769
88 | 0.0053182 | 0.0013328 | -0.0053179 | -0.0013328 | 3.5416e-07 | 5.0119e-08 | 0.0081421 | 0.0081421 | 0.0081421 | 0.97194 | -0.54107 | 0.97187 | -0.54247 | 2.2368
89 | 0.0035686 | 0.00089437 | -0.0035686 | -0.00089437 | 1.5755e-08 | -7.3555e-09 | 0.0054639 | 0.0054639 | 0.0054639 | 0.97187 | -0.54247 | 0.97186 | -0.54256 | 1.5011
90 | 0.0040125 | 0.0010056 | -0.0040125 | -0.0010056 | 3.2136e-09 | -7.9519e-10 | 0.0061228 | 0.0061228 | 0.0061228 | 0.97516 | -0.47752 | 0.97516 | -0.47753 | 1.6821

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27096 | 0.069219

## res_load
| p_mw | q_mvar
0 | 0.0080157 | 0.0020089
1 | 0.0045449 | 0.0011391
2 | 0.0030195 | 0.00075676
3 | 0.010634 | 0.0026652
4 | 0.0018538 | 0.0004646
5 | 0.00083733 | 0.00020985
6 | 0.015481 | 0.00388
7 | 0.0094336 | 0.0023643
8 | 0.015448 | 0.0038716
9 | 0.015444 | 0.0038705
10 | 0.0023212 | 0.00058174
11 | 0.005288 | 0.0013253
12 | 0.0029529 | 0.00074006
13 | 0.0016339 | 0.00040949
14 | 0.002622 | 0.00065713
15 | 0.0035322 | 0.00088527
16 | 0.0022209 | 0.00055661
17 | 0.0022536 | 0.0005648
18 | 0.0030447 | 0.00076308
19 | 0.0018074 | 0.00045297
20 | 0.0021109 | 0.00052905
21 | 0.0024023 | 0.00060207
22 | 0.0024145 | 0.00060513
23 | 0.0040702 | 0.0010201
24 | 0.0023825 | 0.00059712
25 | 0.0023765 | 0.0005956
26 | 0.0017542 | 0.00043964
27 | 0.0023833 | 0.00059732
28 | 0.0028899 | 0.00072427
29 | 0.0023725 | 0.0005946
30 | 0.0034368 | 0.00086135
31 | 0.0037955 | 0.00095125
32 | 0.003576 | 0.00089624
33 | 0.0027751 | 0.0006955
34 | 0.0027394 | 0.00068656
35 | 0.0069319 | 0.0017373
36 | 0.0031297 | 0.00078436
37 | 0.00092119 | 0.00023087
38 | 0.0028133 | 0.00070508
39 | 0.0013913 | 0.00034868
40 | 0.0011477 | 0.00028764
41 | 0.0083872 | 0.002102
42 | 0.0034596 | 0.00086706
43 | 0.0041397 | 0.0010375
44 | 0.0032265 | 0.00080863
45 | 0.0024261 | 0.00060805
46 | 0.0014083 | 0.00035295
47 | 0.0022618 | 0.00056685
48 | 0.0052901 | 0.0013258
49 | 0.0027322 | 0.00068475
50 | 0.0018271 | 0.00045793
51 | 0.00192 | 0.00048121
52 | 0.0022827 | 0.0005721
53 | 0.0032011 | 0.00080226
54 | 0.0036261 | 0.00090878
55 | 0.0016124 | 0.0004041
56 | 0.0040764 | 0.0010216
57 | 0.0037938 | 0.00095082
58 | 0.0018314 | 0.000459
59 | 0.0010752 | 0.00026948
60 | 0.0018818 | 0.00047163
61 | 0.0028857 | 0.00072323
62 | 0.0026674 | 0.0006685
63 | 0.0018331 | 0.00045943
64 | 0.0032348 | 0.00081071
65 | 0.0029652 | 0.00074314
66 | 0.0025556 | 0.00064048
67 | 0.0012463 | 0.00031235
68 | 0.0018502 | 0.0004637
69 | 0.0028865 | 0.00072341
70 | 0.0017492 | 0.0004384
71 | 0.0035686 | 0.00089437
72 | 0.0016418 | 0.00041148
73 | 0.0040125 | 0.0010056
74 | 0.0010686 | 0.00026782

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1