## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2527-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2527-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2527-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2527-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2527-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2527-4_0_4_node_44 | 0.4 | n |  | TRUE
6 | bus_LV_2527-4_0_4_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_2527-4_0_4_node_43 | 0.4 | n |  | TRUE
8 | bus_LV_2527-4_0_4_node_99 | 0.4 | n |  | TRUE
9 | bus_LV_2527-4_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2527-4_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2527-4_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2527-4_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2527-4_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2527-4_0_4_node_124 | 0.4 | n |  | TRUE
15 | bus_LV_2527-4_0_4_node_74 | 0.4 | n |  | TRUE
16 | bus_LV_2527-4_0_4_node_73 | 0.4 | n |  | TRUE
17 | bus_LV_2527-4_0_4_node_125 | 0.4 | n |  | TRUE
18 | bus_LV_2527-4_0_4_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_2527-4_0_4_node_113 | 0.4 | n |  | TRUE
20 | bus_LV_2527-4_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_2527-4_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2527-4_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2527-4_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2527-4_0_4_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_2527-4_0_4_node_39 | 0.4 | n |  | TRUE
26 | bus_LV_2527-4_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_2527-4_0_4_node_54 | 0.4 | n |  | TRUE
28 | bus_LV_2527-4_0_4_node_130 | 0.4 | n |  | TRUE
29 | bus_LV_2527-4_0_4_node_40 | 0.4 | n |  | TRUE
30 | bus_LV_2527-4_0_4_node_55 | 0.4 | n |  | TRUE
31 | bus_LV_2527-4_0_4_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_2527-4_0_4_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_2527-4_0_4_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_2527-4_0_4_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_2527-4_0_4_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_2527-4_0_4_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_2527-4_0_4_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_2527-4_0_4_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_2527-4_0_4_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_2527-4_0_4_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_2527-4_0_4_node_63 | 0.4 | n |  | TRUE
42 | bus_LV_2527-4_0_4_node_51 | 0.4 | n |  | TRUE
43 | bus_LV_2527-4_0_4_node_61 | 0.4 | n |  | TRUE
44 | bus_LV_2527-4_0_4_node_21 | 0.4 | n |  | TRUE
45 | bus_LV_2527-4_0_4_node_22 | 0.4 | n |  | TRUE
46 | bus_LV_2527-4_0_4_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_2527-4_0_4_node_24 | 0.4 | n |  | TRUE
48 | bus_LV_2527-4_0_4_node_53 | 0.4 | n |  | TRUE
49 | bus_LV_2527-4_0_4_node_66 | 0.4 | n |  | TRUE
50 | bus_LV_2527-4_0_4_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_2527-4_0_4_node_120 | 0.4 | n |  | TRUE
52 | bus_LV_2527-4_0_4_node_50 | 0.4 | n |  | TRUE
53 | bus_LV_2527-4_0_4_node_86 | 0.4 | n |  | TRUE
54 | bus_LV_2527-4_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_2527-4_0_4_node_137 | 0.4 | n |  | TRUE
56 | bus_LV_2527-4_0_4_node_26 | 0.4 | n |  | TRUE
57 | bus_LV_2527-4_0_4_node_27 | 0.4 | n |  | TRUE
58 | bus_LV_2527-4_0_4_node_28 | 0.4 | n |  | TRUE
59 | bus_LV_2527-4_0_4_node_29 | 0.4 | n |  | TRUE
60 | bus_LV_2527-4_0_4_node_30 | 0.4 | n |  | TRUE
61 | bus_LV_2527-4_0_4_node_75 | 0.4 | n |  | TRUE
62 | bus_LV_2527-4_0_4_node_72 | 0.4 | n |  | TRUE
63 | bus_LV_2527-4_0_4_node_76 | 0.4 | n |  | TRUE
64 | bus_LV_2527-4_0_4_node_65 | 0.4 | n |  | TRUE
65 | bus_LV_2527-4_0_4_node_34 | 0.4 | n |  | TRUE
66 | bus_LV_2527-4_0_4_node_36 | 0.4 | n |  | TRUE
67 | bus_LV_2527-4_0_4_node_83 | 0.4 | n |  | TRUE
68 | bus_LV_2527-4_0_4_node_136 | 0.4 | n |  | TRUE
69 | bus_LV_2527-4_0_4_node_84 | 0.4 | n |  | TRUE
70 | bus_LV_2527-4_0_4_node_135 | 0.4 | n |  | TRUE
71 | bus_LV_2527-4_0_4_node_41 | 0.4 | n |  | TRUE
72 | bus_LV_2527-4_0_4_node_126 | 0.4 | n |  | TRUE
73 | bus_LV_2527-4_0_4_node_134 | 0.4 | n |  | TRUE
74 | bus_LV_2527-4_0_4_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_2527-4_0_4_node_45 | 0.4 | n |  | TRUE
76 | bus_LV_2527-4_0_4_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_2527-4_0_4_node_128 | 0.4 | n |  | TRUE
78 | bus_LV_2527-4_0_4_node_127 | 0.4 | n |  | TRUE
79 | bus_LV_2527-4_0_4_node_131 | 0.4 | n |  | TRUE
80 | bus_LV_2527-4_0_4_node_49 | 0.4 | n |  | TRUE
81 | bus_LV_2527-4_0_4_node_119 | 0.4 | n |  | TRUE
82 | bus_LV_2527-4_0_4_node_85 | 0.4 | n |  | TRUE
83 | bus_LV_2527-4_0_4_node_103 | 0.4 | n |  | TRUE
84 | bus_LV_2527-4_0_4_node_104 | 0.4 | n |  | TRUE
85 | bus_LV_2527-4_0_4_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_2527-4_0_4_node_57 | 0.4 | n |  | TRUE
87 | bus_LV_2527-4_0_4_node_58 | 0.4 | n |  | TRUE
88 | bus_LV_2527-4_0_4_node_59 | 0.4 | n |  | TRUE
89 | bus_LV_2527-4_0_4_node_106 | 0.4 | n |  | TRUE
90 | bus_LV_2527-4_0_4_node_107 | 0.4 | n |  | TRUE
91 | bus_LV_2527-4_0_4_node_62 | 0.4 | n |  | TRUE
92 | bus_LV_2527-4_0_4_node_64 | 0.4 | n |  | TRUE
93 | bus_LV_2527-4_0_4_node_100 | 0.4 | n |  | TRUE
94 | bus_LV_2527-4_0_4_node_111 | 0.4 | n |  | TRUE
95 | bus_LV_2527-4_0_4_node_67 | 0.4 | n |  | TRUE
96 | bus_LV_2527-4_0_4_node_68 | 0.4 | n |  | TRUE
97 | bus_LV_2527-4_0_4_node_69 | 0.4 | n |  | TRUE
98 | bus_LV_2527-4_0_4_node_70 | 0.4 | n |  | TRUE
99 | bus_LV_2527-4_0_4_node_71 | 0.4 | n |  | TRUE
100 | bus_LV_2527-4_0_4_node_97 | 0.4 | n |  | TRUE
101 | bus_LV_2527-4_0_4_node_92 | 0.4 | n |  | TRUE
102 | bus_LV_2527-4_0_4_node_123 | 0.4 | n |  | TRUE
103 | bus_LV_2527-4_0_4_node_95 | 0.4 | n |  | TRUE
104 | bus_LV_2527-4_0_4_node_90 | 0.4 | n |  | TRUE
105 | bus_LV_2527-4_0_4_node_122 | 0.4 | n |  | TRUE
106 | bus_LV_2527-4_0_4_node_105 | 0.4 | n |  | TRUE
107 | bus_LV_2527-4_0_4_node_77 | 0.4 | n |  | TRUE
108 | bus_LV_2527-4_0_4_node_101 | 0.4 | n |  | TRUE
109 | bus_LV_2527-4_0_4_node_102 | 0.4 | n |  | TRUE
110 | bus_LV_2527-4_0_4_node_78 | 0.4 | n |  | TRUE
111 | bus_LV_2527-4_0_4_node_79 | 0.4 | n |  | TRUE
112 | bus_LV_2527-4_0_4_node_80 | 0.4 | n |  | TRUE
113 | bus_LV_2527-4_0_4_node_81 | 0.4 | n |  | TRUE
114 | bus_LV_2527-4_0_4_node_82 | 0.4 | n |  | TRUE
115 | bus_LV_2527-4_0_4_node_87 | 0.4 | n |  | TRUE
116 | bus_LV_2527-4_0_4_node_88 | 0.4 | n |  | TRUE
117 | bus_LV_2527-4_0_4_node_89 | 0.4 | n |  | TRUE
118 | bus_LV_2527-4_0_4_node_93 | 0.4 | n |  | TRUE
119 | bus_LV_2527-4_0_4_node_94 | 0.4 | n |  | TRUE
120 | bus_LV_2527-4_0_4_node_96 | 0.4 | n |  | TRUE
121 | bus_LV_2527-4_0_4_node_98 | 0.4 | n |  | TRUE
122 | bus_LV_2527-4_0_4_node_112 | 0.4 | n |  | TRUE
123 | bus_LV_2527-4_0_4_node_108 | 0.4 | n |  | TRUE
124 | bus_LV_2527-4_0_4_node_121 | 0.4 | n |  | TRUE
125 | bus_LV_2527-4_0_4_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_2527-4_0_4_node_116 | 0.4 | n |  | TRUE
127 | bus_LV_2527-4_0_4_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_2527-4_0_4_node_114 | 0.4 | n |  | TRUE
129 | bus_LV_2527-4_0_4_node_129 | 0.4 | n |  | TRUE
130 | bus_LV_2527-4_0_4_node_132 | 0.4 | n |  | TRUE
131 | bus_LV_2527-4_0_4_node_133 | 0.4 | n |  | TRUE
132 | bus_MV_392_0_node_54 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2527-4_0_4_load_0 | 0 | 0.0014181 | 0.00035541 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2527-4_0_4_load_1 | 1 | 0.0016377 | 0.00041044 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2527-4_0_4_load_2 | 2 | 0.0038482 | 0.00096444 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2527-4_0_4_load_3 | 3 | 0.0031118 | 0.0007799 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2527-4_0_4_load_4 | 4 | 0.0019311 | 0.00048398 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2527-4_0_4_load_44 | 5 | 0.0025834 | 0.00064747 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2527-4_0_4_load_43 | 7 | 0.0019186 | 0.00048085 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2527-4_0_4_load_5 | 9 | 0.00176 | 0.0004411 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2527-4_0_4_load_6 | 10 | 0.0019783 | 0.00049582 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2527-4_0_4_load_7 | 11 | 0.0020851 | 0.00052257 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2527-4_0_4_load_8 | 12 | 0.0014533 | 0.00036422 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2527-4_0_4_load_74 | 15 | 0.0007654 | 0.00019183 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2527-4_0_4_load_73 | 16 | 0.0014533 | 0.00036422 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2527-4_0_4_load_47 | 18 | 0.0062791 | 0.0015737 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2527-4_0_4_load_113 | 19 | 0.001522 | 0.00038144 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2527-4_0_4_load_10 | 20 | 0.00040006 | 0.00010026 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2527-4_0_4_load_11 | 21 | 0.00022511 | 5.6417e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2527-4_0_4_load_12 | 22 | 0.0031699 | 0.00079445 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2527-4_0_4_load_39 | 25 | 0.00025438 | 6.3754e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2527-4_0_4_load_14 | 26 | 0.0013979 | 0.00035035 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2527-4_0_4_load_54 | 27 | 0.00015633 | 3.918e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2527-4_0_4_load_130 | 28 | 0.00038293 | 9.5971e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2527-4_0_4_load_40 | 29 | 0.00043181 | 0.00010822 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2527-4_0_4_load_55 | 30 | 0.0013031 | 0.00032659 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2527-4_0_4_load_15 | 31 | 0.009935 | 0.0024899 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2527-4_0_4_load_16 | 32 | 0.0077075 | 0.0019317 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2527-4_0_4_load_18 | 33 | 0.0031985 | 0.00080162 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2527-4_0_4_load_19 | 35 | 0.018164 | 0.0045524 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2527-4_0_4_load_37 | 38 | 0.01094 | 0.0027419 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2527-4_0_4_load_38 | 39 | 0.0053929 | 0.0013516 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2527-4_0_4_load_33 | 40 | 0.0045655 | 0.0011442 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2527-4_0_4_load_61 | 43 | 0.018774 | 0.0047052 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2527-4_0_4_load_21 | 44 | 0.00035666 | 8.9388e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2527-4_0_4_load_22 | 45 | 0.0024382 | 0.00061107 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2527-4_0_4_load_23 | 46 | 0.00028445 | 7.129e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2527-4_0_4_load_66 | 49 | 0.0032287 | 0.00080919 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2527-4_0_4_load_120 | 51 | 0.0013912 | 0.00034867 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2527-4_0_4_load_86 | 53 | 0.0080565 | 0.0020192 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2527-4_0_4_load_48 | 54 | 0.0042961 | 0.0010767 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2527-4_0_4_load_137 | 55 | 0.0038399 | 0.00096237 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2527-4_0_4_load_26 | 56 | 0.0027217 | 0.00068212 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2527-4_0_4_load_27 | 57 | 0.0028066 | 0.0007034 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2527-4_0_4_load_28 | 58 | 0.0023525 | 0.00058959 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2527-4_0_4_load_29 | 59 | 0.0010334 | 0.00025898 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2527-4_0_4_load_30 | 60 | 0.0056091 | 0.0014058 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2527-4_0_4_load_75 | 61 | 0.0033089 | 0.00082928 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2527-4_0_4_load_72 | 62 | 0.062678 | 0.015708 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2527-4_0_4_load_76 | 63 | 0.003446 | 0.00086364 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2527-4_0_4_load_34 | 65 | 0.0033245 | 0.00083319 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2527-4_0_4_load_36 | 66 | 0.0021845 | 0.00054748 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2527-4_0_4_load_83 | 67 | 0.0019461 | 0.00048774 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2527-4_0_4_load_136 | 68 | 0.0010605 | 0.00026579 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2527-4_0_4_load_84 | 69 | 0.0021866 | 0.00054801 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2527-4_0_4_load_135 | 70 | 0.0058234 | 0.0014595 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2527-4_0_4_load_134 | 73 | 0.00068376 | 0.00017137 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2527-4_0_4_load_60 | 74 | 0.00023206 | 5.8161e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2527-4_0_4_load_128 | 77 | 0.0010844 | 0.00027177 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2527-4_0_4_load_127 | 78 | 0.0069778 | 0.0017488 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2527-4_0_4_load_131 | 79 | 0.0067756 | 0.0016981 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2527-4_0_4_load_49 | 80 | 0.0070838 | 0.0017754 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2527-4_0_4_load_119 | 81 | 0.044471 | 0.011145 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2527-4_0_4_load_85 | 82 | 0.0042088 | 0.0010548 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2527-4_0_4_load_103 | 83 | 0.0018121 | 0.00045414 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2527-4_0_4_load_104 | 84 | 0.0036075 | 0.00090413 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2527-4_0_4_load_56 | 85 | 0.0020958 | 0.00052526 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2527-4_0_4_load_57 | 86 | 0.0025852 | 0.00064792 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2527-4_0_4_load_58 | 87 | 0.0029613 | 0.00074216 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2527-4_0_4_load_59 | 88 | 0.0024866 | 0.00062319 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2527-4_0_4_load_106 | 89 | 0.0017524 | 0.00043919 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2527-4_0_4_load_62 | 91 | 0.015201 | 0.0038096 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2527-4_0_4_load_64 | 92 | 0.0014266 | 0.00035755 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2527-4_0_4_load_100 | 93 | 0.026352 | 0.0066045 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2527-4_0_4_load_111 | 94 | 0.0043831 | 0.0010985 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2527-4_0_4_load_67 | 95 | 0.002797 | 0.00070101 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2527-4_0_4_load_68 | 96 | 0.0022815 | 0.00057181 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2527-4_0_4_load_69 | 97 | 0.0010059 | 0.00025211 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2527-4_0_4_load_71 | 99 | 0.0010036 | 0.00025152 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2527-4_0_4_load_97 | 100 | 0.0071003 | 0.0017795 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2527-4_0_4_load_92 | 101 | 0.0045563 | 0.0011419 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2527-4_0_4_load_90 | 104 | 0.0038873 | 0.00097424 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2527-4_0_4_load_122 | 105 | 0.0013851 | 0.00034713 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2527-4_0_4_load_77 | 107 | 0.0013175 | 0.00033019 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2527-4_0_4_load_102 | 109 | 0.0033542 | 0.00084063 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2527-4_0_4_load_78 | 110 | 0.0013901 | 0.00034839 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2527-4_0_4_load_79 | 111 | 0.0015376 | 0.00038536 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2527-4_0_4_load_80 | 112 | 0.0013313 | 0.00033365 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2527-4_0_4_load_81 | 113 | 0.0029977 | 0.0007513 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2527-4_0_4_load_82 | 114 | 0.0021496 | 0.00053875 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2527-4_0_4_load_87 | 115 | 0.0040083 | 0.0010046 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2527-4_0_4_load_88 | 116 | 0.0030276 | 0.00075879 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2527-4_0_4_load_89 | 117 | 0.0019196 | 0.0004811 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2527-4_0_4_load_93 | 118 | 0.0021848 | 0.00054755 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2527-4_0_4_load_94 | 119 | 0.0022899 | 0.00057389 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2527-4_0_4_load_98 | 121 | 0.0016319 | 0.000409 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2527-4_0_4_load_112 | 122 | 0.0032052 | 0.00080329 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2527-4_0_4_load_108 | 123 | 0.0036609 | 0.00091751 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2527-4_0_4_load_121 | 124 | 0.0013959 | 0.00034986 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2527-4_0_4_load_109 | 125 | 0.0041663 | 0.0010442 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2527-4_0_4_load_116 | 126 | 0.0032591 | 0.0008168 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2527-4_0_4_load_115 | 127 | 0.0026009 | 0.00065184 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2527-4_0_4_load_114 | 128 | 0.0024556 | 0.00061543 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2527-4_0_4_load_129 | 129 | 0.011106 | 0.0027833 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2527-4_0_4_load_132 | 130 | 0.0013058 | 0.00032727 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2527-4_0_4_load_133 | 131 | 0.0013574 | 0.00034019 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 91 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2527-4_0_4_line_0 |  | 0 | 1 | 0.0088742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2527-4_0_4_line_1 |  | 0 | 2 | 0.018135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2527-4_0_4_line_2 |  | 1 | 3 | 0.005585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2527-4_0_4_line_3 |  | 2 | 4 | 0.00025204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2527-4_0_4_line_4 |  | 3 | 5 | 0.024081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2527-4_0_4_line_5 |  | 4 | 6 | 0.014199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2527-4_0_4_line_6 |  | 5 | 7 | 0.00295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2527-4_0_4_line_7 |  | 6 | 8 | 0.055206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2527-4_0_4_line_8 |  | 7 | 75 | 0.016718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2527-4_0_4_line_9 |  | 8 | 55 | 0.061366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2527-4_0_4_line_10 |  | 9 | 10 | 0.0087927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2527-4_0_4_line_11 |  | 9 | 11 | 0.038666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2527-4_0_4_line_12 |  | 10 | 12 | 0.0071272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2527-4_0_4_line_13 |  | 11 | 13 | 0.0060572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2527-4_0_4_line_14 |  | 12 | 14 | 0.031212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2527-4_0_4_line_15 |  | 13 | 15 | 0.02529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2527-4_0_4_line_16 |  | 13 | 16 | 0.018712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2527-4_0_4_line_17 |  | 14 | 17 | 0.008171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2527-4_0_4_line_18 |  | 14 | 18 | 0.0068144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2527-4_0_4_line_19 |  | 15 | 19 | 0.0063634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2527-4_0_4_line_20 |  | 17 | 129 | 0.014627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2527-4_0_4_line_21 |  | 18 | 75 | 0.0046005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2527-4_0_4_line_22 |  | 20 | 21 | 0.016635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2527-4_0_4_line_23 |  | 20 | 22 | 0.025158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2527-4_0_4_line_24 |  | 21 | 23 | 0.033168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2527-4_0_4_line_25 |  | 23 | 24 | 0.028671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2527-4_0_4_line_26 |  | 23 | 25 | 0.02055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2527-4_0_4_line_27 |  | 24 | 28 | 0.021878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2527-4_0_4_line_28 |  | 25 | 29 | 0.0058776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2527-4_0_4_line_29 |  | 26 | 27 | 0.0007192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2527-4_0_4_line_30 |  | 27 | 30 | 0.018818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2527-4_0_4_line_31 |  | 29 | 71 | 0.0074476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2527-4_0_4_line_32 |  | 30 | 83 | 0.018929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2527-4_0_4_line_33 |  | 31 | 32 | 0.0069018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2527-4_0_4_line_34 |  | 32 | 33 | 0.018959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2527-4_0_4_line_35 |  | 33 | 34 | 0.0025554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2527-4_0_4_line_36 |  | 34 | 37 | 0.016514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2527-4_0_4_line_37 |  | 35 | 36 | 0.023172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2527-4_0_4_line_38 |  | 36 | 38 | 0.01975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2527-4_0_4_line_39 |  | 36 | 39 | 0.041997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2527-4_0_4_line_40 |  | 36 | 40 | 0.024357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2527-4_0_4_line_41 |  | 37 | 38 | 0.0082928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2527-4_0_4_line_42 |  | 39 | 68 | 0.0099477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2527-4_0_4_line_43 |  | 40 | 65 | 0.02988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2527-4_0_4_line_44 |  | 41 | 42 | 0.009889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2527-4_0_4_line_45 |  | 41 | 43 | 0.023698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2527-4_0_4_line_46 |  | 42 | 81 | 0.009516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2527-4_0_4_line_47 |  | 42 | 80 | 0.010629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2527-4_0_4_line_48 |  | 43 | 91 | 0.034846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2527-4_0_4_line_49 |  | 44 | 45 | 0.0022961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2527-4_0_4_line_50 |  | 44 | 46 | 0.0057761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2527-4_0_4_line_51 |  | 46 | 47 | 0.034055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2527-4_0_4_line_52 |  | 47 | 48 | 0.0077275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2527-4_0_4_line_53 |  | 47 | 49 | 0.023623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2527-4_0_4_line_54 |  | 48 | 53 | 0.028468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2527-4_0_4_line_55 |  | 48 | 52 | 0.015883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2527-4_0_4_line_56 |  | 50 | 51 | 0.0089618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2527-4_0_4_line_57 |  | 50 | 52 | 0.009598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2527-4_0_4_line_58 |  | 52 | 54 | 0.010399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2527-4_0_4_line_59 |  | 53 | 82 | 0.0032081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2527-4_0_4_line_60 |  | 54 | 80 | 0.029475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2527-4_0_4_line_61 |  | 56 | 57 | 0.00044439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2527-4_0_4_line_62 |  | 56 | 58 | 0.019516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2527-4_0_4_line_63 |  | 57 | 59 | 0.00023388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_2527-4_0_4_line_64 |  | 58 | 60 | 0.012738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2527-4_0_4_line_65 |  | 59 | 61 | 0.020546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_2527-4_0_4_line_66 |  | 60 | 62 | 0.011423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2527-4_0_4_line_67 |  | 61 | 63 | 0.0014192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2527-4_0_4_line_68 |  | 62 | 64 | 0.016958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2527-4_0_4_line_69 |  | 63 | 107 | 0.026214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_2527-4_0_4_line_70 |  | 64 | 78 | 0.0097555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2527-4_0_4_line_71 |  | 65 | 66 | 0.0037126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2527-4_0_4_line_72 |  | 66 | 67 | 0.016922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2527-4_0_4_line_73 |  | 67 | 69 | 0.0073526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2527-4_0_4_line_74 |  | 68 | 70 | 0.0097338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2527-4_0_4_line_75 |  | 69 | 98 | 0.040346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2527-4_0_4_line_76 |  | 71 | 72 | 0.021647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2527-4_0_4_line_77 |  | 71 | 73 | 0.010854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2527-4_0_4_line_78 |  | 72 | 74 | 0.023105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2527-4_0_4_line_79 |  | 74 | 87 | 0.010888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2527-4_0_4_line_80 |  | 75 | 76 | 0.029759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2527-4_0_4_line_81 |  | 76 | 77 | 0.017526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2527-4_0_4_line_82 |  | 76 | 78 | 0.026978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2527-4_0_4_line_83 |  | 77 | 79 | 0.010637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2527-4_0_4_line_84 |  | 79 | 130 | 0.028022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2527-4_0_4_line_85 |  | 82 | 115 | 0.0031083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2527-4_0_4_line_86 |  | 83 | 84 | 0.004663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2527-4_0_4_line_87 |  | 84 | 106 | 0.015021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2527-4_0_4_line_88 |  | 85 | 86 | 0.0019697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2527-4_0_4_line_89 |  | 85 | 87 | 0.0034675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2527-4_0_4_line_90 |  | 86 | 88 | 0.019799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2527-4_0_4_line_91 |  | 88 | 89 | 0.00024115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2527-4_0_4_line_92 |  | 89 | 90 | 0.012488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2527-4_0_4_line_93 |  | 90 | 126 | 0.012479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2527-4_0_4_line_94 |  | 90 | 106 | 0.024767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2527-4_0_4_line_95 |  | 91 | 92 | 0.028029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_2527-4_0_4_line_96 |  | 92 | 93 | 0.0056774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_2527-4_0_4_line_97 |  | 93 | 94 | 0.01992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_2527-4_0_4_line_98 |  | 94 | 120 | 0.017501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_2527-4_0_4_line_99 |  | 95 | 96 | 0.0030145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2527-4_0_4_line_100 |  | 95 | 97 | 0.023444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2527-4_0_4_line_101 |  | 96 | 98 | 0.017472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2527-4_0_4_line_102 |  | 97 | 99 | 0.0072533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2527-4_0_4_line_103 |  | 98 | 100 | 0.018395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2527-4_0_4_line_104 |  | 98 | 101 | 0.020019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2527-4_0_4_line_105 |  | 99 | 102 | 0.015598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2527-4_0_4_line_106 |  | 100 | 103 | 0.017511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_2527-4_0_4_line_107 |  | 101 | 104 | 0.027106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2527-4_0_4_line_108 |  | 102 | 105 | 0.026435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2527-4_0_4_line_109 |  | 102 | 106 | 0.015514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2527-4_0_4_line_110 |  | 103 | 121 | 0.041325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2527-4_0_4_line_111 |  | 103 | 118 | 0.011428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_2527-4_0_4_line_112 |  | 104 | 117 | 0.018639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2527-4_0_4_line_113 |  | 105 | 114 | 0.0066604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2527-4_0_4_line_114 |  | 107 | 108 | 0.012408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_2527-4_0_4_line_115 |  | 108 | 109 | 0.018433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_2527-4_0_4_line_116 |  | 109 | 124 | 0.0017793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_2527-4_0_4_line_117 |  | 110 | 111 | 0.002701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2527-4_0_4_line_118 |  | 110 | 112 | 0.014366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2527-4_0_4_line_119 |  | 111 | 113 | 0.0078789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2527-4_0_4_line_120 |  | 112 | 114 | 0.0065272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2527-4_0_4_line_121 |  | 115 | 116 | 0.032121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2527-4_0_4_line_122 |  | 118 | 119 | 0.002378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_2527-4_0_4_line_123 |  | 119 | 120 | 0.027121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_2527-4_0_4_line_124 |  | 120 | 122 | 0.013884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
125 | LV_2527-4_0_4_line_125 |  | 120 | 123 | 0.016786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2527-4_0_4_line_126 |  | 122 | 124 | 0.022369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_2527-4_0_4_line_127 |  | 123 | 125 | 0.019606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2527-4_0_4_line_128 |  | 126 | 127 | 0.034426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2527-4_0_4_line_129 |  | 127 | 128 | 0.02011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2527-4_0_4_line_130 |  | 130 | 131 | 0.0045628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2527-4_0_4_trafo_62 | 0.63 MVA 20/0.4 kV | 132 | 91 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2611373.1426 | 1229362.2521 | 2611364.5961 | 1229359.8628
1 | 2611373.1426 | 1229362.2521 | 2611390.6077 | 1229367.1349
2 | 2611359.2174 | 1229358.3591 | 2611364.5961 | 1229359.8628
3 | 2611390.6077 | 1229367.1349 | 2611390.8504 | 1229367.2027
4 | 2611359.2174 | 1229358.3591 | 2611348.8692 | 1229355.466 | 2611343.3501 | 1229353.7546 | 2611336.4314 | 1229350.7141
5 | 2611404.5247 | 1229371.0256 | 2611390.8504 | 1229367.2027
6 | 2611333.7306 | 1229349.5272 | 2611336.4314 | 1229350.7141
7 | 2611457.8252 | 1229385.9697 | 2611404.5247 | 1229371.0256
8 | 2611318.4258 | 1229342.8008 | 2611321.8545 | 1229344.3082 | 2611333.7306 | 1229349.5272
9 | 2611457.8252 | 1229385.9697 | 2611474.1344 | 1229326.8102
10 | 2611348.2375 | 1229306.5084 | 2611348.9068 | 1229307.7377 | 2611350.4005 | 1229314.9782 | 2611350.4005 | 1229314.9782
11 | 2611348.2375 | 1229306.5084 | 2611342.9205 | 1229296.742 | 2611341.4386 | 1229287.2558 | 2611342.4557 | 1229274.2055 | 2611343.3781 | 1229269.4389
12 | 2611348.9555 | 1229321.9574 | 2611350.4005 | 1229314.9782
13 | 2611344.5289 | 1229263.492 | 2611343.3781 | 1229269.4389
14 | 2611321.1738 | 1229331.7217 | 2611325.2041 | 1229331.6181 | 2611337.0068 | 1229331.3181 | 2611343.6117 | 1229327.6951 | 2611348.9555 | 1229321.9574
15 | 2611344.5289 | 1229263.492 | 2611353.2695 | 1229239.7605
16 | 2611344.5289 | 1229263.492 | 2611341.5833 | 1229262.9083 | 2611327.9701 | 1229255.0694
17 | 2611321.1738 | 1229331.7217 | 2611320.1018 | 1229325.805 | 2611319.386 | 1229323.7691
18 | 2611321.1738 | 1229331.7217 | 2611319.5333 | 1229338.3357
19 | 2611355.4688 | 1229233.7893 | 2611353.2695 | 1229239.7605
20 | 2611319.386 | 1229323.7691 | 2611325.802 | 1229319.9012 | 2611321.0578 | 1229314.5711
21 | 2611318.4258 | 1229342.8008 | 2611319.5333 | 1229338.3357
22 | 2610962.815 | 1229511.6688 | 2610955.428 | 1229526.5736
23 | 2610962.815 | 1229511.6688 | 2610973.987 | 1229489.1272
24 | 2610940.6993 | 1229556.2917 | 2610955.428 | 1229526.5736
25 | 2610915.5001 | 1229542.4819 | 2610940.6993 | 1229556.2917
26 | 2610940.6993 | 1229556.2917 | 2610958.7221 | 1229566.1649
27 | 2610915.5001 | 1229542.4819 | 2610925.3501 | 1229522.9462
28 | 2610963.8769 | 1229568.9888 | 2610958.7221 | 1229566.1649
29 | 2611010.5358 | 1229488.5632 | 2611011.1545 | 1229488.9299
30 | 2611027.3428 | 1229498.5245 | 2611011.1545 | 1229488.9299
31 | 2610970.4086 | 1229572.567 | 2610963.8769 | 1229568.9888
32 | 2611043.6261 | 1229508.1754 | 2611027.3428 | 1229498.5245
33 | 2611263.9651 | 1229525.0732 | 2611267.4491 | 1229529.3489 | 2611267.2195 | 1229530.7162
34 | 2611264.0801 | 1229549.4129 | 2611267.2195 | 1229530.7162
35 | 2611263.6569 | 1229551.933 | 2611264.0801 | 1229549.4129
36 | 2611263.6569 | 1229551.933 | 2611247.156 | 1229553.3584
37 | 2611224.9786 | 1229536.1954 | 2611239.6476 | 1229518.2577
38 | 2611224.9786 | 1229536.1954 | 2611240.5978 | 1229548.283
39 | 2611224.9786 | 1229536.1954 | 2611198.4147 | 1229568.7234
40 | 2611224.9786 | 1229536.1954 | 2611204.2782 | 1229523.36
41 | 2611247.156 | 1229553.3584 | 2611240.5978 | 1229548.283
42 | 2611192.1226 | 1229576.4283 | 2611198.4147 | 1229568.7234
43 | 2611178.8839 | 1229507.6141 | 2611204.2782 | 1229523.36
44 | 2611287.5771 | 1229460.4681 | 2611282.5804 | 1229458.9578 | 2611279.6557 | 1229455.2945
45 | 2611279.6557 | 1229455.2945 | 2611273.1494 | 1229454.9487 | 2611271.6876 | 1229454.8681 | 2611257.5695 | 1229447.9571
46 | 2611287.5771 | 1229460.4681 | 2611287.7468 | 1229466.8722 | 2611290.5369 | 1229468.2452
47 | 2611287.5771 | 1229460.4681 | 2611297.6442 | 1229463.8794
48 | 2611257.5695 | 1229447.9571 | 2611226.272 | 1229432.6366
49 | 2611326.2477 | 1229528.4039 | 2611328.0316 | 1229529.8495
50 | 2611326.2477 | 1229528.4039 | 2611326.2477 | 1229528.4039 | 2611328.671 | 1229523.1607
51 | 2611342.9585 | 1229492.2474 | 2611328.671 | 1229523.1607
52 | 2611347.4494 | 1229488.865 | 2611345.0807 | 1229487.6486 | 2611342.9585 | 1229492.2474
53 | 2611342.9585 | 1229492.2474 | 2611359.8071 | 1229499.2946 | 2611364.8316 | 1229501.1614
54 | 2611347.4494 | 1229488.865 | 2611349.3954 | 1229485.2443 | 2611360.9202 | 1229463.786
55 | 2611347.4494 | 1229488.865 | 2611345.0807 | 1229487.6486 | 2611339.072 | 1229484.5465 | 2611333.389 | 1229481.4784
56 | 2611324.3985 | 1229484.9078 | 2611316.1427 | 1229488.3943
57 | 2611333.389 | 1229481.4784 | 2611324.3985 | 1229484.9078
58 | 2611333.389 | 1229481.4784 | 2611326.2145 | 1229477.9849 | 2611324.0613 | 1229476.8813
59 | 2611362.4381 | 1229460.9597 | 2611360.9202 | 1229463.786
60 | 2611324.0613 | 1229476.8813 | 2611300.7416 | 1229464.929 | 2611297.6442 | 1229463.8794
61 | 2611239.6898 | 1229377.2143 | 2611239.2931 | 1229377.0142
62 | 2611257.1139 | 1229386.0042 | 2611239.6898 | 1229377.2143
63 | 2611239.2931 | 1229377.0142 | 2611239.0843 | 1229376.9088
64 | 2611257.1139 | 1229386.0042 | 2611268.487 | 1229391.7416
65 | 2611220.7405 | 1229367.655 | 2611239.0843 | 1229376.9088
66 | 2611268.487 | 1229391.7416 | 2611278.6859 | 1229396.8866
67 | 2611220.7405 | 1229367.655 | 2611219.4734 | 1229367.0158
68 | 2611293.8261 | 1229404.5244 | 2611278.6859 | 1229396.8866
69 | 2611196.0691 | 1229355.2091 | 2611219.4734 | 1229367.0158
70 | 2611293.8261 | 1229404.5244 | 2611297.0421 | 1229395.3142
71 | 2611175.6871 | 1229505.7293 | 2611176.8879 | 1229506.3765 | 2611178.8839 | 1229507.6141
72 | 2611175.6871 | 1229505.7293 | 2611160.7906 | 1229497.7006
73 | 2611154.3182 | 1229494.2122 | 2611160.7906 | 1229497.7006
74 | 2611192.1226 | 1229576.4283 | 2611185.9657 | 1229583.9676
75 | 2611125.148 | 1229467.1678 | 2611139.1751 | 1229484.4486 | 2611145.3622 | 1229489.3853 | 2611154.3182 | 1229494.2122
76 | 2610989.4328 | 1229582.997 | 2610970.4086 | 1229572.567
77 | 2610970.4086 | 1229572.567 | 2610967.4661 | 1229578.6096 | 2610965.5161 | 1229582.2537
78 | 2610989.4328 | 1229582.997 | 2611002.828 | 1229565.0109 | 2611003.3622 | 1229564.5924
79 | 2611011.9334 | 1229557.8776 | 2611003.3622 | 1229564.5924
80 | 2611318.4258 | 1229342.8008 | 2611306.2617 | 1229369.9718
81 | 2611306.2617 | 1229369.9718 | 2611291.2253 | 1229360.9689
82 | 2611306.2617 | 1229369.9718 | 2611304.3976 | 1229374.2486 | 2611297.0421 | 1229395.3142
83 | 2611291.2253 | 1229360.9689 | 2611282.0994 | 1229355.5049
84 | 2611258.0574 | 1229341.1099 | 2611282.0994 | 1229355.5049
85 | 2611362.4381 | 1229460.9597 | 2611363.9088 | 1229458.2214
86 | 2611043.6261 | 1229508.1754 | 2611047.6375 | 1229510.5529
87 | 2611060.5597 | 1229518.2117 | 2611047.6375 | 1229510.5529
88 | 2611014.663 | 1229555.7392 | 2611016.2135 | 1229554.5245
89 | 2611014.663 | 1229555.7392 | 2611011.9334 | 1229557.8776
90 | 2611031.7994 | 1229542.3143 | 2611016.2135 | 1229554.5245
91 | 2611031.7994 | 1229542.3143 | 2611031.9893 | 1229542.1656
92 | 2611041.8195 | 1229534.4645 | 2611031.9893 | 1229542.1656
93 | 2611041.8195 | 1229534.4645 | 2611049.531 | 1229544.2758
94 | 2611060.5597 | 1229518.2117 | 2611041.8195 | 1229534.4645
95 | 2611226.272 | 1229432.6366 | 2611201.0979 | 1229420.3134
96 | 2611195.9986 | 1229417.8173 | 2611201.0979 | 1229420.3134
97 | 2611195.9986 | 1229417.8173 | 2611178.1075 | 1229409.0593
98 | 2611162.3885 | 1229401.3647 | 2611178.1075 | 1229409.0593
99 | 2611109.0744 | 1229479.8694 | 2611111.4396 | 1229478.0004
100 | 2611109.0744 | 1229479.8694 | 2611090.68 | 1229494.4048
101 | 2611125.148 | 1229467.1678 | 2611111.4396 | 1229478.0004
102 | 2611090.68 | 1229494.4048 | 2611084.989 | 1229498.9019
103 | 2611125.148 | 1229467.1678 | 2611132.7258 | 1229461.6341 | 2611138.4503 | 1229454.674
104 | 2611125.148 | 1229467.1678 | 2611111.9885 | 1229452.0812
105 | 2611072.7505 | 1229508.573 | 2611084.989 | 1229498.9019
106 | 2611145.6234 | 1229438.7001 | 2611138.4503 | 1229454.674
107 | 2611092.3166 | 1229433.6701 | 2611095.4973 | 1229435.5828 | 2611103.4387 | 1229442.2793 | 2611111.9885 | 1229452.0812
108 | 2611072.7505 | 1229508.573 | 2611096.41 | 1229520.3649
109 | 2611060.5597 | 1229518.2117 | 2611072.7505 | 1229508.573
110 | 2611145.6234 | 1229438.7001 | 2611182.4915 | 1229457.369
111 | 2611145.6234 | 1229438.7001 | 2611150.3048 | 1229428.2748
112 | 2611076.3433 | 1229424.0648 | 2611092.3166 | 1229433.6701
113 | 2611102.3711 | 1229523.3359 | 2611096.41 | 1229520.3649
114 | 2611184.9911 | 1229349.6205 | 2611196.0691 | 1229355.2091
115 | 2611184.9911 | 1229349.6205 | 2611177.6126 | 1229366.5122
116 | 2611177.6126 | 1229366.5122 | 2611176.9003 | 1229368.1427
117 | 2611121.0705 | 1229532.6558 | 2611123.4879 | 1229533.8606
118 | 2611108.2129 | 1229526.2475 | 2611121.0705 | 1229532.6558
119 | 2611130.5395 | 1229537.3752 | 2611123.4879 | 1229533.8606
120 | 2611108.2129 | 1229526.2475 | 2611102.3711 | 1229523.3359
121 | 2611379.1067 | 1229429.9237 | 2611363.9088 | 1229458.2214
122 | 2611150.3048 | 1229428.2748 | 2611151.2789 | 1229426.1054
123 | 2611162.3885 | 1229401.3647 | 2611151.2789 | 1229426.1054
124 | 2611162.3885 | 1229401.3647 | 2611167.9463 | 1229388.6411
125 | 2611162.3885 | 1229401.3647 | 2611153.6555 | 1229396.7123 | 2611147.572 | 1229393.4748
126 | 2611176.9003 | 1229368.1427 | 2611167.9463 | 1229388.6411
127 | 2611147.572 | 1229393.4748 | 2611130.2642 | 1229384.2641
128 | 2611049.531 | 1229544.2758 | 2611055.2788 | 1229551.5885 | 2611064.3545 | 1229559.2543 | 2611075.9284 | 1229565.6948
129 | 2611093.5012 | 1229575.4735 | 2611075.9284 | 1229565.6948
130 | 2611254.1427 | 1229338.766 | 2611258.0574 | 1229341.1099

## bus_geodata
| x | y | coords
0 | 2611373.1426 | 1229362.2521
1 | 2611364.5961 | 1229359.8628
2 | 2611390.6077 | 1229367.1349
3 | 2611359.2174 | 1229358.3591
4 | 2611390.8504 | 1229367.2027
5 | 2611336.4314 | 1229350.7141
6 | 2611404.5247 | 1229371.0256
7 | 2611333.7306 | 1229349.5272
8 | 2611457.8252 | 1229385.9697
9 | 2611348.2375 | 1229306.5084
10 | 2611350.4005 | 1229314.9782
11 | 2611343.3781 | 1229269.4389
12 | 2611348.9555 | 1229321.9574
13 | 2611344.5289 | 1229263.492
14 | 2611321.1738 | 1229331.7217
15 | 2611353.2695 | 1229239.7605
16 | 2611327.9701 | 1229255.0694
17 | 2611319.386 | 1229323.7691
18 | 2611319.5333 | 1229338.3357
19 | 2611355.4688 | 1229233.7893
20 | 2610962.815 | 1229511.6688
21 | 2610955.428 | 1229526.5736
22 | 2610973.987 | 1229489.1272
23 | 2610940.6993 | 1229556.2917
24 | 2610915.5001 | 1229542.4819
25 | 2610958.7221 | 1229566.1649
26 | 2611010.5358 | 1229488.5632
27 | 2611011.1545 | 1229488.9299
28 | 2610925.3501 | 1229522.9462
29 | 2610963.8769 | 1229568.9888
30 | 2611027.3428 | 1229498.5245
31 | 2611263.9651 | 1229525.0732
32 | 2611267.2195 | 1229530.7162
33 | 2611264.0801 | 1229549.4129
34 | 2611263.6569 | 1229551.933
35 | 2611239.6476 | 1229518.2577
36 | 2611224.9786 | 1229536.1954
37 | 2611247.156 | 1229553.3584
38 | 2611240.5978 | 1229548.283
39 | 2611198.4147 | 1229568.7234
40 | 2611204.2782 | 1229523.36
41 | 2611279.6557 | 1229455.2945
42 | 2611287.5771 | 1229460.4681
43 | 2611257.5695 | 1229447.9571
44 | 2611326.2477 | 1229528.4039
45 | 2611328.0316 | 1229529.8495
46 | 2611328.671 | 1229523.1607
47 | 2611342.9585 | 1229492.2474
48 | 2611347.4494 | 1229488.865
49 | 2611364.8316 | 1229501.1614
50 | 2611324.3985 | 1229484.9078
51 | 2611316.1427 | 1229488.3943
52 | 2611333.389 | 1229481.4784
53 | 2611360.9202 | 1229463.786
54 | 2611324.0613 | 1229476.8813
55 | 2611474.1344 | 1229326.8102
56 | 2611239.6898 | 1229377.2143
57 | 2611239.2931 | 1229377.0142
58 | 2611257.1139 | 1229386.0042
59 | 2611239.0843 | 1229376.9088
60 | 2611268.487 | 1229391.7416
61 | 2611220.7405 | 1229367.655
62 | 2611278.6859 | 1229396.8866
63 | 2611219.4734 | 1229367.0158
64 | 2611293.8261 | 1229404.5244
65 | 2611178.8839 | 1229507.6141
66 | 2611175.6871 | 1229505.7293
67 | 2611160.7906 | 1229497.7006
68 | 2611192.1226 | 1229576.4283
69 | 2611154.3182 | 1229494.2122
70 | 2611185.9657 | 1229583.9676
71 | 2610970.4086 | 1229572.567
72 | 2610989.4328 | 1229582.997
73 | 2610965.5161 | 1229582.2537
74 | 2611003.3622 | 1229564.5924
75 | 2611318.4258 | 1229342.8008
76 | 2611306.2617 | 1229369.9718
77 | 2611291.2253 | 1229360.9689
78 | 2611297.0421 | 1229395.3142
79 | 2611282.0994 | 1229355.5049
80 | 2611297.6442 | 1229463.8794
81 | 2611290.5369 | 1229468.2452
82 | 2611362.4381 | 1229460.9597
83 | 2611043.6261 | 1229508.1754
84 | 2611047.6375 | 1229510.5529
85 | 2611014.663 | 1229555.7392
86 | 2611016.2135 | 1229554.5245
87 | 2611011.9334 | 1229557.8776
88 | 2611031.7994 | 1229542.3143
89 | 2611031.9893 | 1229542.1656
90 | 2611041.8195 | 1229534.4645
91 | 2611226.272 | 1229432.6366
92 | 2611201.0979 | 1229420.3134
93 | 2611195.9986 | 1229417.8173
94 | 2611178.1075 | 1229409.0593
95 | 2611109.0744 | 1229479.8694
96 | 2611111.4396 | 1229478.0004
97 | 2611090.68 | 1229494.4048
98 | 2611125.148 | 1229467.1678
99 | 2611084.989 | 1229498.9019
100 | 2611138.4503 | 1229454.674
101 | 2611111.9885 | 1229452.0812
102 | 2611072.7505 | 1229508.573
103 | 2611145.6234 | 1229438.7001
104 | 2611092.3166 | 1229433.6701
105 | 2611096.41 | 1229520.3649
106 | 2611060.5597 | 1229518.2117
107 | 2611196.0691 | 1229355.2091
108 | 2611184.9911 | 1229349.6205
109 | 2611177.6126 | 1229366.5122
110 | 2611121.0705 | 1229532.6558
111 | 2611123.4879 | 1229533.8606
112 | 2611108.2129 | 1229526.2475
113 | 2611130.5395 | 1229537.3752
114 | 2611102.3711 | 1229523.3359
115 | 2611363.9088 | 1229458.2214
116 | 2611379.1067 | 1229429.9237
117 | 2611076.3433 | 1229424.0648
118 | 2611150.3048 | 1229428.2748
119 | 2611151.2789 | 1229426.1054
120 | 2611162.3885 | 1229401.3647
121 | 2611182.4915 | 1229457.369
122 | 2611167.9463 | 1229388.6411
123 | 2611147.572 | 1229393.4748
124 | 2611176.9003 | 1229368.1427
125 | 2611130.2642 | 1229384.2641
126 | 2611049.531 | 1229544.2758
127 | 2611075.9284 | 1229565.6948
128 | 2611093.5012 | 1229575.4735
129 | 2611321.0578 | 1229314.5711
130 | 2611258.0574 | 1229341.1099
131 | 2611254.1427 | 1229338.766
132 | 2611279.6557 | 1229455.2945

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97633 | -0.45648 | 0.0014181 | 0.00035541
1 | 0.97642 | -0.45469 | 0.0016377 | 0.00041044
2 | 0.97617 | -0.45967 | 0.0038482 | 0.00096444
3 | 0.97649 | -0.4534 | 0.0031118 | 0.0007799
4 | 0.97617 | -0.4597 | 0.0019311 | 0.00048398
5 | 0.97684 | -0.44645 | 0.0025834 | 0.00064747
6 | 0.97612 | -0.4607 | 0 | 0
7 | 0.97689 | -0.44546 | 0.0019186 | 0.00048085
8 | 0.97592 | -0.46458 | 0 | 0
9 | 0.9765 | -0.45315 | 0.00176 | 0.0004411
10 | 0.97656 | -0.45193 | 0.0019783 | 0.00049582
11 | 0.97629 | -0.45727 | 0.0020851 | 0.00052257
12 | 0.97662 | -0.45068 | 0.0014533 | 0.00036422
13 | 0.97627 | -0.45768 | 0 | 0
14 | 0.97694 | -0.4444 | 0 | 0
15 | 0.97621 | -0.45874 | 0.0007654 | 0.00019183
16 | 0.97624 | -0.45818 | 0.0014533 | 0.00036422
17 | 0.97686 | -0.44606 | 0 | 0
18 | 0.97708 | -0.44165 | 0.0062791 | 0.0015737
19 | 0.97621 | -0.45892 | 0.001522 | 0.00038144
20 | 0.98207 | -0.34463 | 0.00040006 | 0.00010026
21 | 0.98212 | -0.34356 | 0.00022511 | 5.6417e-05
22 | 0.982 | -0.34607 | 0.0031699 | 0.00079445
23 | 0.98224 | -0.34128 | 0 | 0
24 | 0.98223 | -0.34148 | 0 | 0
25 | 0.98232 | -0.33973 | 0.00025438 | 6.3754e-05
26 | 0.98354 | -0.31575 | 0.0013979 | 0.00035035
27 | 0.98355 | -0.31573 | 0.00015633 | 3.918e-05
28 | 0.98222 | -0.34163 | 0.00038293 | 9.5971e-05
29 | 0.98234 | -0.33926 | 0.00043181 | 0.00010822
30 | 0.98357 | -0.31521 | 0.0013031 | 0.00032659
31 | 0.97772 | -0.42925 | 0.009935 | 0.0024899
32 | 0.97779 | -0.428 | 0.0077075 | 0.0019317
33 | 0.9781 | -0.42191 | 0.0031985 | 0.00080162
34 | 0.97815 | -0.42094 | 0 | 0
35 | 0.97882 | -0.40776 | 0.018164 | 0.0045524
36 | 0.97921 | -0.40011 | 0 | 0
37 | 0.97847 | -0.41467 | 0 | 0
38 | 0.97863 | -0.41152 | 0.01094 | 0.0027419
39 | 0.97873 | -0.40948 | 0.0053929 | 0.0013516
40 | 0.98061 | -0.37259 | 0.0045655 | 0.0011442
41 | 0.99498 | -0.096437 | 0 | 0
42 | 0.99423 | -0.11087 | 0 | 0
43 | 0.99677 | -0.061927 | 0.018774 | 0.0047052
44 | 0.99223 | -0.14953 | 0.00035666 | 8.9388e-05
45 | 0.99222 | -0.14963 | 0.0024382 | 0.00061107
46 | 0.99224 | -0.14925 | 0.00028445 | 7.129e-05
47 | 0.99234 | -0.14739 | 0 | 0
48 | 0.99238 | -0.14653 | 0 | 0
49 | 0.99227 | -0.14874 | 0.0032287 | 0.00080919
50 | 0.99274 | -0.13957 | 0 | 0
51 | 0.99273 | -0.13979 | 0.0013912 | 0.00034867
52 | 0.99276 | -0.13933 | 0 | 0
53 | 0.99188 | -0.15626 | 0.0080565 | 0.0020192
54 | 0.99301 | -0.13437 | 0.0042961 | 0.0010767
55 | 0.9757 | -0.46889 | 0.0038399 | 0.00096237
56 | 0.9871 | -0.24643 | 0.0027217 | 0.00068212
57 | 0.98715 | -0.24532 | 0.0028066 | 0.0007034
58 | 0.98462 | -0.29432 | 0.0023525 | 0.00058959
59 | 0.98717 | -0.24502 | 0.0010334 | 0.00025898
60 | 0.98304 | -0.32517 | 0.0056091 | 0.0014058
61 | 0.98808 | -0.22747 | 0.0033089 | 0.00082928
62 | 0.98167 | -0.35176 | 0.062678 | 0.015708
63 | 0.98814 | -0.22623 | 0.003446 | 0.00086364
64 | 0.98063 | -0.37209 | 0 | 0
65 | 0.98246 | -0.33649 | 0.0033245 | 0.00083319
66 | 0.9827 | -0.33179 | 0.0021845 | 0.00054748
67 | 0.98384 | -0.30973 | 0.0019461 | 0.00048774
68 | 0.97867 | -0.41073 | 0.0010605 | 0.00026579
69 | 0.98434 | -0.2999 | 0.0021866 | 0.00054801
70 | 0.97861 | -0.41176 | 0.0058234 | 0.0014595
71 | 0.98238 | -0.3386 | 0 | 0
72 | 0.98249 | -0.33643 | 0 | 0
73 | 0.98237 | -0.33874 | 0.00068376 | 0.00017137
74 | 0.98261 | -0.33411 | 0.00023206 | 5.8161e-05
75 | 0.9772 | -0.43926 | 0 | 0
76 | 0.97855 | -0.41284 | 0 | 0
77 | 0.97838 | -0.4162 | 0.0010844 | 0.00027177
78 | 0.98003 | -0.3838 | 0.0069778 | 0.0017488
79 | 0.97829 | -0.41803 | 0.0067756 | 0.0016981
80 | 0.99385 | -0.11807 | 0.0070838 | 0.0017754
81 | 0.99384 | -0.11834 | 0.044471 | 0.011145
82 | 0.99185 | -0.1569 | 0.0042088 | 0.0010548
83 | 0.98362 | -0.31423 | 0.0018121 | 0.00045414
84 | 0.98364 | -0.31384 | 0.0036075 | 0.00090413
85 | 0.98269 | -0.33243 | 0.0020958 | 0.00052526
86 | 0.98271 | -0.33204 | 0.0025852 | 0.00064792
87 | 0.98266 | -0.33298 | 0.0029613 | 0.00074216
88 | 0.98296 | -0.32725 | 0.0024866 | 0.00062319
89 | 0.98296 | -0.32718 | 0.0017524 | 0.00043919
90 | 0.98316 | -0.3232 | 0 | 0
91 | 1 | 0 | -0.46093 | -0.11745
92 | 0.99697 | -0.057431 | 0.0014266 | 0.00035755
93 | 0.99635 | -0.06906 | 0.026352 | 0.0066045
94 | 0.99437 | -0.10689 | 0.0043831 | 0.0010985
95 | 0.98622 | -0.26359 | 0.002797 | 0.00070101
96 | 0.98636 | -0.2609 | 0.0022815 | 0.00057181
97 | 0.9852 | -0.28339 | 0.0010059 | 0.00025211
98 | 0.9872 | -0.24459 | 0 | 0
99 | 0.9849 | -0.28939 | 0.0010036 | 0.00025152
100 | 0.98956 | -0.19898 | 0.0071003 | 0.0017795
101 | 0.98701 | -0.2483 | 0.0045563 | 0.0011419
102 | 0.98425 | -0.30203 | 0 | 0
103 | 0.99074 | -0.17625 | 0 | 0
104 | 0.98686 | -0.25112 | 0.0038873 | 0.00097424
105 | 0.98398 | -0.30716 | 0.0013851 | 0.00034713
106 | 0.98376 | -0.3116 | 0 | 0
107 | 0.98936 | -0.20284 | 0.0013175 | 0.00033019
108 | 0.98994 | -0.19169 | 0 | 0
109 | 0.9908 | -0.17515 | 0.0033542 | 0.00084063
110 | 0.9838 | -0.31068 | 0.0013901 | 0.00034839
111 | 0.98379 | -0.3109 | 0.0015376 | 0.00038536
112 | 0.98388 | -0.30914 | 0.0013313 | 0.00033365
113 | 0.98377 | -0.31132 | 0.0029977 | 0.0007513
114 | 0.98393 | -0.30829 | 0.0021496 | 0.00053875
115 | 0.99183 | -0.15729 | 0.0040083 | 0.0010046
116 | 0.99174 | -0.15901 | 0.0030276 | 0.00075879
117 | 0.98683 | -0.25176 | 0.0019196 | 0.0004811
118 | 0.99126 | -0.16627 | 0.0021848 | 0.00054755
119 | 0.99137 | -0.16416 | 0.0022899 | 0.00057389
120 | 0.99264 | -0.13979 | 0 | 0
121 | 0.99068 | -0.17745 | 0.0016319 | 0.000409
122 | 0.99196 | -0.15286 | 0.0032052 | 0.00080329
123 | 0.99252 | -0.14212 | 0.0036609 | 0.00091751
124 | 0.99088 | -0.17351 | 0.0013959 | 0.00034986
125 | 0.99245 | -0.14356 | 0.0041663 | 0.0010442
126 | 0.98307 | -0.32507 | 0.0032591 | 0.0008168
127 | 0.98291 | -0.32821 | 0.0026009 | 0.00065184
128 | 0.98286 | -0.3291 | 0.0024556 | 0.00061543
129 | 0.97671 | -0.44903 | 0.011106 | 0.0027833
130 | 0.97822 | -0.41939 | 0.0013058 | 0.00032727
131 | 0.97821 | -0.4195 | 0.0013574 | 0.00034019
132 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.01104 | -0.0027664 | 0.011041 | 0.0027668 | 9.422e-07 | 4.9202e-07 | 0.016826 | 0.016826 | 0.016826 | 0.97633 | -0.45648 | 0.97642 | -0.45469 | 4.6226
1 | 0.0096223 | 0.0024109 | -0.0096209 | -0.0024102 | 1.4626e-06 | 7.093e-07 | 0.014665 | 0.014665 | 0.014665 | 0.97633 | -0.45648 | 0.97617 | -0.45967 | 4.0289
2 | -0.012679 | -0.0031773 | 0.01268 | 0.0031777 | 7.8192e-07 | 4.3057e-07 | 0.019322 | 0.019322 | 0.019322 | 0.97642 | -0.45469 | 0.97649 | -0.4534 | 5.3083
3 | 0.0057727 | 0.0014458 | -0.0057727 | -0.0014458 | 7.3176e-09 | 1.5326e-09 | 0.0087992 | 0.0087992 | 0.0087992 | 0.97617 | -0.45967 | 0.97617 | -0.4597 | 2.4174
4 | -0.015792 | -0.0039576 | 0.015797 | 0.0039607 | 5.2292e-06 | 3.0453e-06 | 0.024064 | 0.024064 | 0.024064 | 0.97649 | -0.4534 | 0.97684 | -0.44645 | 6.611
5 | 0.0038416 | 0.00096181 | -0.0038414 | -0.00096187 | 1.8256e-07 | -6.0651e-08 | 0.0058555 | 0.0058556 | 0.0058556 | 0.97617 | -0.4597 | 0.97612 | -0.4607 | 1.6087
6 | -0.01838 | -0.0046081 | 0.018381 | 0.0046087 | 8.6726e-07 | 5.1811e-07 | 0.027999 | 0.027999 | 0.027999 | 0.97684 | -0.44645 | 0.97689 | -0.44546 | 7.6921
7 | 0.0038414 | 0.00096187 | -0.0038407 | -0.00096211 | 7.0987e-07 | -2.3562e-07 | 0.0058556 | 0.0058559 | 0.0058559 | 0.97612 | -0.4607 | 0.97592 | -0.46458 | 1.6088
8 | -0.0203 | -0.0050895 | 0.020306 | 0.0050931 | 5.9943e-06 | 3.627e-06 | 0.030922 | 0.030922 | 0.030922 | 0.97689 | -0.44546 | 0.9772 | -0.43926 | 8.495
9 | 0.0038407 | 0.00096211 | -0.0038399 | -0.00096237 | 7.8916e-07 | -2.6154e-07 | 0.0058559 | 0.0058561 | 0.0058561 | 0.97592 | -0.46458 | 0.9757 | -0.46889 | 1.6088
10 | -0.0075871 | -0.0019008 | 0.0075875 | 0.001901 | 4.4071e-07 | 1.7205e-07 | 0.011561 | 0.011561 | 0.011561 | 0.9765 | -0.45315 | 0.97656 | -0.45193 | 3.1761
11 | 0.0058271 | 0.0014598 | -0.0058259 | -0.0014595 | 1.1432e-06 | 2.4804e-07 | 0.0088792 | 0.0088794 | 0.0088794 | 0.9765 | -0.45315 | 0.97629 | -0.45727 | 2.4394
12 | -0.0095659 | -0.0023968 | 0.0095664 | 0.0023971 | 5.6781e-07 | 2.7422e-07 | 0.014576 | 0.014576 | 0.014576 | 0.97656 | -0.45193 | 0.97662 | -0.45068 | 4.0043
13 | 0.0037409 | 0.00093693 | -0.0037408 | -0.00093696 | 7.3837e-08 | -2.8486e-08 | 0.0057014 | 0.0057014 | 0.0057014 | 0.97629 | -0.45727 | 0.97627 | -0.45768 | 1.5663
14 | -0.01102 | -0.0027613 | 0.011023 | 0.0027631 | 3.2995e-06 | 1.721e-06 | 0.01679 | 0.01679 | 0.01679 | 0.97662 | -0.45068 | 0.97694 | -0.4444 | 4.6126
15 | 0.0022875 | 0.00057295 | -0.0022874 | -0.00057319 | 1.1528e-07 | -2.4243e-07 | 0.0034864 | 0.0034865 | 0.0034865 | 0.97627 | -0.45768 | 0.97621 | -0.45874 | 0.95784
16 | 0.0014533 | 0.00036401 | -0.0014533 | -0.00036422 | 3.4428e-08 | -2.1193e-07 | 0.002215 | 0.0022151 | 0.0022151 | 0.97627 | -0.45768 | 0.97624 | -0.45818 | 0.60854
17 | 0.011108 | 0.0027846 | -0.011107 | -0.0027841 | 8.7714e-07 | 4.5907e-07 | 0.016919 | 0.016919 | 0.016919 | 0.97694 | -0.4444 | 0.97686 | -0.44606 | 4.6481
18 | -0.022131 | -0.0055477 | 0.022134 | 0.0055494 | 2.9037e-06 | 1.773e-06 | 0.033709 | 0.033709 | 0.033709 | 0.97694 | -0.4444 | 0.97708 | -0.44165 | 9.2607
19 | 0.001522 | 0.00038137 | -0.001522 | -0.00038144 | 1.2842e-08 | -7.1339e-08 | 0.0023199 | 0.0023199 | 0.0023199 | 0.97621 | -0.45874 | 0.97621 | -0.45892 | 0.63733
20 | 0.011107 | 0.0027841 | -0.011106 | -0.0027833 | 1.5702e-06 | 8.2184e-07 | 0.016919 | 0.016919 | 0.016919 | 0.97686 | -0.44606 | 0.97671 | -0.44903 | 4.6482
21 | -0.028413 | -0.0071231 | 0.028416 | 0.0071251 | 3.2302e-06 | 2.0097e-06 | 0.043271 | 0.043271 | 0.043271 | 0.97708 | -0.44165 | 0.9772 | -0.43926 | 11.8877
22 | -0.0035702 | -0.00089454 | 0.0035704 | 0.00089444 | 1.8253e-07 | -9.3672e-08 | 0.0054094 | 0.0054093 | 0.0054094 | 0.98207 | -0.34463 | 0.98212 | -0.34356 | 1.4861
23 | 0.0031701 | 0.00079427 | -0.0031699 | -0.00079445 | 2.1766e-07 | -1.79e-07 | 0.0048032 | 0.0048033 | 0.0048033 | 0.98207 | -0.34463 | 0.982 | -0.34607 | 1.3196
24 | -0.0037955 | -0.00095086 | 0.0037959 | 0.0009507 | 4.1127e-07 | -1.5656e-07 | 0.0057504 | 0.0057502 | 0.0057504 | 0.98212 | -0.34356 | 0.98224 | -0.34128 | 1.5798
25 | 0.00038294 | 9.5336e-05 | -0.00038293 | -9.5696e-05 | 3.6163e-09 | -3.6058e-07 | 0.00057989 | 0.00058002 | 0.00058002 | 0.98224 | -0.34128 | 0.98223 | -0.34148 | 0.15935
26 | -0.0041788 | -0.001046 | 0.0041791 | 0.001046 | 3.0879e-07 | -6.2507e-08 | 0.0063301 | 0.00633 | 0.0063301 | 0.98224 | -0.34128 | 0.98232 | -0.33973 | 1.739
27 | 0.00038293 | 9.5696e-05 | -0.00038293 | -9.5971e-05 | 2.7606e-09 | -2.7515e-07 | 0.00058002 | 0.00058012 | 0.00058012 | 0.98223 | -0.34148 | 0.98222 | -0.34163 | 0.15937
28 | -0.0044335 | -0.0011097 | 0.0044336 | 0.0011097 | 9.9396e-08 | -1.0796e-08 | 0.0067154 | 0.0067153 | 0.0067154 | 0.98232 | -0.33973 | 0.98234 | -0.33926 | 1.8449
29 | -0.0013979 | -0.00035035 | 0.0013979 | 0.00035034 | 1.2064e-09 | -8.3554e-09 | 0.0021149 | 0.0021149 | 0.0021149 | 0.98354 | -0.31575 | 0.98355 | -0.31573 | 0.58102
30 | -0.0015542 | -0.00038952 | 0.0015543 | 0.00038931 | 3.9017e-08 | -2.1386e-07 | 0.0023514 | 0.0023513 | 0.0023514 | 0.98355 | -0.31573 | 0.98357 | -0.31521 | 0.646
31 | -0.0048654 | -0.0012179 | 0.0048656 | 0.0012179 | 1.5167e-07 | 2.7809e-09 | 0.0073694 | 0.0073694 | 0.0073694 | 0.98234 | -0.33926 | 0.98238 | -0.3386 | 2.0246
32 | -0.0028574 | -0.0007159 | 0.0028575 | 0.00071575 | 1.3264e-07 | -1.5536e-07 | 0.0043228 | 0.0043227 | 0.0043228 | 0.98357 | -0.31521 | 0.98362 | -0.31423 | 1.1876
33 | -0.009935 | -0.0024899 | 0.0099356 | 0.0024902 | 5.9172e-07 | 2.9213e-07 | 0.01512 | 0.01512 | 0.01512 | 0.97772 | -0.42925 | 0.97779 | -0.428 | 4.1539
34 | -0.017643 | -0.0044219 | 0.017648 | 0.004425 | 5.1252e-06 | 3.0423e-06 | 0.02685 | 0.02685 | 0.02685 | 0.97779 | -0.428 | 0.9781 | -0.42191 | 7.3763
35 | -0.020847 | -0.0052266 | 0.020848 | 0.0052272 | 9.6389e-07 | 5.8482e-07 | 0.031716 | 0.031716 | 0.031716 | 0.9781 | -0.42191 | 0.97815 | -0.42094 | 8.7131
36 | -0.020848 | -0.0052272 | 0.020854 | 0.005231 | 6.2292e-06 | 3.7793e-06 | 0.031716 | 0.031716 | 0.031716 | 0.97815 | -0.42094 | 0.97847 | -0.41467 | 8.7131
37 | -0.018164 | -0.0045524 | 0.018171 | 0.0045564 | 6.626e-06 | 3.9492e-06 | 0.027614 | 0.027614 | 0.027614 | 0.97882 | -0.40776 | 0.97921 | -0.40011 | 7.5862
38 | 0.031815 | 0.0079856 | -0.031797 | -0.0079747 | 1.7314e-05 | 1.0833e-05 | 0.04835 | 0.04835 | 0.04835 | 0.97921 | -0.40011 | 0.97863 | -0.41152 | 13.283
39 | 0.012283 | 0.00308 | -0.012277 | -0.0030771 | 5.4872e-06 | 2.9838e-06 | 0.018666 | 0.018666 | 0.018666 | 0.97921 | -0.40011 | 0.97873 | -0.40948 | 5.1281
40 | -0.062269 | -0.015622 | 0.06235 | 0.015674 | 8.1792e-05 | 5.204e-05 | 0.09463 | 0.09463 | 0.09463 | 0.97921 | -0.40011 | 0.98061 | -0.37259 | 25.9972
41 | -0.020854 | -0.005231 | 0.020857 | 0.0052329 | 3.1281e-06 | 1.8978e-06 | 0.031716 | 0.031716 | 0.031716 | 0.97847 | -0.41467 | 0.97863 | -0.41152 | 8.7131
42 | 0.0068846 | 0.0017255 | -0.0068842 | -0.0017253 | 4.087e-07 | 1.3656e-07 | 0.010467 | 0.010467 | 0.010467 | 0.97873 | -0.40948 | 0.97867 | -0.41073 | 2.8756
43 | -0.066916 | -0.016818 | 0.067032 | 0.016892 | 0.00011557 | 7.3585e-05 | 0.10156 | 0.10156 | 0.10156 | 0.98061 | -0.37259 | 0.98246 | -0.33649 | 27.9005
44 | 0.082987 | 0.020848 | -0.08293 | -0.020812 | 5.7137e-05 | 3.644e-05 | 0.12413 | 0.12413 | 0.12413 | 0.99498 | -0.096437 | 0.99423 | -0.11087 | 34.101
45 | -0.082987 | -0.020848 | 0.083124 | 0.020936 | 0.00013693 | 8.7325e-05 | 0.12413 | 0.12413 | 0.12413 | 0.99498 | -0.096437 | 0.99677 | -0.061927 | 34.101
46 | 0.044486 | 0.011155 | -0.044471 | -0.011145 | 1.582e-05 | 1.0002e-05 | 0.066583 | 0.066583 | 0.066583 | 0.99423 | -0.11087 | 0.99384 | -0.11834 | 18.292
47 | 0.038444 | 0.0096566 | -0.038431 | -0.0096483 | 1.3199e-05 | 8.3098e-06 | 0.057545 | 0.057545 | 0.057545 | 0.99423 | -0.11087 | 0.99385 | -0.11807 | 15.809
48 | -0.1019 | -0.025641 | 0.1022 | 0.025834 | 0.00030252 | 0.00019316 | 0.15215 | 0.15215 | 0.15215 | 0.99677 | -0.061927 | 1 | 0 | 41.8005
49 | 0.0024382 | 0.00061105 | -0.0024382 | -0.00061107 | 1.1512e-08 | -2.2289e-08 | 0.0036565 | 0.0036565 | 0.0036565 | 0.99223 | -0.14953 | 0.99222 | -0.14963 | 1.0045
50 | -0.0027949 | -0.00070043 | 0.0027949 | 0.00070038 | 3.8052e-08 | -5.0253e-08 | 0.0041914 | 0.0041913 | 0.0041914 | 0.99223 | -0.14953 | 0.99224 | -0.14925 | 1.1515
51 | -0.0030793 | -0.00077167 | 0.0030796 | 0.00077141 | 2.7233e-07 | -2.6563e-07 | 0.0046179 | 0.0046178 | 0.0046179 | 0.99224 | -0.14925 | 0.99234 | -0.14739 | 1.2687
52 | -0.0063085 | -0.0015804 | 0.0063088 | 0.0015805 | 2.593e-07 | 6.6115e-08 | 0.0094595 | 0.0094594 | 0.0094595 | 0.99234 | -0.14739 | 0.99238 | -0.14653 | 2.5988
53 | 0.0032289 | 0.00080902 | -0.0032287 | -0.00080919 | 2.0767e-07 | -1.7226e-07 | 0.0048417 | 0.0048418 | 0.0048418 | 0.99234 | -0.14739 | 0.99227 | -0.14874 | 1.3302
54 | 0.019311 | 0.0048427 | -0.019302 | -0.0048373 | 8.9512e-06 | 5.3612e-06 | 0.028957 | 0.028957 | 0.028957 | 0.99238 | -0.14653 | 0.99188 | -0.15626 | 7.9551
55 | -0.02562 | -0.0064232 | 0.025629 | 0.0064286 | 8.7901e-06 | 5.4204e-06 | 0.038416 | 0.038416 | 0.038416 | 0.99238 | -0.14653 | 0.99276 | -0.13933 | 10.5538
56 | 0.0013912 | 0.00034857 | -0.0013912 | -0.00034867 | 1.4614e-08 | -1.0652e-07 | 0.0020853 | 0.0020853 | 0.0020853 | 0.99274 | -0.13957 | 0.99273 | -0.13979 | 0.57289
57 | -0.0013912 | -0.00034857 | 0.0013913 | 0.00034845 | 1.5651e-08 | -1.1408e-07 | 0.0020853 | 0.0020852 | 0.0020853 | 0.99274 | -0.13957 | 0.99276 | -0.13933 | 0.57288
58 | -0.02702 | -0.006777 | 0.027026 | 0.006781 | 6.3969e-06 | 3.9595e-06 | 0.040501 | 0.040501 | 0.040501 | 0.99276 | -0.13933 | 0.99301 | -0.13437 | 11.1267
59 | 0.011245 | 0.0028182 | -0.011245 | -0.002818 | 3.424e-07 | 1.7773e-07 | 0.01687 | 0.01687 | 0.01687 | 0.99188 | -0.15626 | 0.99185 | -0.1569 | 4.6347
60 | -0.031322 | -0.0078577 | 0.031347 | 0.0078729 | 2.4353e-05 | 1.5204e-05 | 0.046939 | 0.046939 | 0.046939 | 0.99301 | -0.13437 | 0.99385 | -0.11807 | 12.8953
61 | -0.14051 | -0.035582 | 0.14052 | 0.035587 | 7.4861e-06 | 4.7854e-06 | 0.21195 | 0.21195 | 0.21195 | 0.9871 | -0.24643 | 0.98715 | -0.24532 | 58.2274
62 | 0.13779 | 0.0349 | -0.13747 | -0.034698 | 0.00031615 | 0.00020209 | 0.20785 | 0.20785 | 0.20785 | 0.9871 | -0.24643 | 0.98462 | -0.29432 | 57.1003
63 | -0.14333 | -0.03629 | 0.14333 | 0.036291 | 2.0493e-06 | 1.3056e-06 | 0.21618 | 0.21618 | 0.21618 | 0.98715 | -0.24532 | 0.98717 | -0.24502 | 29.6949
64 | 0.13512 | 0.034108 | -0.13492 | -0.033981 | 0.00019936 | 0.00012743 | 0.20429 | 0.20429 | 0.20429 | 0.98462 | -0.29432 | 0.98304 | -0.32517 | 56.1236
65 | -0.14436 | -0.03655 | 0.14448 | 0.036627 | 0.00012176 | 7.7135e-05 | 0.21774 | 0.21774 | 0.21774 | 0.98717 | -0.24502 | 0.98808 | -0.22747 | 19.9392
66 | 0.12931 | 0.032575 | -0.12915 | -0.03247 | 0.00016423 | 0.00010496 | 0.1958 | 0.1958 | 0.1958 | 0.98304 | -0.32517 | 0.98167 | -0.35176 | 53.7911
67 | -0.14779 | -0.037457 | 0.1478 | 0.037462 | 8.7998e-06 | 5.5774e-06 | 0.22272 | 0.22272 | 0.22272 | 0.98808 | -0.22747 | 0.98814 | -0.22623 | 20.3955
68 | 0.066471 | 0.016761 | -0.066407 | -0.01672 | 6.4604e-05 | 4.1133e-05 | 0.10079 | 0.10079 | 0.10079 | 0.98167 | -0.35176 | 0.98063 | -0.37209 | 27.6905
69 | -0.15125 | -0.038326 | 0.15142 | 0.038434 | 0.0001702 | 0.00010792 | 0.22791 | 0.22791 | 0.22791 | 0.98814 | -0.22623 | 0.98936 | -0.20284 | 20.8707
70 | 0.066407 | 0.01672 | -0.06637 | -0.016697 | 3.7166e-05 | 2.3663e-05 | 0.10079 | 0.10079 | 0.10079 | 0.98063 | -0.37209 | 0.98003 | -0.3838 | 27.6905
71 | -0.070356 | -0.017725 | 0.070372 | 0.017735 | 1.5819e-05 | 1.0077e-05 | 0.10659 | 0.10659 | 0.10659 | 0.98246 | -0.33649 | 0.9827 | -0.33179 | 29.2837
72 | -0.072556 | -0.018283 | 0.072633 | 0.018331 | 7.6646e-05 | 4.8839e-05 | 0.1099 | 0.1099 | 0.1099 | 0.9827 | -0.33179 | 0.98384 | -0.30973 | 30.1924
73 | -0.074579 | -0.018819 | 0.074614 | 0.018842 | 3.511e-05 | 2.2377e-05 | 0.11284 | 0.11284 | 0.11284 | 0.98384 | -0.30973 | 0.98434 | -0.2999 | 31.001
74 | 0.0058237 | 0.0014595 | -0.0058234 | -0.0014595 | 2.8619e-07 | 6.0859e-08 | 0.0088546 | 0.0088547 | 0.0088547 | 0.97867 | -0.41073 | 0.97861 | -0.41176 | 2.4326
75 | -0.076801 | -0.01939 | 0.077005 | 0.01952 | 0.00020411 | 0.00013012 | 0.11615 | 0.11615 | 0.11615 | 0.98434 | -0.2999 | 0.9872 | -0.24459 | 31.9091
76 | -0.0055493 | -0.0013892 | 0.0055499 | 0.0013893 | 5.7346e-07 | 9.2912e-08 | 0.008405 | 0.0084049 | 0.008405 | 0.98238 | -0.3386 | 0.98249 | -0.33643 | 2.3091
77 | 0.00068376 | 0.00017123 | -0.00068376 | -0.00017137 | 4.3659e-09 | -1.3463e-07 | 0.0010357 | 0.0010357 | 0.0010357 | 0.98238 | -0.3386 | 0.98237 | -0.33874 | 0.28453
78 | -0.0055499 | -0.0013893 | 0.0055505 | 0.0013894 | 6.1206e-07 | 9.9091e-08 | 0.0084049 | 0.0084048 | 0.0084049 | 0.98249 | -0.33643 | 0.98261 | -0.33411 | 2.309
79 | -0.0057826 | -0.0014475 | 0.0057829 | 0.0014476 | 3.1306e-07 | 6.2429e-08 | 0.0087563 | 0.0087562 | 0.0087563 | 0.98261 | -0.33411 | 0.98266 | -0.33298 | 2.4056
80 | -0.048722 | -0.012218 | 0.048783 | 0.012257 | 6.1429e-05 | 3.8941e-05 | 0.074193 | 0.074193 | 0.074193 | 0.9772 | -0.43926 | 0.97855 | -0.41284 | 20.3827
81 | 0.010526 | 0.0026383 | -0.010524 | -0.0026375 | 1.6837e-06 | 8.5747e-07 | 0.016006 | 0.016006 | 0.016006 | 0.97855 | -0.41284 | 0.97838 | -0.4162 | 4.3973
82 | -0.059309 | -0.014896 | 0.059392 | 0.014948 | 8.2309e-05 | 5.2338e-05 | 0.090199 | 0.090199 | 0.090199 | 0.97855 | -0.41284 | 0.98003 | -0.3838 | 24.78
83 | 0.0094398 | 0.0023657 | -0.009439 | -0.0023653 | 8.2216e-07 | 3.9262e-07 | 0.014357 | 0.014357 | 0.014357 | 0.97838 | -0.4162 | 0.97829 | -0.41803 | 3.9442
84 | 0.0026634 | 0.00066717 | -0.0026632 | -0.00066741 | 1.7245e-07 | -2.4144e-07 | 0.004051 | 0.0040511 | 0.0040511 | 0.97829 | -0.41803 | 0.97822 | -0.41939 | 1.1129
85 | 0.0070363 | 0.0017632 | -0.0070362 | -0.0017631 | 1.2988e-07 | 4.301e-08 | 0.010556 | 0.010556 | 0.010556 | 0.99185 | -0.1569 | 0.99183 | -0.15729 | 2.9
86 | -0.0046696 | -0.0011699 | 0.0046697 | 0.0011699 | 8.7255e-08 | -3.3456e-09 | 0.007064 | 0.0070639 | 0.007064 | 0.98362 | -0.31423 | 0.98364 | -0.31384 | 1.9407
87 | -0.0082772 | -0.002074 | 0.0082781 | 0.0020744 | 8.8314e-07 | 3.7451e-07 | 0.012521 | 0.012521 | 0.012521 | 0.98364 | -0.31384 | 0.98376 | -0.3116 | 3.4399
88 | -0.01084 | -0.0027151 | 0.01084 | 0.0027152 | 1.99e-07 | 1.024e-07 | 0.016414 | 0.016414 | 0.016414 | 0.98269 | -0.33243 | 0.98271 | -0.33204 | 4.5093
89 | 0.0087444 | 0.0021899 | -0.0087441 | -0.0021898 | 2.2795e-07 | 1.0196e-07 | 0.01324 | 0.01324 | 0.01324 | 0.98269 | -0.33243 | 0.98266 | -0.33298 | 3.6375
90 | -0.013426 | -0.0033631 | 0.013429 | 0.0033649 | 3.0682e-06 | 1.7127e-06 | 0.020328 | 0.020328 | 0.020328 | 0.98271 | -0.33204 | 0.98296 | -0.32725 | 5.5847
91 | -0.015915 | -0.003988 | 0.015915 | 0.0039881 | 5.2491e-08 | 3.0537e-08 | 0.024093 | 0.024093 | 0.024093 | 0.98296 | -0.32725 | 0.98296 | -0.32718 | 6.6188
92 | -0.017668 | -0.0044273 | 0.017671 | 0.0044293 | 3.3497e-06 | 1.9855e-06 | 0.026745 | 0.026745 | 0.026745 | 0.98296 | -0.32718 | 0.98316 | -0.3232 | 7.3476
93 | 0.0083171 | 0.0020842 | -0.0083164 | -0.0020839 | 7.4152e-07 | 3.1634e-07 | 0.012588 | 0.012588 | 0.012588 | 0.98316 | -0.3232 | 0.98307 | -0.32507 | 3.4582
94 | -0.025988 | -0.0065135 | 0.026003 | 0.0065224 | 1.4369e-05 | 8.8818e-06 | 0.039333 | 0.039333 | 0.039333 | 0.98316 | -0.3232 | 0.98376 | -0.3116 | 10.8058
95 | 0.35708 | 0.091621 | -0.35609 | -0.090987 | 0.00099196 | 0.00063375 | 0.5321 | 0.5321 | 0.5321 | 1 | 0 | 0.99697 | -0.057431 | 48.727
96 | 0.35466 | 0.090629 | -0.35446 | -0.090502 | 0.00019932 | 0.00012735 | 0.52997 | 0.52997 | 0.52997 | 0.99697 | -0.057431 | 0.99635 | -0.06906 | 48.532
97 | 0.32811 | 0.083897 | -0.32751 | -0.083515 | 0.00059934 | 0.0003828 | 0.49061 | 0.49061 | 0.49061 | 0.99635 | -0.06906 | 0.99437 | -0.10689 | 44.928
98 | 0.32313 | 0.082416 | -0.32262 | -0.082089 | 0.00051259 | 0.00032738 | 0.48405 | 0.48405 | 0.48405 | 0.99437 | -0.10689 | 0.99264 | -0.13979 | 44.3274
99 | -0.049983 | -0.012571 | 0.04999 | 0.012575 | 6.4321e-06 | 4.0781e-06 | 0.075431 | 0.075431 | 0.075431 | 0.98622 | -0.26359 | 0.98636 | -0.2609 | 20.7228
100 | 0.047186 | 0.01187 | -0.047142 | -0.011842 | 4.4582e-05 | 2.8234e-05 | 0.071211 | 0.071211 | 0.071211 | 0.98622 | -0.26359 | 0.9852 | -0.28339 | 19.5634
101 | -0.052271 | -0.013147 | 0.052312 | 0.013173 | 4.0759e-05 | 2.5863e-05 | 0.078873 | 0.078873 | 0.078873 | 0.98636 | -0.2609 | 0.9872 | -0.24459 | 21.6684
102 | 0.046136 | 0.01159 | -0.046123 | -0.011582 | 1.3211e-05 | 8.3626e-06 | 0.069691 | 0.069692 | 0.069692 | 0.9852 | -0.28339 | 0.9849 | -0.28939 | 19.146
103 | -0.13968 | -0.035291 | 0.13999 | 0.035487 | 0.00030608 | 0.00019566 | 0.21065 | 0.21065 | 0.21065 | 0.9872 | -0.24459 | 0.98956 | -0.19898 | 57.8699
104 | 0.010366 | 0.0025981 | -0.010364 | -0.0025972 | 1.8328e-06 | 9.1707e-07 | 0.015625 | 0.015625 | 0.015625 | 0.9872 | -0.24459 | 0.98701 | -0.2483 | 4.2925
105 | 0.045119 | 0.01133 | -0.045092 | -0.011313 | 2.7187e-05 | 1.7202e-05 | 0.068175 | 0.068175 | 0.068175 | 0.9849 | -0.28939 | 0.98425 | -0.30203 | 18.7295
106 | -0.14709 | -0.037266 | 0.14725 | 0.037369 | 0.00016083 | 0.00010248 | 0.22132 | 0.22132 | 0.22132 | 0.98956 | -0.19898 | 0.99074 | -0.17625 | 30.4015
107 | 0.0058077 | 0.0014553 | -0.005807 | -0.0014551 | 7.7926e-07 | 1.5234e-07 | 0.0087557 | 0.0087558 | 0.0087558 | 0.98701 | -0.2483 | 0.98686 | -0.25112 | 2.4054
108 | 0.010795 | 0.0027063 | -0.010793 | -0.002705 | 2.6407e-06 | 1.3542e-06 | 0.016321 | 0.016321 | 0.016321 | 0.98425 | -0.30203 | 0.98398 | -0.30716 | 4.4839
109 | 0.034296 | 0.0086066 | -0.034281 | -0.0085968 | 1.5643e-05 | 9.8145e-06 | 0.051854 | 0.051854 | 0.051854 | 0.98425 | -0.30203 | 0.98376 | -0.3116 | 14.2457
110 | 0.001632 | 0.00040853 | -0.0016319 | -0.000409 | 9.3102e-08 | -4.7255e-07 | 0.002451 | 0.0024512 | 0.0024512 | 0.99074 | -0.17625 | 0.99068 | -0.17745 | 0.6734
111 | -0.14888 | -0.037777 | 0.14895 | 0.037822 | 7.1532e-05 | 4.5339e-05 | 0.22377 | 0.22377 | 0.22377 | 0.99074 | -0.17625 | 0.99126 | -0.16627 | 20.4921
112 | 0.0019197 | 0.0004809 | -0.0019196 | -0.0004811 | 5.856e-08 | -2.0066e-07 | 0.0028945 | 0.0028946 | 0.0028946 | 0.98686 | -0.25112 | 0.98683 | -0.25176 | 0.79521
113 | 0.0094077 | 0.0023578 | -0.0094072 | -0.0023576 | 5.0552e-07 | 2.3894e-07 | 0.014227 | 0.014227 | 0.014227 | 0.98398 | -0.30716 | 0.98393 | -0.30829 | 3.9084
114 | -0.15273 | -0.038764 | 0.15282 | 0.038816 | 8.1968e-05 | 5.1981e-05 | 0.22989 | 0.22989 | 0.22989 | 0.98936 | -0.20284 | 0.98994 | -0.19169 | 21.0521
115 | -0.15282 | -0.038816 | 0.15294 | 0.038893 | 0.00012177 | 7.7221e-05 | 0.22989 | 0.22989 | 0.22989 | 0.98994 | -0.19169 | 0.9908 | -0.17515 | 21.0521
116 | -0.15629 | -0.039734 | 0.1563 | 0.039742 | 1.2275e-05 | 7.7872e-06 | 0.23493 | 0.23493 | 0.23493 | 0.9908 | -0.17515 | 0.99088 | -0.17351 | 21.5134
117 | 0.0045355 | 0.0011366 | -0.0045354 | -0.0011366 | 4.7664e-08 | -3.7912e-09 | 0.0068599 | 0.0068599 | 0.0068599 | 0.9838 | -0.31068 | 0.98379 | -0.3109 | 1.8846
118 | -0.0059256 | -0.001485 | 0.005926 | 0.0014851 | 4.3273e-07 | 9.4518e-08 | 0.0089625 | 0.0089624 | 0.0089625 | 0.9838 | -0.31068 | 0.98388 | -0.30914 | 2.4622
119 | 0.0029978 | 0.00075124 | -0.0029977 | -0.0007513 | 6.0744e-08 | -6.1163e-08 | 0.0045342 | 0.0045343 | 0.0045343 | 0.98379 | -0.3109 | 0.98377 | -0.31132 | 1.2457
120 | -0.0072573 | -0.0018187 | 0.0072576 | 0.0018188 | 2.9487e-07 | 1.0582e-07 | 0.010976 | 0.010976 | 0.010976 | 0.98388 | -0.30914 | 0.98393 | -0.30829 | 3.0153
121 | 0.0030279 | 0.00075854 | -0.0030276 | -0.00075879 | 2.4856e-07 | -2.5543e-07 | 0.0045425 | 0.0045427 | 0.0045427 | 0.99183 | -0.15729 | 0.99174 | -0.15901 | 1.248
122 | -0.15114 | -0.03837 | 0.15115 | 0.03838 | 1.5324e-05 | 9.7156e-06 | 0.22705 | 0.22705 | 0.22705 | 0.99126 | -0.16627 | 0.99137 | -0.16416 | 20.7924
123 | -0.15344 | -0.038954 | 0.15362 | 0.039068 | 0.0001801 | 0.00011421 | 0.23049 | 0.23049 | 0.23049 | 0.99137 | -0.16416 | 0.99264 | -0.13979 | 21.1072
124 | 0.16116 | 0.041059 | -0.16106 | -0.040995 | 0.0001015 | 6.4421e-05 | 0.24183 | 0.24183 | 0.24183 | 0.99264 | -0.13979 | 0.99196 | -0.15286 | 22.1456
125 | 0.0078284 | 0.001962 | -0.0078276 | -0.0019616 | 8.6689e-07 | 3.3784e-07 | 0.011735 | 0.011735 | 0.011735 | 0.99264 | -0.13979 | 0.99252 | -0.14212 | 3.224
126 | 0.15786 | 0.040191 | -0.1577 | -0.040092 | 0.00015708 | 9.9668e-05 | 0.23702 | 0.23702 | 0.23702 | 0.99196 | -0.15286 | 0.99088 | -0.17351 | 21.7054
127 | 0.0041666 | 0.0010441 | -0.0041663 | -0.0010442 | 2.8689e-07 | -6.9753e-08 | 0.0062467 | 0.0062468 | 0.0062468 | 0.99252 | -0.14212 | 0.99245 | -0.14356 | 1.7161
128 | 0.0050573 | 0.0012671 | -0.0050566 | -0.0012671 | 7.5649e-07 | 4.7743e-08 | 0.0076549 | 0.007655 | 0.007655 | 0.98307 | -0.32507 | 0.98291 | -0.32821 | 2.103
129 | 0.0024557 | 0.00061524 | -0.0024556 | -0.00061543 | 1.0423e-07 | -1.8817e-07 | 0.0037176 | 0.0037177 | 0.0037177 | 0.98291 | -0.32821 | 0.98286 | -0.3291 | 1.0213
130 | 0.0013574 | 0.00034014 | -0.0013574 | -0.00034019 | 7.2947e-09 | -5.2612e-08 | 0.0020648 | 0.0020648 | 0.0020648 | 0.97822 | -0.41939 | 0.97821 | -0.4195 | 0.56725

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47613 | 0.12126

## res_load
| p_mw | q_mvar
0 | 0.0014181 | 0.00035541
1 | 0.0016377 | 0.00041044
2 | 0.0038482 | 0.00096444
3 | 0.0031118 | 0.0007799
4 | 0.0019311 | 0.00048398
5 | 0.0025834 | 0.00064747
6 | 0.0019186 | 0.00048085
7 | 0.00176 | 0.0004411
8 | 0.0019783 | 0.00049582
9 | 0.0020851 | 0.00052257
10 | 0.0014533 | 0.00036422
11 | 0.0007654 | 0.00019183
12 | 0.0014533 | 0.00036422
13 | 0.0062791 | 0.0015737
14 | 0.001522 | 0.00038144
15 | 0.00040006 | 0.00010026
16 | 0.00022511 | 5.6417e-05
17 | 0.0031699 | 0.00079445
18 | 0.00025438 | 6.3754e-05
19 | 0.0013979 | 0.00035035
20 | 0.00015633 | 3.918e-05
21 | 0.00038293 | 9.5971e-05
22 | 0.00043181 | 0.00010822
23 | 0.0013031 | 0.00032659
24 | 0.009935 | 0.0024899
25 | 0.0077075 | 0.0019317
26 | 0.0031985 | 0.00080162
27 | 0.018164 | 0.0045524
28 | 0.01094 | 0.0027419
29 | 0.0053929 | 0.0013516
30 | 0.0045655 | 0.0011442
31 | 0.018774 | 0.0047052
32 | 0.00035666 | 8.9388e-05
33 | 0.0024382 | 0.00061107
34 | 0.00028445 | 7.129e-05
35 | 0.0032287 | 0.00080919
36 | 0.0013912 | 0.00034867
37 | 0.0080565 | 0.0020192
38 | 0.0042961 | 0.0010767
39 | 0.0038399 | 0.00096237
40 | 0.0027217 | 0.00068212
41 | 0.0028066 | 0.0007034
42 | 0.0023525 | 0.00058959
43 | 0.0010334 | 0.00025898
44 | 0.0056091 | 0.0014058
45 | 0.0033089 | 0.00082928
46 | 0.062678 | 0.015708
47 | 0.003446 | 0.00086364
48 | 0.0033245 | 0.00083319
49 | 0.0021845 | 0.00054748
50 | 0.0019461 | 0.00048774
51 | 0.0010605 | 0.00026579
52 | 0.0021866 | 0.00054801
53 | 0.0058234 | 0.0014595
54 | 0.00068376 | 0.00017137
55 | 0.00023206 | 5.8161e-05
56 | 0.0010844 | 0.00027177
57 | 0.0069778 | 0.0017488
58 | 0.0067756 | 0.0016981
59 | 0.0070838 | 0.0017754
60 | 0.044471 | 0.011145
61 | 0.0042088 | 0.0010548
62 | 0.0018121 | 0.00045414
63 | 0.0036075 | 0.00090413
64 | 0.0020958 | 0.00052526
65 | 0.0025852 | 0.00064792
66 | 0.0029613 | 0.00074216
67 | 0.0024866 | 0.00062319
68 | 0.0017524 | 0.00043919
69 | 0.015201 | 0.0038096
70 | 0.0014266 | 0.00035755
71 | 0.026352 | 0.0066045
72 | 0.0043831 | 0.0010985
73 | 0.002797 | 0.00070101
74 | 0.0022815 | 0.00057181
75 | 0.0010059 | 0.00025211
76 | 0.0010036 | 0.00025152
77 | 0.0071003 | 0.0017795
78 | 0.0045563 | 0.0011419
79 | 0.0038873 | 0.00097424
80 | 0.0013851 | 0.00034713
81 | 0.0013175 | 0.00033019
82 | 0.0033542 | 0.00084063
83 | 0.0013901 | 0.00034839
84 | 0.0015376 | 0.00038536
85 | 0.0013313 | 0.00033365
86 | 0.0029977 | 0.0007513
87 | 0.0021496 | 0.00053875
88 | 0.0040083 | 0.0010046
89 | 0.0030276 | 0.00075879
90 | 0.0019196 | 0.0004811
91 | 0.0021848 | 0.00054755
92 | 0.0022899 | 0.00057389
93 | 0.0016319 | 0.000409
94 | 0.0032052 | 0.00080329
95 | 0.0036609 | 0.00091751
96 | 0.0013959 | 0.00034986
97 | 0.0041663 | 0.0010442
98 | 0.0032591 | 0.0008168
99 | 0.0026009 | 0.00065184
100 | 0.0024556 | 0.00061543
101 | 0.011106 | 0.0027833
102 | 0.0013058 | 0.00032727
103 | 0.0013574 | 0.00034019

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1