## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2527-5_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2527-5_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2527-5_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2527-5_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2527-5_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2527-5_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2527-5_0_5_node_126 | 0.4 | n |  | TRUE
7 | bus_LV_2527-5_0_5_node_36 | 0.4 | n |  | TRUE
8 | bus_LV_2527-5_0_5_node_74 | 0.4 | n |  | TRUE
9 | bus_LV_2527-5_0_5_node_48 | 0.4 | n |  | TRUE
10 | bus_LV_2527-5_0_5_node_69 | 0.4 | n |  | TRUE
11 | bus_LV_2527-5_0_5_node_123 | 0.4 | n |  | TRUE
12 | bus_LV_2527-5_0_5_node_118 | 0.4 | n |  | TRUE
13 | bus_LV_2527-5_0_5_node_38 | 0.4 | n |  | TRUE
14 | bus_LV_2527-5_0_5_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_2527-5_0_5_node_93 | 0.4 | n |  | TRUE
16 | bus_LV_2527-5_0_5_node_73 | 0.4 | n |  | TRUE
17 | bus_LV_2527-5_0_5_node_47 | 0.4 | n |  | TRUE
18 | bus_LV_2527-5_0_5_node_78 | 0.4 | n |  | TRUE
19 | bus_LV_2527-5_0_5_node_6 | 0.4 | n |  | TRUE
20 | bus_LV_2527-5_0_5_node_7 | 0.4 | n |  | TRUE
21 | bus_LV_2527-5_0_5_node_8 | 0.4 | n |  | TRUE
22 | bus_LV_2527-5_0_5_node_9 | 0.4 | n |  | TRUE
23 | bus_LV_2527-5_0_5_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_2527-5_0_5_node_57 | 0.4 | n |  | TRUE
25 | bus_LV_2527-5_0_5_node_71 | 0.4 | n |  | TRUE
26 | bus_LV_2527-5_0_5_node_59 | 0.4 | n |  | TRUE
27 | bus_LV_2527-5_0_5_node_56 | 0.4 | n |  | TRUE
28 | bus_LV_2527-5_0_5_node_72 | 0.4 | n |  | TRUE
29 | bus_LV_2527-5_0_5_node_11 | 0.4 | n |  | TRUE
30 | bus_LV_2527-5_0_5_node_12 | 0.4 | n |  | TRUE
31 | bus_LV_2527-5_0_5_node_13 | 0.4 | n |  | TRUE
32 | bus_LV_2527-5_0_5_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_2527-5_0_5_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_2527-5_0_5_node_14 | 0.4 | n |  | TRUE
35 | bus_LV_2527-5_0_5_node_16 | 0.4 | n |  | TRUE
36 | bus_LV_2527-5_0_5_node_15 | 0.4 | n |  | TRUE
37 | bus_LV_2527-5_0_5_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_2527-5_0_5_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_2527-5_0_5_node_75 | 0.4 | n |  | TRUE
40 | bus_LV_2527-5_0_5_node_64 | 0.4 | n |  | TRUE
41 | bus_LV_2527-5_0_5_node_18 | 0.4 | n |  | TRUE
42 | bus_LV_2527-5_0_5_node_53 | 0.4 | n |  | TRUE
43 | bus_LV_2527-5_0_5_node_85 | 0.4 | n |  | TRUE
44 | bus_LV_2527-5_0_5_node_54 | 0.4 | n |  | TRUE
45 | bus_LV_2527-5_0_5_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_2527-5_0_5_node_61 | 0.4 | n |  | TRUE
47 | bus_LV_2527-5_0_5_node_55 | 0.4 | n |  | TRUE
48 | bus_LV_2527-5_0_5_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_2527-5_0_5_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_2527-5_0_5_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_2527-5_0_5_node_20 | 0.4 | n |  | TRUE
52 | bus_LV_2527-5_0_5_node_21 | 0.4 | n |  | TRUE
53 | bus_LV_2527-5_0_5_node_22 | 0.4 | n |  | TRUE
54 | bus_LV_2527-5_0_5_node_23 | 0.4 | n |  | TRUE
55 | bus_LV_2527-5_0_5_node_25 | 0.4 | n |  | TRUE
56 | bus_LV_2527-5_0_5_node_26 | 0.4 | n |  | TRUE
57 | bus_LV_2527-5_0_5_node_40 | 0.4 | n |  | TRUE
58 | bus_LV_2527-5_0_5_node_24 | 0.4 | n |  | TRUE
59 | bus_LV_2527-5_0_5_node_112 | 0.4 | n |  | TRUE
60 | bus_LV_2527-5_0_5_node_32 | 0.4 | n |  | TRUE
61 | bus_LV_2527-5_0_5_node_39 | 0.4 | n |  | TRUE
62 | bus_LV_2527-5_0_5_node_113 | 0.4 | n |  | TRUE
63 | bus_LV_2527-5_0_5_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_2527-5_0_5_node_27 | 0.4 | n |  | TRUE
65 | bus_LV_2527-5_0_5_node_29 | 0.4 | n |  | TRUE
66 | bus_LV_2527-5_0_5_node_33 | 0.4 | n |  | TRUE
67 | bus_LV_2527-5_0_5_node_31 | 0.4 | n |  | TRUE
68 | bus_LV_2527-5_0_5_node_79 | 0.4 | n |  | TRUE
69 | bus_LV_2527-5_0_5_node_110 | 0.4 | n |  | TRUE
70 | bus_LV_2527-5_0_5_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_2527-5_0_5_node_80 | 0.4 | n |  | TRUE
72 | bus_LV_2527-5_0_5_node_35 | 0.4 | n |  | TRUE
73 | bus_LV_2527-5_0_5_node_37 | 0.4 | n |  | TRUE
74 | bus_LV_2527-5_0_5_node_76 | 0.4 | n |  | TRUE
75 | bus_LV_2527-5_0_5_node_49 | 0.4 | n |  | TRUE
76 | bus_LV_2527-5_0_5_node_77 | 0.4 | n |  | TRUE
77 | bus_LV_2527-5_0_5_node_41 | 0.4 | n |  | TRUE
78 | bus_LV_2527-5_0_5_node_101 | 0.4 | n |  | TRUE
79 | bus_LV_2527-5_0_5_node_107 | 0.4 | n |  | TRUE
80 | bus_LV_2527-5_0_5_node_99 | 0.4 | n |  | TRUE
81 | bus_LV_2527-5_0_5_node_109 | 0.4 | n |  | TRUE
82 | bus_LV_2527-5_0_5_node_105 | 0.4 | n |  | TRUE
83 | bus_LV_2527-5_0_5_node_58 | 0.4 | n |  | TRUE
84 | bus_LV_2527-5_0_5_node_60 | 0.4 | n |  | TRUE
85 | bus_LV_2527-5_0_5_node_62 | 0.4 | n |  | TRUE
86 | bus_LV_2527-5_0_5_node_63 | 0.4 | n |  | TRUE
87 | bus_LV_2527-5_0_5_node_83 | 0.4 | n |  | TRUE
88 | bus_LV_2527-5_0_5_node_81 | 0.4 | n |  | TRUE
89 | bus_LV_2527-5_0_5_node_129 | 0.4 | n |  | TRUE
90 | bus_LV_2527-5_0_5_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_2527-5_0_5_node_65 | 0.4 | n |  | TRUE
92 | bus_LV_2527-5_0_5_node_66 | 0.4 | n |  | TRUE
93 | bus_LV_2527-5_0_5_node_67 | 0.4 | n |  | TRUE
94 | bus_LV_2527-5_0_5_node_68 | 0.4 | n |  | TRUE
95 | bus_LV_2527-5_0_5_node_70 | 0.4 | n |  | TRUE
96 | bus_LV_2527-5_0_5_node_102 | 0.4 | n |  | TRUE
97 | bus_LV_2527-5_0_5_node_100 | 0.4 | n |  | TRUE
98 | bus_LV_2527-5_0_5_node_128 | 0.4 | n |  | TRUE
99 | bus_LV_2527-5_0_5_node_98 | 0.4 | n |  | TRUE
100 | bus_LV_2527-5_0_5_node_94 | 0.4 | n |  | TRUE
101 | bus_LV_2527-5_0_5_node_84 | 0.4 | n |  | TRUE
102 | bus_LV_2527-5_0_5_node_111 | 0.4 | n |  | TRUE
103 | bus_LV_2527-5_0_5_node_125 | 0.4 | n |  | TRUE
104 | bus_LV_2527-5_0_5_node_121 | 0.4 | n |  | TRUE
105 | bus_LV_2527-5_0_5_node_119 | 0.4 | n |  | TRUE
106 | bus_LV_2527-5_0_5_node_120 | 0.4 | n |  | TRUE
107 | bus_LV_2527-5_0_5_node_86 | 0.4 | n |  | TRUE
108 | bus_LV_2527-5_0_5_node_87 | 0.4 | n |  | TRUE
109 | bus_LV_2527-5_0_5_node_88 | 0.4 | n |  | TRUE
110 | bus_LV_2527-5_0_5_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_2527-5_0_5_node_92 | 0.4 | n |  | TRUE
112 | bus_LV_2527-5_0_5_node_114 | 0.4 | n |  | TRUE
113 | bus_LV_2527-5_0_5_node_91 | 0.4 | n |  | TRUE
114 | bus_LV_2527-5_0_5_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_2527-5_0_5_node_103 | 0.4 | n |  | TRUE
116 | bus_LV_2527-5_0_5_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_2527-5_0_5_node_97 | 0.4 | n |  | TRUE
118 | bus_LV_2527-5_0_5_node_106 | 0.4 | n |  | TRUE
119 | bus_LV_2527-5_0_5_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_2527-5_0_5_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_2527-5_0_5_node_116 | 0.4 | n |  | TRUE
122 | bus_LV_2527-5_0_5_node_117 | 0.4 | n |  | TRUE
123 | bus_LV_2527-5_0_5_node_127 | 0.4 | n |  | TRUE
124 | bus_MV_392_0_node_56 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2527-5_0_5_load_0 | 0 | 0.0016916 | 0.00042396 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2527-5_0_5_load_1 | 1 | 0.0019795 | 0.00049612 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2527-5_0_5_load_126 | 6 | 0.0019964 | 0.00050035 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2527-5_0_5_load_48 | 9 | 0.0046281 | 0.0011599 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2527-5_0_5_load_123 | 11 | 0.0026277 | 0.00065858 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2527-5_0_5_load_38 | 13 | 0.0018243 | 0.0004572 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2527-5_0_5_load_34 | 14 | 0.0037533 | 0.00094067 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2527-5_0_5_load_93 | 15 | 0.001763 | 0.00044185 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2527-5_0_5_load_47 | 17 | 0.0020896 | 0.0005237 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2527-5_0_5_load_78 | 18 | 0.0027116 | 0.00067959 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2527-5_0_5_load_6 | 19 | 0.0020457 | 0.0005127 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2527-5_0_5_load_7 | 20 | 0.0021804 | 0.00054646 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2527-5_0_5_load_8 | 21 | 0.0011495 | 0.00028808 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2527-5_0_5_load_9 | 22 | 0.0018434 | 0.00046201 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2527-5_0_5_load_10 | 23 | 0.0020301 | 0.00050878 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2527-5_0_5_load_71 | 25 | 0.00096594 | 0.00024209 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2527-5_0_5_load_59 | 26 | 0.0013949 | 0.00034959 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2527-5_0_5_load_56 | 27 | 0.0016686 | 0.00041819 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2527-5_0_5_load_72 | 28 | 0.002747 | 0.00068846 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2527-5_0_5_load_11 | 29 | 0.0076152 | 0.0019086 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2527-5_0_5_load_12 | 30 | 0.0011233 | 0.00028152 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2527-5_0_5_load_13 | 31 | 0.0027196 | 0.0006816 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2527-5_0_5_load_44 | 32 | 0.0042552 | 0.0010664 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2527-5_0_5_load_45 | 33 | 0.0025911 | 0.00064939 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2527-5_0_5_load_14 | 34 | 0.012601 | 0.0031581 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2527-5_0_5_load_15 | 36 | 0.00331 | 0.00082956 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2527-5_0_5_load_19 | 38 | 0.0025371 | 0.00063587 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2527-5_0_5_load_75 | 39 | 0.0083718 | 0.0020982 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2527-5_0_5_load_85 | 43 | 0.012069 | 0.0030247 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2527-5_0_5_load_42 | 45 | 0.0024172 | 0.00060581 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2527-5_0_5_load_51 | 48 | 0.0060923 | 0.0015269 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2527-5_0_5_load_52 | 50 | 0.0076908 | 0.0019275 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2527-5_0_5_load_20 | 51 | 0.00081233 | 0.00020359 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2527-5_0_5_load_21 | 52 | 0.004436 | 0.0011118 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2527-5_0_5_load_23 | 54 | 0.01869 | 0.0046842 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2527-5_0_5_load_26 | 56 | 0.0021424 | 0.00053694 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2527-5_0_5_load_40 | 57 | 0.0043055 | 0.0010791 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2527-5_0_5_load_24 | 58 | 0.011996 | 0.0030065 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2527-5_0_5_load_112 | 59 | 0.0027517 | 0.00068964 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2527-5_0_5_load_39 | 61 | 0.018353 | 0.0045996 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2527-5_0_5_load_113 | 62 | 0.0018363 | 0.00046021 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2527-5_0_5_load_43 | 63 | 0.0015192 | 0.00038075 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2527-5_0_5_load_27 | 64 | 0.00063791 | 0.00015988 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2527-5_0_5_load_33 | 66 | 0.00062355 | 0.00015628 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2527-5_0_5_load_31 | 67 | 0.0012117 | 0.00030367 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2527-5_0_5_load_79 | 68 | 0.001228 | 0.00030776 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2527-5_0_5_load_110 | 69 | 0.0032629 | 0.00081777 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2527-5_0_5_load_80 | 71 | 0.0024223 | 0.00060709 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2527-5_0_5_load_35 | 72 | 0.0012438 | 0.00031172 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2527-5_0_5_load_37 | 73 | 0.0019839 | 0.00049721 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2527-5_0_5_load_76 | 74 | 0.0012473 | 0.00031261 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2527-5_0_5_load_49 | 75 | 0.0021382 | 0.00053589 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2527-5_0_5_load_77 | 76 | 0.0018203 | 0.00045622 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2527-5_0_5_load_41 | 77 | 0.0024247 | 0.00060769 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2527-5_0_5_load_101 | 78 | 0.0012791 | 0.00032057 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2527-5_0_5_load_99 | 80 | 0.0068454 | 0.0017156 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2527-5_0_5_load_105 | 82 | 0.0064632 | 0.0016198 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2527-5_0_5_load_58 | 83 | 0.003964 | 0.00099346 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2527-5_0_5_load_60 | 84 | 0.00016836 | 4.2195e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2527-5_0_5_load_62 | 85 | 0.0044043 | 0.0011038 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2527-5_0_5_load_81 | 88 | 0.0010426 | 0.0002613 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2527-5_0_5_load_129 | 89 | 0.00046668 | 0.00011696 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2527-5_0_5_load_65 | 91 | 0.0028554 | 0.00071564 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2527-5_0_5_load_66 | 92 | 0.0019177 | 0.00048063 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2527-5_0_5_load_70 | 95 | 0.0012917 | 0.00032372 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2527-5_0_5_load_100 | 97 | 0.0014749 | 0.00036963 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2527-5_0_5_load_128 | 98 | 0.0076277 | 0.0019117 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2527-5_0_5_load_98 | 99 | 0.002177 | 0.00054562 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2527-5_0_5_load_94 | 100 | 0.0032503 | 0.0008146 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2527-5_0_5_load_84 | 101 | 0.00053729 | 0.00013466 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2527-5_0_5_load_111 | 102 | 0.00083006 | 0.00020803 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2527-5_0_5_load_125 | 103 | 0.00015076 | 3.7784e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2527-5_0_5_load_119 | 105 | 0.00073217 | 0.0001835 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2527-5_0_5_load_120 | 106 | 0.0013079 | 0.0003278 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2527-5_0_5_load_86 | 107 | 0.00078225 | 0.00019605 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2527-5_0_5_load_92 | 111 | 0.010432 | 0.0026146 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2527-5_0_5_load_114 | 112 | 0.0064598 | 0.001619 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2527-5_0_5_load_103 | 115 | 0.018699 | 0.0046864 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2527-5_0_5_load_96 | 116 | 0.001794 | 0.00044962 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2527-5_0_5_load_97 | 117 | 0.0029237 | 0.00073274 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2527-5_0_5_load_106 | 118 | 0.0073831 | 0.0018504 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2527-5_0_5_load_108 | 119 | 0.0027858 | 0.00069818 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2527-5_0_5_load_115 | 120 | 0.0023633 | 0.0005923 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2527-5_0_5_load_117 | 122 | 0.0054966 | 0.0013776 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2527-5_0_5_load_127 | 123 | 0.0018235 | 0.00045702 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2527-5_0_5_line_0 |  | 0 | 1 | 0.030515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2527-5_0_5_line_1 |  | 0 | 2 | 0.025444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2527-5_0_5_line_2 |  | 1 | 3 | 0.027737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2527-5_0_5_line_3 |  | 2 | 4 | 0.013364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_2527-5_0_5_line_4 |  | 2 | 5 | 0.005177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2527-5_0_5_line_5 |  | 3 | 6 | 0.015829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2527-5_0_5_line_6 |  | 3 | 7 | 0.007438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2527-5_0_5_line_7 |  | 4 | 8 | 0.00512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2527-5_0_5_line_8 |  | 4 | 9 | 0.026964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2527-5_0_5_line_9 |  | 5 | 10 | 0.01216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2527-5_0_5_line_10 |  | 5 | 11 | 0.041453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2527-5_0_5_line_11 |  | 6 | 12 | 0.005389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2527-5_0_5_line_12 |  | 7 | 13 | 0.015897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2527-5_0_5_line_13 |  | 7 | 14 | 0.01689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2527-5_0_5_line_14 |  | 8 | 15 | 0.023191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2527-5_0_5_line_15 |  | 8 | 16 | 0.04958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2527-5_0_5_line_16 |  | 9 | 17 | 0.014446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2527-5_0_5_line_17 |  | 10 | 18 | 0.015171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2527-5_0_5_line_18 |  | 12 | 123 | 0.012684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2527-5_0_5_line_19 |  | 12 | 121 | 0.011265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2527-5_0_5_line_20 |  | 13 | 74 | 0.0022417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2527-5_0_5_line_21 |  | 14 | 72 | 0.014895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2527-5_0_5_line_22 |  | 15 | 100 | 0.011515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2527-5_0_5_line_23 |  | 16 | 71 | 0.0046425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2527-5_0_5_line_24 |  | 16 | 28 | 0.024158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_2527-5_0_5_line_25 |  | 18 | 95 | 0.023299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2527-5_0_5_line_26 |  | 19 | 20 | 0.0096064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2527-5_0_5_line_27 |  | 19 | 21 | 0.00091647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2527-5_0_5_line_28 |  | 20 | 22 | 0.0093125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2527-5_0_5_line_29 |  | 21 | 23 | 0.014123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_2527-5_0_5_line_30 |  | 22 | 24 | 0.012909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2527-5_0_5_line_31 |  | 23 | 25 | 0.035785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2527-5_0_5_line_32 |  | 24 | 26 | 0.021403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2527-5_0_5_line_33 |  | 24 | 27 | 0.038789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2527-5_0_5_line_34 |  | 25 | 28 | 0.014701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2527-5_0_5_line_35 |  | 26 | 60 | 0.01301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2527-5_0_5_line_36 |  | 27 | 83 | 0.015956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2527-5_0_5_line_37 |  | 29 | 30 | 0.052724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2527-5_0_5_line_38 |  | 30 | 31 | 0.015019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2527-5_0_5_line_39 |  | 31 | 32 | 0.014469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2527-5_0_5_line_40 |  | 32 | 33 | 0.0072537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2527-5_0_5_line_41 |  | 33 | 49 | 0.014228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2527-5_0_5_line_42 |  | 34 | 35 | 0.046232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2527-5_0_5_line_43 |  | 35 | 38 | 0.029326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2527-5_0_5_line_44 |  | 36 | 37 | 0.046467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2527-5_0_5_line_45 |  | 37 | 39 | 0.014948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2527-5_0_5_line_46 |  | 37 | 40 | 0.047263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2527-5_0_5_line_47 |  | 38 | 44 | 0.012791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2527-5_0_5_line_48 |  | 40 | 45 | 0.033952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_2527-5_0_5_line_49 |  | 40 | 46 | 0.099558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2527-5_0_5_line_50 |  | 41 | 42 | 0.042099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_2527-5_0_5_line_51 |  | 41 | 43 | 0.025481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2527-5_0_5_line_52 |  | 42 | 47 | 0.02886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2527-5_0_5_line_53 |  | 42 | 48 | 0.02366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2527-5_0_5_line_54 |  | 43 | 49 | 0.025628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2527-5_0_5_line_55 |  | 44 | 50 | 0.018848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2527-5_0_5_line_56 |  | 45 | 77 | 0.020059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_2527-5_0_5_line_57 |  | 46 | 85 | 0.020071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2527-5_0_5_line_58 |  | 46 | 86 | 0.064354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2527-5_0_5_line_59 |  | 46 | 84 | 0.028734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2527-5_0_5_line_60 |  | 47 | 78 | 0.013713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_2527-5_0_5_line_61 |  | 47 | 79 | 0.023822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_2527-5_0_5_line_62 |  | 48 | 50 | 0.018438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2527-5_0_5_line_63 |  | 49 | 58 | 0.013392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2527-5_0_5_line_64 |  | 51 | 52 | 0.026435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_2527-5_0_5_line_65 |  | 51 | 53 | 0.013035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_2527-5_0_5_line_66 |  | 52 | 54 | 0.00032934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_2527-5_0_5_line_67 |  | 53 | 55 | 0.046514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_2527-5_0_5_line_68 |  | 53 | 56 | 0.034732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_2527-5_0_5_line_69 |  | 54 | 57 | 0.038374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2527-5_0_5_line_70 |  | 55 | 59 | 0.11643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_2527-5_0_5_line_71 |  | 56 | 60 | 0.03576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_2527-5_0_5_line_72 |  | 57 | 61 | 0.019959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_2527-5_0_5_line_73 |  | 59 | 62 | 0.018907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2527-5_0_5_line_74 |  | 60 | 63 | 0.022098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2527-5_0_5_line_75 |  | 61 | 77 | 0.014109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_2527-5_0_5_line_76 |  | 63 | 66 | 0.025137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2527-5_0_5_line_77 |  | 64 | 65 | 0.014908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2527-5_0_5_line_78 |  | 65 | 66 | 0.0099941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2527-5_0_5_line_79 |  | 67 | 68 | 0.0027551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2527-5_0_5_line_80 |  | 68 | 71 | 0.022132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2527-5_0_5_line_81 |  | 69 | 70 | 0.012676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2527-5_0_5_line_82 |  | 70 | 75 | 0.029299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2527-5_0_5_line_83 |  | 70 | 73 | 0.0091925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2527-5_0_5_line_84 |  | 72 | 73 | 0.021154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2527-5_0_5_line_85 |  | 74 | 76 | 0.006798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2527-5_0_5_line_86 |  | 78 | 80 | 0.0131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_2527-5_0_5_line_87 |  | 79 | 81 | 0.021365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_2527-5_0_5_line_88 |  | 79 | 82 | 0.024543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2527-5_0_5_line_89 |  | 80 | 117 | 0.023665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2527-5_0_5_line_90 |  | 81 | 112 | 0.0080124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_2527-5_0_5_line_91 |  | 82 | 118 | 0.018409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2527-5_0_5_line_92 |  | 86 | 87 | 0.07921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2527-5_0_5_line_93 |  | 86 | 88 | 0.031613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2527-5_0_5_line_94 |  | 87 | 89 | 0.098593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2527-5_0_5_line_95 |  | 88 | 90 | 0.023857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2527-5_0_5_line_96 |  | 90 | 101 | 0.012724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2527-5_0_5_line_97 |  | 90 | 102 | 0.1697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2527-5_0_5_line_98 |  | 91 | 92 | 0.01486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_2527-5_0_5_line_99 |  | 91 | 93 | 0.044036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_2527-5_0_5_line_100 |  | 92 | 94 | 0.015271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_2527-5_0_5_line_101 |  | 93 | 95 | 0.0593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_2527-5_0_5_line_102 |  | 94 | 96 | 0.064025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_2527-5_0_5_line_103 |  | 94 | 97 | 0.022952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_2527-5_0_5_line_104 |  | 96 | 98 | 0.047585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_2527-5_0_5_line_105 |  | 97 | 99 | 0.01695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_2527-5_0_5_line_106 |  | 99 | 116 | 0.0058275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_2527-5_0_5_line_107 |  | 101 | 103 | 0.021036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2527-5_0_5_line_108 |  | 102 | 104 | 0.038632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2527-5_0_5_line_109 |  | 104 | 105 | 0.025817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2527-5_0_5_line_110 |  | 105 | 106 | 0.017903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2527-5_0_5_line_111 |  | 107 | 108 | 0.069504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2527-5_0_5_line_112 |  | 107 | 109 | 0.030559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2527-5_0_5_line_113 |  | 108 | 110 | 0.1026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2527-5_0_5_line_114 |  | 109 | 111 | 0.079507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2527-5_0_5_line_115 |  | 110 | 112 | 0.10433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
116 | LV_2527-5_0_5_line_116 |  | 111 | 114 | 0.052511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2527-5_0_5_line_117 |  | 113 | 114 | 0.05174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2527-5_0_5_line_118 |  | 113 | 115 | 0.046285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2527-5_0_5_line_119 |  | 116 | 117 | 0.0065847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2527-5_0_5_line_120 |  | 118 | 119 | 0.015232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2527-5_0_5_line_121 |  | 120 | 121 | 0.02304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2527-5_0_5_line_122 |  | 120 | 122 | 0.010534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2527-5_0_5_trafo_85 | 0.63 MVA 20/0.4 kV | 124 | 43 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2610808.3923 | 1229230.1513 | 2610800.5132 | 1229244.3292 | 2610798.7729 | 1229251.5748 | 2610797.6214 | 1229258.3206
1 | 2610820.7521 | 1229207.9108 | 2610808.3923 | 1229230.1513
2 | 2610792.9541 | 1229285.6623 | 2610797.6214 | 1229258.3206
3 | 2610820.7521 | 1229207.9108 | 2610832.6875 | 1229213.9915
4 | 2610816.067 | 1229205.6787 | 2610820.7521 | 1229207.9108
5 | 2610792.9541 | 1229285.6623 | 2610777.9933 | 1229280.4931
6 | 2610799.774 | 1229288.6764 | 2610792.9541 | 1229285.6623
7 | 2610837.2588 | 1229216.3234 | 2610832.6875 | 1229213.9915
8 | 2610832.6875 | 1229213.9915 | 2610832.3716 | 1229221.1063 | 2610836.7185 | 1229240.4666
9 | 2610816.067 | 1229205.6787 | 2610821.3139 | 1229194.7039
10 | 2610816.067 | 1229205.6787 | 2610805.0065 | 1229201.7787 | 2610791.2509 | 1229196.8287 | 2610776.6073 | 1229193.119
11 | 2610772.8997 | 1229278.7332 | 2610777.9933 | 1229280.4931
12 | 2610799.774 | 1229288.6764 | 2610792.1988 | 1229302.6524
13 | 2610799.774 | 1229288.6764 | 2610815.1625 | 1229295.6373
14 | 2610837.2588 | 1229216.3234 | 2610853.3255 | 1229199.6001
15 | 2610881.1535 | 1229239.6169 | 2610862.0518 | 1229229.4762 | 2610837.2588 | 1229216.3234
16 | 2610839.8832 | 1229254.5615 | 2610836.7185 | 1229240.4666
17 | 2610821.3139 | 1229194.7039 | 2610825.1125 | 1229192.8542 | 2610832.889 | 1229185.1506
18 | 2610772.8997 | 1229278.7332 | 2610766.8031 | 1229289.8555
19 | 2610772.8997 | 1229278.7332 | 2610762.2557 | 1229274.9562
20 | 2610792.1988 | 1229302.6524 | 2610791.1306 | 1229304.6232
21 | 2610828.7335 | 1229301.776 | 2610815.1625 | 1229295.6373
22 | 2610861.303 | 1229191.2966 | 2610853.3255 | 1229199.6001
23 | 2610881.1535 | 1229239.6169 | 2610885.1305 | 1229242.0119
24 | 2610881.1535 | 1229239.6169 | 2610893.3322 | 1229218.7531
25 | 2610849.4414 | 1229168.7535 | 2610832.889 | 1229185.1506
26 | 2610933.7017 | 1229169.6653 | 2610938.4624 | 1229161.3216
27 | 2610933.2475 | 1229170.4614 | 2610933.7017 | 1229169.6653
28 | 2610938.4624 | 1229161.3216 | 2610941.0365 | 1229156.8103 | 2610945.0756 | 1229156.0061 | 2610945.0756 | 1229156.0061
29 | 2610925.2105 | 1229181.8456 | 2610928.0712 | 1229179.5334 | 2610933.2475 | 1229170.4614
30 | 2610956.5796 | 1229161.8639 | 2610945.0756 | 1229156.0061
31 | 2610900.7418 | 1229206.0559 | 2610906.8991 | 1229195.5043 | 2610910.6901 | 1229189.5632 | 2610922.6089 | 1229183.9483 | 2610925.2105 | 1229181.8456
32 | 2610956.5796 | 1229161.8639 | 2610975.7756 | 1229171.3307
33 | 2610956.5796 | 1229161.8639 | 2610973.8516 | 1229127.1328
34 | 2610900.7418 | 1229206.0559 | 2610893.5551 | 1229218.3713 | 2610893.3322 | 1229218.7531
35 | 2610987.4442 | 1229177.0851 | 2610975.7756 | 1229171.3307
36 | 2610980.9564 | 1229112.8462 | 2610973.8516 | 1229127.1328
37 | 2610914.7423 | 1229138.9281 | 2610916.2861 | 1229136.8198 | 2610919.7457 | 1229134.0023 | 2610923.1198 | 1229132.3185 | 2610930.116 | 1229130.1411 | 2610942.2557 | 1229111.4856 | 2610931.9243 | 1229104.8235
38 | 2610931.9243 | 1229104.8235 | 2610930.187 | 1229103.7033 | 2610937.2151 | 1229092.8246
39 | 2610937.2151 | 1229092.8246 | 2610945.0666 | 1229080.6713
40 | 2610949.0028 | 1229074.5784 | 2610945.0666 | 1229080.6713
41 | 2610956.7235 | 1229062.6274 | 2610949.0028 | 1229074.5784
42 | 2610932.9445 | 1228995.9777 | 2610957.1014 | 1229009.3965 | 2610965.3008 | 1229007.9996 | 2610974.4794 | 1229012.6302
43 | 2610932.9445 | 1228995.9777 | 2610935.1191 | 1228991.6346 | 2610935.5367 | 1228986.9993 | 2610932.7194 | 1228982.3692 | 2610920.028 | 1228975.5762
44 | 2611046.2225 | 1228951.1814 | 2611035.3265 | 1228972.8741 | 2611024.579 | 1228992.2889
45 | 2611046.2225 | 1228951.1814 | 2611032.4625 | 1228945.3415
46 | 2611046.2225 | 1228951.1814 | 2611073.1108 | 1228962.271 | 2611082.4387 | 1228965.2011 | 2611090.8451 | 1228966.6064
47 | 2610908.7507 | 1228969.54 | 2610920.028 | 1228975.5762
48 | 2611090.8451 | 1228966.6064 | 2611091.4145 | 1228974.0675 | 2611090.5194 | 1228986.9624 | 2611084.1453 | 1228998.9123
49 | 2611090.8451 | 1228966.6064 | 2611109.7042 | 1228964.8515 | 2611125.0611 | 1228960.244 | 2611134.5661 | 1228953.4243 | 2611145.2934 | 1228941.1592 | 2611158.1021 | 1228917.8025 | 2611149.1785 | 1228913.3944
50 | 2610911.6095 | 1229038.6085 | 2610874.1685 | 1229019.151
51 | 2610911.6095 | 1229038.6085 | 2610934.1018 | 1229050.5835
52 | 2610848.5038 | 1229005.8076 | 2610874.1685 | 1229019.151
53 | 2610874.1685 | 1229019.151 | 2610890.0087 | 1229001.5766
54 | 2610956.7235 | 1229062.6274 | 2610934.1018 | 1229050.5835
55 | 2610908.7507 | 1228969.54 | 2610899.9659 | 1228986.2156
56 | 2611074.705 | 1229016.6107 | 2611084.1453 | 1228998.9123
57 | 2611149.1785 | 1228913.3944 | 2611131.1804 | 1228904.5116
58 | 2611149.1785 | 1228913.3944 | 2611158.1021 | 1228917.8025 | 2611177.2028 | 1228924.6978 | 2611189.9682 | 1228924.5661 | 2611206.5052 | 1228920.9393 | 2611210.8024 | 1228920.0023
59 | 2611149.1785 | 1228913.3944 | 2611155.7915 | 1228885.4321
60 | 2610848.5038 | 1229005.8076 | 2610840.4604 | 1229016.9137
61 | 2610848.5038 | 1229005.8076 | 2610827.4184 | 1228994.6072
62 | 2610890.0087 | 1229001.5766 | 2610894.497 | 1228996.5968 | 2610899.9659 | 1228986.2156
63 | 2610956.7235 | 1229062.6274 | 2610968.1148 | 1229069.6688
64 | 2611028.0147 | 1229104.1439 | 2611040.4559 | 1229080.8195
65 | 2611020.9509 | 1229115.0655 | 2611025.7129 | 1229108.4592 | 2611028.0147 | 1229104.1439
66 | 2611040.4559 | 1229080.8195 | 2611040.6109 | 1229080.5289
67 | 2611052.576 | 1229149.2552 | 2611020.9509 | 1229115.0655
68 | 2611020.9509 | 1229115.0655 | 2611004.4419 | 1229145.623
69 | 2611040.6109 | 1229080.5289 | 2611058.671 | 1229046.6705
70 | 2611052.576 | 1229149.2552 | 2611081.4006 | 1229100.2016 | 2611110.5441 | 1229048.2858
71 | 2610987.4442 | 1229177.0851 | 2611004.4419 | 1229145.623
72 | 2611058.671 | 1229046.6705 | 2611068.0646 | 1229029.0599
73 | 2611119.7992 | 1229031.7989 | 2611110.5441 | 1229048.2858
74 | 2610987.4442 | 1229177.0851 | 2610976.8343 | 1229196.4698
75 | 2611074.705 | 1229016.6107 | 2611068.0646 | 1229029.0599
76 | 2610976.8343 | 1229196.4698 | 2610964.7655 | 1229218.52
77 | 2610959.9671 | 1229227.2868 | 2610952.81 | 1229240.3644
78 | 2610959.9671 | 1229227.2868 | 2610964.7655 | 1229218.52
79 | 2610904.0897 | 1229253.4291 | 2610906.4499 | 1229254.8504
80 | 2610904.0897 | 1229253.4291 | 2610885.1305 | 1229242.0119
81 | 2610856.3829 | 1229314.283 | 2610867.7883 | 1229319.8142
82 | 2610856.3829 | 1229314.283 | 2610847.8344 | 1229286.2585
83 | 2610856.3829 | 1229314.283 | 2610848.0075 | 1229310.4945
84 | 2610828.7335 | 1229301.776 | 2610848.0075 | 1229310.4945
85 | 2610787.8912 | 1229310.5998 | 2610791.1306 | 1229304.6232
86 | 2610832.7768 | 1229027.5231 | 2610840.4604 | 1229016.9137
87 | 2610827.4184 | 1228994.6072 | 2610808.505 | 1228984.567
88 | 2610827.4184 | 1228994.6072 | 2610845.1307 | 1228977.6181
89 | 2610818.8959 | 1229046.6895 | 2610832.7768 | 1229027.5231
90 | 2610808.505 | 1228984.567 | 2610801.4283 | 1228980.8094
91 | 2610845.1307 | 1228977.6181 | 2610853.3851 | 1228961.1638
92 | 2611210.8024 | 1228920.0023 | 2611218.2191 | 1228956.3045 | 2611223.5058 | 1228993.203 | 2611223.6255 | 1228998.0839
93 | 2611210.8024 | 1228920.0023 | 2611204.3064 | 1228889.0635
94 | 2611223.6255 | 1228998.0839 | 2611201.1604 | 1229003.9008 | 2611173.6924 | 1229007.2737 | 2611157.9348 | 1229007.4443 | 2611126.4482 | 1229000.5371
95 | 2611199.4041 | 1228865.7154 | 2611204.3064 | 1228889.0635
96 | 2611199.4041 | 1228865.7154 | 2611212.0443 | 1228867.1764
97 | 2611199.4041 | 1228865.7154 | 2611124.998 | 1228713.1972
98 | 2610813.0948 | 1229106.0463 | 2610811.719 | 1229104.9999 | 2610800.8503 | 1229097.6299
99 | 2610841.8023 | 1229137.8961 | 2610839.0209 | 1229130.2088 | 2610838.2218 | 1229128.006 | 2610830.5636 | 1229119.3314 | 2610813.0948 | 1229106.0463
100 | 2610788.2107 | 1229089.0591 | 2610800.8503 | 1229097.6299
101 | 2610841.8023 | 1229137.8961 | 2610848.6544 | 1229135.7517 | 2610851.5082 | 1229136.8909 | 2610869.0152 | 1229149.3635 | 2610849.4414 | 1229168.7535
102 | 2610741.761 | 1229095.5794 | 2610751.063 | 1229087.5469 | 2610768.4496 | 1229070.3013 | 2610788.2107 | 1229089.0591
103 | 2610788.2107 | 1229089.0591 | 2610801.6735 | 1229070.4699
104 | 2610741.761 | 1229095.5794 | 2610748.9308 | 1229106.3876 | 2610755.9936 | 1229113.449 | 2610775.3516 | 1229128.7818
105 | 2610801.6735 | 1229070.4699 | 2610811.6155 | 1229056.7422
106 | 2610815.0336 | 1229052.0225 | 2610811.6155 | 1229056.7422
107 | 2611212.0443 | 1228867.1764 | 2611232.9409 | 1228869.5917
108 | 2611158.4292 | 1228693.8368 | 2611124.998 | 1228713.1972
109 | 2611158.4292 | 1228693.8368 | 2611184.2179 | 1228692.6377
110 | 2611202.1012 | 1228691.8061 | 2611184.2179 | 1228692.6377
111 | 2610786.0521 | 1228836.7943 | 2610789.787 | 1228836.801 | 2610847.4819 | 1228868.374
112 | 2610877.0257 | 1228872.7248 | 2610854.7081 | 1228872.3284 | 2610847.4819 | 1228868.374
113 | 2610722.1304 | 1228915.2927 | 2610734.9654 | 1228893.2248 | 2610737.8397 | 1228887.282 | 2610743.128 | 1228882.8444 | 2610755.401 | 1228870.1033 | 2610782.0498 | 1228838.0656 | 2610786.0521 | 1228836.7943
114 | 2610877.0257 | 1228872.7248 | 2610922.7236 | 1228893.0534 | 2610936.3699 | 1228866.9088
115 | 2610722.1304 | 1228915.2927 | 2610732.709 | 1228922.1157 | 2610741.49 | 1228930.1807 | 2610766.5713 | 1228960.655 | 2610774.2806 | 1228966.3945 | 2610801.4283 | 1228980.8094
116 | 2610960.6676 | 1228820.3574 | 2610936.3699 | 1228866.9088
117 | 2610914.1633 | 1228797.4032 | 2610924.4573 | 1228802.4917 | 2610960.6676 | 1228820.3574
118 | 2610914.1633 | 1228797.4032 | 2610910.9238 | 1228795.8075 | 2610872.6555 | 1228776.9233
119 | 2610815.0336 | 1229052.0225 | 2610818.8959 | 1229046.6895
120 | 2610853.3851 | 1228961.1638 | 2610859.0445 | 1228949.8824 | 2610861.2161 | 1228951.3316
121 | 2610762.2557 | 1229274.9562 | 2610768.8644 | 1229256.4015 | 2610768.8686 | 1229254.1002 | 2610767.8902 | 1229253.74
122 | 2610758.0052 | 1229250.1005 | 2610767.8902 | 1229253.74

## bus_geodata
| x | y | coords
0 | 2610808.3923 | 1229230.1513
1 | 2610797.6214 | 1229258.3206
2 | 2610820.7521 | 1229207.9108
3 | 2610792.9541 | 1229285.6623
4 | 2610832.6875 | 1229213.9915
5 | 2610816.067 | 1229205.6787
6 | 2610777.9933 | 1229280.4931
7 | 2610799.774 | 1229288.6764
8 | 2610837.2588 | 1229216.3234
9 | 2610836.7185 | 1229240.4666
10 | 2610821.3139 | 1229194.7039
11 | 2610776.6073 | 1229193.119
12 | 2610772.8997 | 1229278.7332
13 | 2610792.1988 | 1229302.6524
14 | 2610815.1625 | 1229295.6373
15 | 2610853.3255 | 1229199.6001
16 | 2610881.1535 | 1229239.6169
17 | 2610839.8832 | 1229254.5615
18 | 2610832.889 | 1229185.1506
19 | 2610933.7017 | 1229169.6653
20 | 2610938.4624 | 1229161.3216
21 | 2610933.2475 | 1229170.4614
22 | 2610945.0756 | 1229156.0061
23 | 2610925.2105 | 1229181.8456
24 | 2610956.5796 | 1229161.8639
25 | 2610900.7418 | 1229206.0559
26 | 2610975.7756 | 1229171.3307
27 | 2610973.8516 | 1229127.1328
28 | 2610893.3322 | 1229218.7531
29 | 2610914.7423 | 1229138.9281
30 | 2610931.9243 | 1229104.8235
31 | 2610937.2151 | 1229092.8246
32 | 2610945.0666 | 1229080.6713
33 | 2610949.0028 | 1229074.5784
34 | 2610974.4794 | 1229012.6302
35 | 2610932.9445 | 1228995.9777
36 | 2611024.579 | 1228992.2889
37 | 2611046.2225 | 1228951.1814
38 | 2610920.028 | 1228975.5762
39 | 2611032.4625 | 1228945.3415
40 | 2611090.8451 | 1228966.6064
41 | 2610911.6095 | 1229038.6085
42 | 2610874.1685 | 1229019.151
43 | 2610934.1018 | 1229050.5835
44 | 2610908.7507 | 1228969.54
45 | 2611084.1453 | 1228998.9123
46 | 2611149.1785 | 1228913.3944
47 | 2610848.5038 | 1229005.8076
48 | 2610890.0087 | 1229001.5766
49 | 2610956.7235 | 1229062.6274
50 | 2610899.9659 | 1228986.2156
51 | 2611028.0147 | 1229104.1439
52 | 2611040.4559 | 1229080.8195
53 | 2611020.9509 | 1229115.0655
54 | 2611040.6109 | 1229080.5289
55 | 2611052.576 | 1229149.2553
56 | 2611004.4419 | 1229145.623
57 | 2611058.671 | 1229046.6705
58 | 2610968.1148 | 1229069.6688
59 | 2611110.5441 | 1229048.2858
60 | 2610987.4442 | 1229177.0851
61 | 2611068.0646 | 1229029.0599
62 | 2611119.7992 | 1229031.7989
63 | 2610976.8343 | 1229196.4698
64 | 2610952.81 | 1229240.3644
65 | 2610959.9671 | 1229227.2868
66 | 2610964.7655 | 1229218.52
67 | 2610906.4499 | 1229254.8504
68 | 2610904.0897 | 1229253.4291
69 | 2610867.7883 | 1229319.8142
70 | 2610856.3829 | 1229314.283
71 | 2610885.1305 | 1229242.0119
72 | 2610828.7335 | 1229301.776
73 | 2610848.0075 | 1229310.4945
74 | 2610791.1306 | 1229304.6232
75 | 2610847.8344 | 1229286.2585
76 | 2610787.8912 | 1229310.5998
77 | 2611074.705 | 1229016.6107
78 | 2610840.4604 | 1229016.9137
79 | 2610827.4184 | 1228994.6072
80 | 2610832.7768 | 1229027.5231
81 | 2610808.505 | 1228984.567
82 | 2610845.1307 | 1228977.6181
83 | 2610980.9564 | 1229112.8462
84 | 2611155.7915 | 1228885.4321
85 | 2611131.1804 | 1228904.5116
86 | 2611210.8024 | 1228920.0023
87 | 2611223.6255 | 1228998.0839
88 | 2611204.3064 | 1228889.0635
89 | 2611126.4482 | 1229000.5371
90 | 2611199.4041 | 1228865.7154
91 | 2610813.0948 | 1229106.0463
92 | 2610800.8503 | 1229097.6299
93 | 2610841.8023 | 1229137.8961
94 | 2610788.2107 | 1229089.0591
95 | 2610849.4414 | 1229168.7535
96 | 2610741.761 | 1229095.5794
97 | 2610801.6735 | 1229070.4699
98 | 2610775.3516 | 1229128.7818
99 | 2610811.6155 | 1229056.7422
100 | 2610861.303 | 1229191.2966
101 | 2611212.0443 | 1228867.1764
102 | 2611124.998 | 1228713.1972
103 | 2611232.9409 | 1228869.5917
104 | 2611158.4292 | 1228693.8368
105 | 2611184.2179 | 1228692.6377
106 | 2611202.1012 | 1228691.8061
107 | 2610847.4819 | 1228868.374
108 | 2610786.0521 | 1228836.7943
109 | 2610877.0257 | 1228872.7248
110 | 2610722.1304 | 1228915.2927
111 | 2610936.3699 | 1228866.9088
112 | 2610801.4283 | 1228980.8094
113 | 2610914.1633 | 1228797.4032
114 | 2610960.6676 | 1228820.3574
115 | 2610872.6555 | 1228776.9233
116 | 2610815.0336 | 1229052.0225
117 | 2610818.8959 | 1229046.6895
118 | 2610853.3851 | 1228961.1638
119 | 2610861.2161 | 1228951.3316
120 | 2610767.8902 | 1229253.74
121 | 2610762.2557 | 1229274.9562
122 | 2610758.0052 | 1229250.1005
123 | 2610766.8031 | 1229289.8555
124 | 2610911.6095 | 1229038.6085

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98267 | -0.33224 | 0.0016916 | 0.00042396
1 | 0.98179 | -0.3493 | 0.0019795 | 0.00049612
2 | 0.98305 | -0.32475 | 0 | 0
3 | 0.98105 | -0.36383 | 0 | 0
4 | 0.98268 | -0.33192 | 0 | 0
5 | 0.98323 | -0.32121 | 0 | 0
6 | 0.98088 | -0.36718 | 0.0019964 | 0.00050035
7 | 0.98093 | -0.36616 | 0 | 0
8 | 0.98255 | -0.33451 | 0 | 0
9 | 0.98252 | -0.33519 | 0.0046281 | 0.0011599
10 | 0.98367 | -0.31276 | 0 | 0
11 | 0.98313 | -0.32317 | 0.0026277 | 0.00065858
12 | 0.98083 | -0.36813 | 0 | 0
13 | 0.98086 | -0.36757 | 0.0018243 | 0.0004572
14 | 0.98074 | -0.36995 | 0.0037533 | 0.00094067
15 | 0.98244 | -0.33661 | 0.001763 | 0.00044185
16 | 0.98132 | -0.35854 | 0 | 0
17 | 0.98249 | -0.33573 | 0.0020896 | 0.0005237
18 | 0.98421 | -0.30223 | 0.0027116 | 0.00067959
19 | 0.97925 | -0.39898 | 0.0020457 | 0.0005127
20 | 0.97904 | -0.40306 | 0.0021804 | 0.00054646
21 | 0.97927 | -0.39858 | 0.0011495 | 0.00028808
22 | 0.97884 | -0.40692 | 0.0018434 | 0.00046201
23 | 0.97958 | -0.39239 | 0.0020301 | 0.00050878
24 | 0.97857 | -0.41217 | 0 | 0
25 | 0.9804 | -0.37637 | 0.00096594 | 0.00024209
26 | 0.97816 | -0.42033 | 0.0013949 | 0.00034959
27 | 0.97837 | -0.41615 | 0.0016686 | 0.00041819
28 | 0.98074 | -0.36974 | 0.002747 | 0.00068846
29 | 0.99832 | -0.032295 | 0.0076152 | 0.0019086
30 | 0.99869 | -0.025275 | 0.0011233 | 0.00028152
31 | 0.9988 | -0.022981 | 0.0027196 | 0.0006816
32 | 0.99896 | -0.020085 | 0.0042552 | 0.0010664
33 | 0.99906 | -0.018094 | 0.0025911 | 0.00064939
34 | 0.99349 | -0.12428 | 0.012601 | 0.0031581
35 | 0.99402 | -0.114 | 0 | 0
36 | 0.97429 | -0.49642 | 0.00331 | 0.00082956
37 | 0.97443 | -0.49359 | 0 | 0
38 | 0.99436 | -0.10748 | 0.0025371 | 0.00063587
39 | 0.97432 | -0.49589 | 0.0083718 | 0.0020982
40 | 0.97495 | -0.48346 | 0 | 0
41 | 0.99842 | -0.029932 | 0 | 0
42 | 0.9958 | -0.079592 | 0 | 0
43 | 1 | 0 | -0.30517 | -0.077647
44 | 0.99454 | -0.10407 | 0 | 0
45 | 0.97512 | -0.48014 | 0.0024172 | 0.00060581
46 | 0.97405 | -0.50111 | 0 | 0
47 | 0.9942 | -0.1101 | 0 | 0
48 | 0.99518 | -0.091628 | 0.0060923 | 0.0015269
49 | 0.9993 | -0.013546 | 0 | 0
50 | 0.9948 | -0.09904 | 0.0076908 | 0.0019275
51 | 0.9764 | -0.4548 | 0.00081233 | 0.00020359
52 | 0.97596 | -0.4635 | 0.004436 | 0.0011118
53 | 0.97662 | -0.45046 | 0 | 0
54 | 0.97595 | -0.4636 | 0.01869 | 0.0046842
55 | 0.97657 | -0.45144 | 0 | 0
56 | 0.97725 | -0.43819 | 0.0021424 | 0.00053694
57 | 0.97552 | -0.47219 | 0.0043055 | 0.0010791
58 | 0.99915 | -0.016351 | 0.011996 | 0.0030065
59 | 0.97645 | -0.45389 | 0.0027517 | 0.00068964
60 | 0.97791 | -0.42521 | 0 | 0
61 | 0.97531 | -0.47626 | 0.018353 | 0.0045996
62 | 0.97642 | -0.45452 | 0.0018363 | 0.00046021
63 | 0.97785 | -0.42633 | 0.0015192 | 0.00038075
64 | 0.97781 | -0.4272 | 0.00063791 | 0.00015988
65 | 0.97782 | -0.42703 | 0 | 0
66 | 0.97782 | -0.42691 | 0.00062355 | 0.00015628
67 | 0.98124 | -0.35999 | 0.0012117 | 0.00030367
68 | 0.98124 | -0.35993 | 0.001228 | 0.00030776
69 | 0.98039 | -0.37676 | 0.0032629 | 0.00081777
70 | 0.98043 | -0.37601 | 0 | 0
71 | 0.98129 | -0.35895 | 0.0024223 | 0.00060709
72 | 0.98062 | -0.37228 | 0.0012438 | 0.00031172
73 | 0.98048 | -0.37511 | 0.0019839 | 0.00049721
74 | 0.98086 | -0.36769 | 0.0012473 | 0.00031261
75 | 0.98037 | -0.37715 | 0.0021382 | 0.00053589
76 | 0.98084 | -0.36792 | 0.0018203 | 0.00045622
77 | 0.97523 | -0.47795 | 0.0024247 | 0.00060769
78 | 0.99361 | -0.12143 | 0.0012791 | 0.00032057
79 | 0.99391 | -0.11568 | 0 | 0
80 | 0.99304 | -0.13218 | 0.0068454 | 0.0017156
81 | 0.99373 | -0.11911 | 0 | 0
82 | 0.99354 | -0.12288 | 0.0064632 | 0.0016198
83 | 0.97831 | -0.4173 | 0.003964 | 0.00099346
84 | 0.97405 | -0.5012 | 0.00016836 | 4.2195e-05
85 | 0.97397 | -0.50274 | 0.0044043 | 0.0011038
86 | 0.97375 | -0.50713 | 0 | 0
87 | 0.97372 | -0.50781 | 0 | 0
88 | 0.97362 | -0.50981 | 0.0010426 | 0.0002613
89 | 0.97367 | -0.50866 | 0.00046668 | 0.00011696
90 | 0.97354 | -0.51137 | 0 | 0
91 | 0.98885 | -0.21264 | 0.0028554 | 0.00071564
92 | 0.9894 | -0.20198 | 0.0019177 | 0.00048063
93 | 0.98723 | -0.24375 | 0 | 0
94 | 0.98998 | -0.1909 | 0 | 0
95 | 0.98506 | -0.28579 | 0.0012917 | 0.00032372
96 | 0.98987 | -0.19307 | 0 | 0
97 | 0.99088 | -0.1735 | 0.0014749 | 0.00036963
98 | 0.9897 | -0.1963 | 0.0076277 | 0.0019117
99 | 0.99156 | -0.16056 | 0.002177 | 0.00054562
100 | 0.98241 | -0.33729 | 0.0032503 | 0.0008146
101 | 0.97353 | -0.51153 | 0.00053729 | 0.00013466
102 | 0.97308 | -0.52035 | 0.00083006 | 0.00020803
103 | 0.97353 | -0.51159 | 0.00015076 | 3.7784e-05
104 | 0.97301 | -0.5218 | 0 | 0
105 | 0.97296 | -0.52277 | 0.00073217 | 0.0001835
106 | 0.97294 | -0.5232 | 0.0013079 | 0.0003278
107 | 0.98747 | -0.23961 | 0.00078225 | 0.00019605
108 | 0.98939 | -0.20251 | 0 | 0
109 | 0.98665 | -0.25554 | 0 | 0
110 | 0.99223 | -0.14799 | 0 | 0
111 | 0.98452 | -0.29711 | 0.010432 | 0.0026146
112 | 0.99367 | -0.12039 | 0.0064598 | 0.001619
113 | 0.98272 | -0.33223 | 0 | 0
114 | 0.98361 | -0.31478 | 0 | 0
115 | 0.98192 | -0.34786 | 0.018699 | 0.0046864
116 | 0.9918 | -0.15606 | 0.001794 | 0.00044962
117 | 0.99206 | -0.15092 | 0.0029237 | 0.00073274
118 | 0.99337 | -0.12619 | 0.0073831 | 0.0018504
119 | 0.99333 | -0.12694 | 0.0027858 | 0.00069818
120 | 0.98058 | -0.37301 | 0.0023633 | 0.0005923
121 | 0.98075 | -0.36973 | 0 | 0
122 | 0.98053 | -0.37406 | 0.0054966 | 0.0013776
123 | 0.98081 | -0.36855 | 0.0018235 | 0.00045702
124 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.03099 | 0.0077855 | -0.030965 | -0.0077697 | 2.5207e-05 | 1.5746e-05 | 0.046934 | 0.046934 | 0.046934 | 0.98267 | -0.33224 | 0.98179 | -0.3493 | 12.894
1 | -0.032682 | -0.0082094 | 0.032694 | 0.0082163 | 1.1687e-05 | 6.835e-06 | 0.049496 | 0.049495 | 0.049496 | 0.98267 | -0.33224 | 0.98305 | -0.32475 | 6.7988
2 | 0.028985 | 0.0072736 | -0.028965 | -0.0072611 | 2.0077e-05 | 1.2499e-05 | 0.043934 | 0.043934 | 0.043934 | 0.98179 | -0.3493 | 0.98105 | -0.36383 | 12.0698
3 | 0.11954 | 0.030179 | -0.11949 | -0.030153 | 4.1053e-05 | 2.5596e-05 | 0.18102 | 0.18102 | 0.18102 | 0.98305 | -0.32475 | 0.98268 | -0.33192 | 12.4325
4 | -0.15223 | -0.038395 | 0.15225 | 0.038411 | 2.5789e-05 | 1.6242e-05 | 0.23051 | 0.23051 | 0.23051 | 0.98305 | -0.32475 | 0.98323 | -0.32121 | 15.8318
5 | 0.011684 | 0.0029291 | -0.011683 | -0.0029281 | 1.8644e-06 | 9.9337e-07 | 0.017723 | 0.017723 | 0.017723 | 0.98105 | -0.36383 | 0.98088 | -0.36718 | 4.8689
6 | 0.017281 | 0.004332 | -0.017279 | -0.0043309 | 1.9163e-06 | 1.1325e-06 | 0.026211 | 0.026211 | 0.026211 | 0.98105 | -0.36383 | 0.98093 | -0.36616 | 7.2009
7 | 0.11278 | 0.028469 | -0.11276 | -0.028461 | 1.401e-05 | 8.7069e-06 | 0.17084 | 0.17084 | 0.17084 | 0.98268 | -0.33192 | 0.98255 | -0.33451 | 11.7337
8 | 0.0067188 | 0.0016838 | -0.0067177 | -0.0016835 | 1.0466e-06 | 3.2829e-07 | 0.010174 | 0.010174 | 0.010174 | 0.98268 | -0.33192 | 0.98252 | -0.33519 | 2.795
9 | -0.15488 | -0.03907 | 0.15495 | 0.039109 | 6.2683e-05 | 3.95e-05 | 0.23449 | 0.23449 | 0.23449 | 0.98323 | -0.32121 | 0.98367 | -0.31276 | 16.105
10 | 0.002628 | 0.00065821 | -0.0026277 | -0.00065858 | 2.4588e-07 | -3.6834e-07 | 0.003977 | 0.0039772 | 0.0039772 | 0.98323 | -0.32121 | 0.98313 | -0.32317 | 1.0926
11 | 0.0096861 | 0.0024278 | -0.0096856 | -0.0024276 | 4.3634e-07 | 2.1124e-07 | 0.014694 | 0.014694 | 0.014694 | 0.98088 | -0.36718 | 0.98083 | -0.36813 | 4.0368
12 | 0.0048923 | 0.001226 | -0.004892 | -0.0012259 | 3.2833e-07 | 9.4651e-09 | 0.0074213 | 0.0074214 | 0.0074214 | 0.98093 | -0.36616 | 0.98086 | -0.36757 | 2.0388
13 | 0.012387 | 0.0031049 | -0.012385 | -0.0031037 | 2.2362e-06 | 1.218e-06 | 0.01879 | 0.01879 | 0.01879 | 0.98093 | -0.36616 | 0.98074 | -0.36995 | 5.1622
14 | 0.0050139 | 0.0012564 | -0.0050134 | -0.0012564 | 5.0142e-07 | 2.7222e-08 | 0.0075932 | 0.0075933 | 0.0075933 | 0.98255 | -0.33451 | 0.98244 | -0.33661 | 2.0861
15 | 0.10775 | 0.027204 | -0.10762 | -0.027128 | 0.00012388 | 7.6771e-05 | 0.16325 | 0.16325 | 0.16325 | 0.98255 | -0.33451 | 0.98132 | -0.35854 | 11.2123
16 | 0.0020896 | 0.00052355 | -0.0020896 | -0.0005237 | 5.4256e-08 | -1.4822e-07 | 0.0031647 | 0.0031648 | 0.0031648 | 0.98252 | -0.33519 | 0.98249 | -0.33573 | 0.86944
17 | -0.15495 | -0.039109 | 0.15502 | 0.039158 | 7.8205e-05 | 4.928e-05 | 0.23449 | 0.23449 | 0.23449 | 0.98367 | -0.31276 | 0.98421 | -0.30223 | 16.105
18 | 0.0018236 | 0.00045689 | -0.0018235 | -0.00045702 | 3.6403e-08 | -1.3678e-07 | 0.0027665 | 0.0027665 | 0.0027665 | 0.98083 | -0.36813 | 0.98081 | -0.36855 | 0.76004
19 | 0.0078621 | 0.0019707 | -0.0078615 | -0.0019704 | 6.0099e-07 | 2.4247e-07 | 0.011928 | 0.011928 | 0.011928 | 0.98083 | -0.36813 | 0.98075 | -0.36973 | 3.2768
20 | 0.0030677 | 0.00076874 | -0.0030677 | -0.00076876 | 1.8207e-08 | -1.6642e-08 | 0.0046539 | 0.0046539 | 0.0046539 | 0.98086 | -0.36757 | 0.98086 | -0.36769 | 1.2785
21 | 0.0086312 | 0.002163 | -0.0086303 | -0.0021626 | 9.5789e-07 | 4.2512e-07 | 0.013096 | 0.013096 | 0.013096 | 0.98074 | -0.36995 | 0.98062 | -0.37228 | 3.5977
22 | 0.0032504 | 0.00081452 | -0.0032503 | -0.0008146 | 1.0465e-07 | -7.8822e-08 | 0.0049231 | 0.0049231 | 0.0049231 | 0.98244 | -0.33661 | 0.98241 | -0.33729 | 1.3525
23 | 0.0048622 | 0.0012183 | -0.0048621 | -0.0012183 | 9.463e-08 | 1.9129e-09 | 0.0073726 | 0.0073727 | 0.0073727 | 0.98132 | -0.35854 | 0.98129 | -0.35895 | 2.0255
24 | 0.10276 | 0.025909 | -0.10271 | -0.025875 | 5.5031e-05 | 3.4e-05 | 0.15588 | 0.15588 | 0.15588 | 0.98132 | -0.35854 | 0.98074 | -0.36974 | 10.7059
25 | -0.15774 | -0.039838 | 0.15786 | 0.039916 | 0.00012434 | 7.8391e-05 | 0.23859 | 0.23859 | 0.23859 | 0.98421 | -0.30223 | 0.98506 | -0.28579 | 16.3865
26 | 0.09363 | 0.02355 | -0.093612 | -0.023539 | 1.8238e-05 | 1.1189e-05 | 0.14231 | 0.14231 | 0.14231 | 0.97925 | -0.39898 | 0.97904 | -0.40306 | 9.7738
27 | -0.095676 | -0.024063 | 0.095678 | 0.024064 | 1.8168e-06 | 1.1166e-06 | 0.14542 | 0.14542 | 0.14542 | 0.97925 | -0.39898 | 0.97927 | -0.39858 | 9.9873
28 | 0.091432 | 0.022992 | -0.091415 | -0.022982 | 1.6866e-05 | 1.0326e-05 | 0.13899 | 0.13899 | 0.13899 | 0.97904 | -0.40306 | 0.97884 | -0.40692 | 9.5462
29 | -0.096827 | -0.024352 | 0.096856 | 0.02437 | 2.8674e-05 | 1.7641e-05 | 0.14716 | 0.14716 | 0.14716 | 0.97927 | -0.39858 | 0.97958 | -0.39239 | 10.1073
30 | 0.089572 | 0.02252 | -0.089549 | -0.022506 | 2.2448e-05 | 1.3718e-05 | 0.13619 | 0.13619 | 0.13619 | 0.97884 | -0.40692 | 0.97857 | -0.41217 | 9.3538
31 | -0.098886 | -0.024878 | 0.098962 | 0.024925 | 7.573e-05 | 4.6664e-05 | 0.15025 | 0.15024 | 0.15025 | 0.97958 | -0.39239 | 0.9804 | -0.37637 | 10.319
32 | 0.083915 | 0.021095 | -0.083883 | -0.021075 | 3.2683e-05 | 1.9842e-05 | 0.12762 | 0.12762 | 0.12762 | 0.97857 | -0.41217 | 0.97816 | -0.42033 | 8.7654
33 | 0.0056338 | 0.0014118 | -0.0056328 | -0.0014116 | 1.0675e-06 | 1.9601e-07 | 0.0085667 | 0.0085669 | 0.0085669 | 0.97857 | -0.41217 | 0.97837 | -0.41615 | 2.3535
34 | -0.099928 | -0.025167 | 0.09996 | 0.025187 | 3.1721e-05 | 1.956e-05 | 0.15171 | 0.15171 | 0.15171 | 0.9804 | -0.37637 | 0.98074 | -0.36974 | 10.4197
35 | 0.082488 | 0.020725 | -0.082468 | -0.020714 | 1.9212e-05 | 1.1642e-05 | 0.1255 | 0.1255 | 0.1255 | 0.97816 | -0.42033 | 0.97791 | -0.42521 | 8.6197
36 | 0.0039642 | 0.0009934 | -0.003964 | -0.00099346 | 2.175e-07 | -6.1158e-08 | 0.0060291 | 0.0060292 | 0.0060292 | 0.97837 | -0.41615 | 0.97831 | -0.4173 | 1.6564
37 | -0.0076152 | -0.0019086 | 0.0076178 | 0.0019095 | 2.5472e-06 | 9.406e-07 | 0.011351 | 0.01135 | 0.011351 | 0.99832 | -0.032295 | 0.99869 | -0.025275 | 3.1183
38 | -0.0087411 | -0.002191 | 0.008742 | 0.0021914 | 9.5532e-07 | 4.1487e-07 | 0.013024 | 0.013024 | 0.013024 | 0.99869 | -0.025275 | 0.9988 | -0.022981 | 3.578
39 | -0.011462 | -0.002873 | 0.011463 | 0.0028739 | 1.5821e-06 | 8.2312e-07 | 0.017076 | 0.017076 | 0.017076 | 0.9988 | -0.022981 | 0.99896 | -0.020085 | 4.6911
40 | -0.015718 | -0.0039403 | 0.01572 | 0.0039412 | 1.4912e-06 | 8.5941e-07 | 0.023414 | 0.023414 | 0.023414 | 0.99896 | -0.020085 | 0.99906 | -0.018094 | 6.4324
41 | -0.018311 | -0.0045906 | 0.018315 | 0.0045929 | 3.9687e-06 | 2.3536e-06 | 0.027273 | 0.027273 | 0.027273 | 0.99906 | -0.018094 | 0.9993 | -0.013546 | 7.4926
42 | -0.012601 | -0.0031581 | 0.012607 | 0.0031614 | 6.1753e-06 | 3.3532e-06 | 0.018873 | 0.018873 | 0.018873 | 0.99349 | -0.12428 | 0.99402 | -0.114 | 5.185
43 | -0.012607 | -0.0031614 | 0.012611 | 0.0031636 | 3.9171e-06 | 2.1267e-06 | 0.018873 | 0.018873 | 0.018873 | 0.99402 | -0.114 | 0.99436 | -0.10748 | 5.1849
44 | -0.00331 | -0.00082956 | 0.0033104 | 0.00082927 | 4.4529e-07 | -2.9376e-07 | 0.0050553 | 0.0050551 | 0.0050553 | 0.97429 | -0.49642 | 0.97443 | -0.49359 | 1.3888
45 | 0.0083728 | 0.0020986 | -0.0083718 | -0.0020982 | 9.1636e-07 | 4.0029e-07 | 0.012786 | 0.012786 | 0.012786 | 0.97443 | -0.49359 | 0.97432 | -0.49589 | 3.5126
46 | -0.011683 | -0.0029279 | 0.011689 | 0.0029309 | 5.6413e-06 | 3.0214e-06 | 0.017841 | 0.017841 | 0.017841 | 0.97443 | -0.49359 | 0.97495 | -0.48346 | 4.9013
47 | -0.015148 | -0.0037994 | 0.015151 | 0.0038008 | 2.4651e-06 | 1.4117e-06 | 0.02267 | 0.02267 | 0.02267 | 0.99436 | -0.10748 | 0.99454 | -0.10407 | 6.2279
48 | -0.021341 | -0.0053457 | 0.021345 | 0.0053461 | 3.3767e-06 | 4.6726e-07 | 0.032571 | 0.032571 | 0.032571 | 0.97495 | -0.48346 | 0.97512 | -0.48014 | 2.237
49 | 0.0096524 | 0.0024148 | -0.0096443 | -0.0024109 | 8.1013e-06 | 3.9445e-06 | 0.014731 | 0.014731 | 0.014731 | 0.97495 | -0.48346 | 0.97405 | -0.50111 | 4.047
50 | 0.27279 | 0.069782 | -0.27213 | -0.069366 | 0.00065397 | 0.00041634 | 0.40706 | 0.40706 | 0.40706 | 0.99842 | -0.029932 | 0.9958 | -0.079592 | 27.9574
51 | -0.27279 | -0.069782 | 0.27318 | 0.070034 | 0.00039583 | 0.000252 | 0.40706 | 0.40706 | 0.40706 | 0.99842 | -0.029932 | 1 | 0 | 27.9573
52 | 0.24317 | 0.062093 | -0.24281 | -0.061866 | 0.00035805 | 0.00022765 | 0.36378 | 0.36378 | 0.36378 | 0.9958 | -0.079592 | 0.9942 | -0.1101 | 24.9848
53 | 0.028962 | 0.0072726 | -0.028945 | -0.0072622 | 1.6621e-05 | 1.033e-05 | 0.043283 | 0.043283 | 0.043283 | 0.9958 | -0.079592 | 0.99518 | -0.091628 | 11.8908
54 | 0.030332 | 0.0076125 | -0.030313 | -0.0076003 | 1.9582e-05 | 1.2196e-05 | 0.045139 | 0.045139 | 0.045139 | 1 | 0 | 0.9993 | -0.013546 | 12.4008
55 | -0.015151 | -0.0038008 | 0.015154 | 0.0038029 | 3.6323e-06 | 2.08e-06 | 0.02267 | 0.022669 | 0.02267 | 0.99454 | -0.10407 | 0.9948 | -0.09904 | 6.2279
56 | -0.023762 | -0.005952 | 0.023764 | 0.0059525 | 2.4723e-06 | 5.8129e-07 | 0.036259 | 0.036259 | 0.036259 | 0.97512 | -0.48014 | 0.97523 | -0.47795 | 2.4903
57 | 0.0044047 | 0.0011038 | -0.0044043 | -0.0011038 | 3.4077e-07 | -3.171e-08 | 0.0067287 | 0.0067288 | 0.0067288 | 0.97405 | -0.50111 | 0.97397 | -0.50274 | 1.8486
58 | 0.0050713 | 0.0012652 | -0.0050699 | -0.0012651 | 1.4477e-06 | 1.2575e-07 | 0.0077452 | 0.0077454 | 0.0077454 | 0.97405 | -0.50111 | 0.97375 | -0.50713 | 2.1279
59 | 0.00016836 | 4.1838e-05 | -0.00016836 | -4.2195e-05 | 7.1241e-10 | -3.572e-07 | 0.00025707 | 0.0002572 | 0.0002572 | 0.97405 | -0.50111 | 0.97405 | -0.5012 | 0.070658
60 | 0.18948 | 0.048383 | -0.18938 | -0.048318 | 0.00010363 | 6.561e-05 | 0.28391 | 0.28391 | 0.28391 | 0.9942 | -0.1101 | 0.99361 | -0.12143 | 19.4995
61 | 0.053334 | 0.013483 | -0.053319 | -0.013475 | 1.4245e-05 | 7.8816e-06 | 0.079865 | 0.079866 | 0.079866 | 0.9942 | -0.1101 | 0.99391 | -0.11568 | 5.4853
62 | 0.022853 | 0.0057353 | -0.022845 | -0.0057304 | 8.0744e-06 | 4.9282e-06 | 0.034173 | 0.034173 | 0.034173 | 0.99518 | -0.091628 | 0.9948 | -0.09904 | 9.3883
63 | 0.011998 | 0.0030074 | -0.011996 | -0.0030065 | 1.6029e-06 | 8.5046e-07 | 0.017866 | 0.017866 | 0.017866 | 0.9993 | -0.013546 | 0.99915 | -0.016351 | 4.9082
64 | 0.072034 | 0.018069 | -0.072005 | -0.018051 | 2.987e-05 | 1.7795e-05 | 0.10978 | 0.10978 | 0.10978 | 0.9764 | -0.4548 | 0.97596 | -0.4635 | 7.5402
65 | -0.072847 | -0.018273 | 0.072862 | 0.018281 | 1.5062e-05 | 8.9875e-06 | 0.11102 | 0.11102 | 0.11102 | 0.9764 | -0.4548 | 0.97662 | -0.45046 | 7.6252
66 | 0.067569 | 0.016939 | -0.067568 | -0.016939 | 3.2769e-07 | 1.9326e-07 | 0.10302 | 0.10302 | 0.10302 | 0.97596 | -0.4635 | 0.97595 | -0.4636 | 7.0757
67 | 0.0045888 | 0.001142 | -0.0045886 | -0.0011442 | 2.1301e-07 | -2.1917e-06 | 0.0069888 | 0.0069896 | 0.0069896 | 0.97662 | -0.45046 | 0.97657 | -0.45144 | 0.48005
68 | -0.077451 | -0.019423 | 0.077496 | 0.019451 | 4.5346e-05 | 2.7282e-05 | 0.11801 | 0.11801 | 0.11801 | 0.97662 | -0.45046 | 0.97725 | -0.43819 | 8.1051
69 | 0.048878 | 0.012255 | -0.048858 | -0.012244 | 1.9981e-05 | 1.0871e-05 | 0.074525 | 0.074526 | 0.074526 | 0.97595 | -0.4636 | 0.97552 | -0.47219 | 5.1185
70 | 0.0045886 | 0.0011442 | -0.004588 | -0.0011497 | 5.3343e-07 | -5.485e-06 | 0.0069896 | 0.0069917 | 0.0069917 | 0.97657 | -0.45144 | 0.97645 | -0.45389 | 0.4802
71 | -0.079638 | -0.019988 | 0.079688 | 0.020017 | 4.9305e-05 | 2.9762e-05 | 0.12127 | 0.12127 | 0.12127 | 0.97725 | -0.43819 | 0.97791 | -0.42521 | 8.3292
72 | 0.044553 | 0.011165 | -0.044544 | -0.011161 | 8.6418e-06 | 4.5342e-06 | 0.067958 | 0.067959 | 0.067959 | 0.97552 | -0.47219 | 0.97531 | -0.47626 | 4.6675
73 | 0.0018363 | 0.00046001 | -0.0018363 | -0.00046021 | 5.5522e-08 | -2.0096e-07 | 0.0027983 | 0.0027984 | 0.0027984 | 0.97645 | -0.45389 | 0.97642 | -0.45452 | 0.76879
74 | 0.0027809 | 0.00069612 | -0.0027807 | -0.0006963 | 1.4836e-07 | -1.8228e-07 | 0.0042311 | 0.0042312 | 0.0042312 | 0.97791 | -0.42521 | 0.97785 | -0.42633 | 1.1624
75 | 0.026191 | 0.0065609 | -0.026189 | -0.0065602 | 2.112e-06 | 6.4743e-07 | 0.039958 | 0.039958 | 0.039958 | 0.97531 | -0.47626 | 0.97523 | -0.47795 | 2.7444
76 | 0.0012615 | 0.00031555 | -0.0012615 | -0.00031585 | 3.4731e-08 | -2.9309e-07 | 0.0019194 | 0.0019196 | 0.0019196 | 0.97785 | -0.42633 | 0.97782 | -0.42691 | 0.52735
77 | -0.00063791 | -0.00015988 | 0.00063792 | 0.00015969 | 5.268e-09 | -1.8363e-07 | 0.00097077 | 0.0009707 | 0.00097077 | 0.97781 | -0.4272 | 0.97782 | -0.42703 | 0.26669
78 | -0.00063792 | -0.00015969 | 0.00063792 | 0.00015957 | 3.5312e-09 | -1.231e-07 | 0.0009707 | 0.00097066 | 0.0009707 | 0.97782 | -0.42703 | 0.97782 | -0.42691 | 0.26668
79 | -0.0012117 | -0.00030367 | 0.0012117 | 0.00030364 | 3.4881e-09 | -3.257e-08 | 0.0018374 | 0.0018374 | 0.0018374 | 0.98124 | -0.35999 | 0.98124 | -0.35993 | 0.50479
80 | -0.0024396 | -0.00061139 | 0.0024397 | 0.00061119 | 1.1359e-07 | -2.0688e-07 | 0.0036996 | 0.0036995 | 0.0036996 | 0.98124 | -0.35993 | 0.98129 | -0.35895 | 1.0164
81 | -0.0032629 | -0.00081777 | 0.003263 | 0.00081768 | 1.1658e-07 | -8.5234e-08 | 0.0049524 | 0.0049523 | 0.0049524 | 0.98039 | -0.37676 | 0.98043 | -0.37601 | 1.3605
82 | 0.0021383 | 0.00053559 | -0.0021382 | -0.00053589 | 1.1572e-07 | -2.9541e-07 | 0.0032453 | 0.0032454 | 0.0032454 | 0.98043 | -0.37601 | 0.98037 | -0.37715 | 0.89159
83 | -0.0054014 | -0.0013533 | 0.0054016 | 0.0013533 | 2.3165e-07 | 3.2326e-08 | 0.0081976 | 0.0081975 | 0.0081976 | 0.98043 | -0.37601 | 0.98048 | -0.37511 | 2.2521
84 | 0.0073865 | 0.0018509 | -0.0073855 | -0.0018505 | 9.9657e-07 | 3.7097e-07 | 0.011208 | 0.011208 | 0.011208 | 0.98062 | -0.37228 | 0.98048 | -0.37511 | 3.0792
85 | 0.0018204 | 0.00045615 | -0.0018203 | -0.00045622 | 1.9441e-08 | -7.3359e-08 | 0.0027616 | 0.0027616 | 0.0027616 | 0.98086 | -0.36769 | 0.98084 | -0.36792 | 0.75868
86 | 0.1881 | 0.047997 | -0.188 | -0.047935 | 9.7661e-05 | 6.1824e-05 | 0.282 | 0.282 | 0.282 | 0.99361 | -0.12143 | 0.99304 | -0.13218 | 19.368
87 | 0.03668 | 0.0093024 | -0.036674 | -0.0092996 | 6.0488e-06 | 2.7638e-06 | 0.054953 | 0.054954 | 0.054954 | 0.99391 | -0.11568 | 0.99373 | -0.11911 | 3.7743
88 | 0.016639 | 0.0041724 | -0.016634 | -0.004169 | 5.712e-06 | 3.3377e-06 | 0.024912 | 0.024912 | 0.024912 | 0.99391 | -0.11568 | 0.99354 | -0.12288 | 6.844
89 | 0.18115 | 0.04622 | -0.18099 | -0.046116 | 0.00016383 | 0.00010363 | 0.27174 | 0.27174 | 0.27174 | 0.99304 | -0.13218 | 0.99206 | -0.15092 | 18.6635
90 | 0.036674 | 0.0092996 | -0.036672 | -0.0092986 | 2.2685e-06 | 1.0366e-06 | 0.054954 | 0.054954 | 0.054954 | 0.99373 | -0.11911 | 0.99367 | -0.12039 | 3.7743
91 | 0.010171 | 0.0025492 | -0.010169 | -0.0025484 | 1.6017e-06 | 7.8676e-07 | 0.015232 | 0.015233 | 0.015233 | 0.99354 | -0.12288 | 0.99337 | -0.12619 | 4.1848
92 | 0.00046671 | 0.00011477 | -0.0004667 | -0.00011575 | 1.5083e-08 | -9.7565e-07 | 0.00071241 | 0.00071276 | 0.00071276 | 0.97375 | -0.50713 | 0.97372 | -0.50781 | 0.19581
93 | 0.0046032 | 0.0011503 | -0.0046026 | -0.0011504 | 5.864e-07 | -1.7905e-08 | 0.007033 | 0.0070332 | 0.0070332 | 0.97375 | -0.50713 | 0.97362 | -0.50981 | 1.9322
94 | 0.0004667 | 0.00011575 | -0.00046668 | -0.00011696 | 1.8795e-08 | -1.2143e-06 | 0.00071276 | 0.0007132 | 0.0007132 | 0.97372 | -0.50781 | 0.97367 | -0.50866 | 0.19593
95 | 0.00356 | 0.00088905 | -0.0035597 | -0.00088918 | 2.6474e-07 | -1.2724e-07 | 0.0054397 | 0.0054398 | 0.0054398 | 0.97362 | -0.50981 | 0.97354 | -0.51137 | 1.4945
96 | 0.00068806 | 0.00017203 | -0.00068805 | -0.00017218 | 5.2762e-09 | -1.5484e-07 | 0.0010515 | 0.0010516 | 0.0010516 | 0.97354 | -0.51137 | 0.97353 | -0.51153 | 0.2889
97 | 0.0028717 | 0.00071715 | -0.0028704 | -0.00071848 | 1.2257e-06 | -1.3246e-06 | 0.0043883 | 0.0043891 | 0.0043891 | 0.97354 | -0.51137 | 0.97308 | -0.52035 | 1.2058
98 | -0.16257 | -0.041309 | 0.16265 | 0.041362 | 8.351e-05 | 5.2684e-05 | 0.24483 | 0.24483 | 0.24483 | 0.98885 | -0.21264 | 0.9894 | -0.20198 | 16.8155
99 | 0.15971 | 0.040593 | -0.15947 | -0.040443 | 0.00023886 | 0.00015062 | 0.24054 | 0.24054 | 0.24054 | 0.98885 | -0.21264 | 0.98723 | -0.24375 | 16.5204
100 | -0.16457 | -0.041842 | 0.16466 | 0.041898 | 8.7854e-05 | 5.5442e-05 | 0.24772 | 0.24772 | 0.24772 | 0.9894 | -0.20198 | 0.98998 | -0.1909 | 17.0135
101 | 0.15947 | 0.040443 | -0.15915 | -0.04024 | 0.00032166 | 0.00020283 | 0.24054 | 0.24054 | 0.24054 | 0.98723 | -0.24375 | 0.98506 | -0.28579 | 16.5205
102 | 0.0076297 | 0.0019084 | -0.0076289 | -0.0019112 | 7.893e-07 | -2.7873e-06 | 0.011467 | 0.011468 | 0.011468 | 0.98998 | -0.1909 | 0.98987 | -0.19307 | 0.78763
103 | -0.17229 | -0.043806 | 0.17243 | 0.043898 | 0.00014455 | 9.1329e-05 | 0.25918 | 0.25918 | 0.25918 | 0.98998 | -0.1909 | 0.99088 | -0.1735 | 17.8011
104 | 0.0076289 | 0.0019112 | -0.0076277 | -0.0019117 | 1.1734e-06 | -4.7219e-07 | 0.011468 | 0.011468 | 0.011468 | 0.98987 | -0.19307 | 0.9897 | -0.1963 | 1.5753
105 | -0.17391 | -0.044267 | 0.17401 | 0.044336 | 0.00010858 | 6.8615e-05 | 0.2614 | 0.2614 | 0.2614 | 0.99088 | -0.1735 | 0.99156 | -0.16056 | 17.9531
106 | -0.17619 | -0.044881 | 0.17623 | 0.044906 | 3.8269e-05 | 2.4191e-05 | 0.26466 | 0.26466 | 0.26466 | 0.99156 | -0.16056 | 0.9918 | -0.15606 | 18.1775
107 | 0.00015076 | 3.7523e-05 | -0.00015076 | -3.7784e-05 | 4.187e-10 | -2.6129e-07 | 0.00023034 | 0.00023043 | 0.00023043 | 0.97353 | -0.51153 | 0.97353 | -0.51159 | 0.063306
108 | 0.0020404 | 0.00051044 | -0.0020402 | -0.00051083 | 1.4101e-07 | -3.8963e-07 | 0.0031198 | 0.0031199 | 0.0031199 | 0.97308 | -0.52035 | 0.97301 | -0.5218 | 0.85712
109 | 0.0020402 | 0.00051083 | -0.0020401 | -0.00051109 | 9.424e-08 | -2.6033e-07 | 0.0031199 | 0.00312 | 0.00312 | 0.97301 | -0.5218 | 0.97296 | -0.52277 | 0.85716
110 | 0.001308 | 0.0003276 | -0.0013079 | -0.0003278 | 2.6863e-08 | -2.0514e-07 | 0.0020003 | 0.0020004 | 0.0020004 | 0.97296 | -0.52277 | 0.97294 | -0.5232 | 0.54955
111 | -0.030039 | -0.0075742 | 0.030093 | 0.0076075 | 5.3443e-05 | 3.3313e-05 | 0.045282 | 0.045282 | 0.045282 | 0.98747 | -0.23961 | 0.98939 | -0.20251 | 12.4402
112 | 0.029257 | 0.0073781 | -0.029235 | -0.0073642 | 2.229e-05 | 1.3875e-05 | 0.044103 | 0.044104 | 0.044104 | 0.98747 | -0.23961 | 0.98665 | -0.25554 | 12.1164
113 | -0.030093 | -0.0076075 | 0.030172 | 0.0076566 | 7.8887e-05 | 4.9167e-05 | 0.045282 | 0.045281 | 0.045282 | 0.98939 | -0.20251 | 0.99223 | -0.14799 | 12.4401
114 | 0.029235 | 0.0073642 | -0.029177 | -0.0073281 | 5.7995e-05 | 3.6104e-05 | 0.044104 | 0.044104 | 0.044104 | 0.98665 | -0.25554 | 0.98452 | -0.29711 | 12.1165
115 | -0.030172 | -0.0076566 | 0.030212 | 0.0076796 | 4.0108e-05 | 2.297e-05 | 0.045281 | 0.04528 | 0.045281 | 0.99223 | -0.14799 | 0.99367 | -0.12039 | 6.22
116 | 0.018744 | 0.0047135 | -0.018729 | -0.0047041 | 1.5811e-05 | 9.4522e-06 | 0.028336 | 0.028337 | 0.028337 | 0.98452 | -0.29711 | 0.98361 | -0.31478 | 7.7848
117 | -0.018713 | -0.0046948 | 0.018729 | 0.0047041 | 1.558e-05 | 9.3148e-06 | 0.028337 | 0.028337 | 0.028337 | 0.98272 | -0.33223 | 0.98361 | -0.31478 | 7.7848
118 | 0.018713 | 0.0046948 | -0.018699 | -0.0046864 | 1.3937e-05 | 8.334e-06 | 0.028337 | 0.028337 | 0.028337 | 0.98272 | -0.33223 | 0.98192 | -0.34786 | 7.7849
119 | -0.17802 | -0.045355 | 0.17807 | 0.045383 | 4.4125e-05 | 2.79e-05 | 0.26736 | 0.26736 | 0.26736 | 0.9918 | -0.15606 | 0.99206 | -0.15092 | 18.3624
120 | 0.0027859 | 0.00069804 | -0.0027858 | -0.00069818 | 9.9473e-08 | -1.3352e-07 | 0.004173 | 0.0041731 | 0.0041731 | 0.99337 | -0.12619 | 0.99333 | -0.12694 | 1.1465
121 | -0.0078602 | -0.0019699 | 0.0078615 | 0.0019704 | 1.2292e-06 | 4.9601e-07 | 0.011928 | 0.011928 | 0.011928 | 0.98058 | -0.37301 | 0.98075 | -0.36973 | 3.2769
122 | 0.0054969 | 0.0013776 | -0.0054966 | -0.0013776 | 2.7485e-07 | 4.3032e-08 | 0.0083415 | 0.0083415 | 0.0083415 | 0.98058 | -0.37301 | 0.98053 | -0.37406 | 2.2916

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31724 | 0.080672

## res_load
| p_mw | q_mvar
0 | 0.0016916 | 0.00042396
1 | 0.0019795 | 0.00049612
2 | 0.0019964 | 0.00050035
3 | 0.0046281 | 0.0011599
4 | 0.0026277 | 0.00065858
5 | 0.0018243 | 0.0004572
6 | 0.0037533 | 0.00094067
7 | 0.001763 | 0.00044185
8 | 0.0020896 | 0.0005237
9 | 0.0027116 | 0.00067959
10 | 0.0020457 | 0.0005127
11 | 0.0021804 | 0.00054646
12 | 0.0011495 | 0.00028808
13 | 0.0018434 | 0.00046201
14 | 0.0020301 | 0.00050878
15 | 0.00096594 | 0.00024209
16 | 0.0013949 | 0.00034959
17 | 0.0016686 | 0.00041819
18 | 0.002747 | 0.00068846
19 | 0.0076152 | 0.0019086
20 | 0.0011233 | 0.00028152
21 | 0.0027196 | 0.0006816
22 | 0.0042552 | 0.0010664
23 | 0.0025911 | 0.00064939
24 | 0.012601 | 0.0031581
25 | 0.00331 | 0.00082956
26 | 0.0025371 | 0.00063587
27 | 0.0083718 | 0.0020982
28 | 0.012069 | 0.0030247
29 | 0.0024172 | 0.00060581
30 | 0.0060923 | 0.0015269
31 | 0.0076908 | 0.0019275
32 | 0.00081233 | 0.00020359
33 | 0.004436 | 0.0011118
34 | 0.01869 | 0.0046842
35 | 0.0021424 | 0.00053694
36 | 0.0043055 | 0.0010791
37 | 0.011996 | 0.0030065
38 | 0.0027517 | 0.00068964
39 | 0.018353 | 0.0045996
40 | 0.0018363 | 0.00046021
41 | 0.0015192 | 0.00038075
42 | 0.00063791 | 0.00015988
43 | 0.00062355 | 0.00015628
44 | 0.0012117 | 0.00030367
45 | 0.001228 | 0.00030776
46 | 0.0032629 | 0.00081777
47 | 0.0024223 | 0.00060709
48 | 0.0012438 | 0.00031172
49 | 0.0019839 | 0.00049721
50 | 0.0012473 | 0.00031261
51 | 0.0021382 | 0.00053589
52 | 0.0018203 | 0.00045622
53 | 0.0024247 | 0.00060769
54 | 0.0012791 | 0.00032057
55 | 0.0068454 | 0.0017156
56 | 0.0064632 | 0.0016198
57 | 0.003964 | 0.00099346
58 | 0.00016836 | 4.2195e-05
59 | 0.0044043 | 0.0011038
60 | 0.0010426 | 0.0002613
61 | 0.00046668 | 0.00011696
62 | 0.0028554 | 0.00071564
63 | 0.0019177 | 0.00048063
64 | 0.0012917 | 0.00032372
65 | 0.0014749 | 0.00036963
66 | 0.0076277 | 0.0019117
67 | 0.002177 | 0.00054562
68 | 0.0032503 | 0.0008146
69 | 0.00053729 | 0.00013466
70 | 0.00083006 | 0.00020803
71 | 0.00015076 | 3.7784e-05
72 | 0.00073217 | 0.0001835
73 | 0.0013079 | 0.0003278
74 | 0.00078225 | 0.00019605
75 | 0.010432 | 0.0026146
76 | 0.0064598 | 0.001619
77 | 0.018699 | 0.0046864
78 | 0.001794 | 0.00044962
79 | 0.0029237 | 0.00073274
80 | 0.0073831 | 0.0018504
81 | 0.0027858 | 0.00069818
82 | 0.0023633 | 0.0005923
83 | 0.0054966 | 0.0013776
84 | 0.0018235 | 0.00045702

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1