## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2527-6_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2527-6_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2527-6_0_2_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2527-6_0_2_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_2527-6_0_2_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_2527-6_0_2_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2527-6_0_2_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_2527-6_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2527-6_0_2_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_2527-6_0_2_node_133 | 0.4 | n |  | TRUE
10 | bus_LV_2527-6_0_2_node_135 | 0.4 | n |  | TRUE
11 | bus_LV_2527-6_0_2_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_2527-6_0_2_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_2527-6_0_2_node_28 | 0.4 | n |  | TRUE
14 | bus_LV_2527-6_0_2_node_132 | 0.4 | n |  | TRUE
15 | bus_LV_2527-6_0_2_node_138 | 0.4 | n |  | TRUE
16 | bus_LV_2527-6_0_2_node_134 | 0.4 | n |  | TRUE
17 | bus_LV_2527-6_0_2_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2527-6_0_2_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_2527-6_0_2_node_155 | 0.4 | n |  | TRUE
20 | bus_LV_2527-6_0_2_node_156 | 0.4 | n |  | TRUE
21 | bus_LV_2527-6_0_2_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2527-6_0_2_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_2527-6_0_2_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_2527-6_0_2_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_2527-6_0_2_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_2527-6_0_2_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_2527-6_0_2_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_2527-6_0_2_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_2527-6_0_2_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_2527-6_0_2_node_139 | 0.4 | n |  | TRUE
31 | bus_LV_2527-6_0_2_node_162 | 0.4 | n |  | TRUE
32 | bus_LV_2527-6_0_2_node_179 | 0.4 | n |  | TRUE
33 | bus_LV_2527-6_0_2_node_165 | 0.4 | n |  | TRUE
34 | bus_LV_2527-6_0_2_node_137 | 0.4 | n |  | TRUE
35 | bus_LV_2527-6_0_2_node_163 | 0.4 | n |  | TRUE
36 | bus_LV_2527-6_0_2_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_2527-6_0_2_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_2527-6_0_2_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_2527-6_0_2_node_113 | 0.4 | n |  | TRUE
40 | bus_LV_2527-6_0_2_node_84 | 0.4 | n |  | TRUE
41 | bus_LV_2527-6_0_2_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_2527-6_0_2_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_2527-6_0_2_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_2527-6_0_2_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_2527-6_0_2_node_86 | 0.4 | n |  | TRUE
46 | bus_LV_2527-6_0_2_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_2527-6_0_2_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_2527-6_0_2_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_2527-6_0_2_node_194 | 0.4 | n |  | TRUE
50 | bus_LV_2527-6_0_2_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_2527-6_0_2_node_85 | 0.4 | n |  | TRUE
52 | bus_LV_2527-6_0_2_node_205 | 0.4 | n |  | TRUE
53 | bus_LV_2527-6_0_2_node_193 | 0.4 | n |  | TRUE
54 | bus_LV_2527-6_0_2_node_88 | 0.4 | n |  | TRUE
55 | bus_LV_2527-6_0_2_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_2527-6_0_2_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_2527-6_0_2_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_2527-6_0_2_node_44 | 0.4 | n |  | TRUE
59 | bus_LV_2527-6_0_2_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_2527-6_0_2_node_46 | 0.4 | n |  | TRUE
61 | bus_LV_2527-6_0_2_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_2527-6_0_2_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_2527-6_0_2_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_2527-6_0_2_node_182 | 0.4 | n |  | TRUE
65 | bus_LV_2527-6_0_2_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_2527-6_0_2_node_127 | 0.4 | n |  | TRUE
67 | bus_LV_2527-6_0_2_node_124 | 0.4 | n |  | TRUE
68 | bus_LV_2527-6_0_2_node_204 | 0.4 | n |  | TRUE
69 | bus_LV_2527-6_0_2_node_181 | 0.4 | n |  | TRUE
70 | bus_LV_2527-6_0_2_node_129 | 0.4 | n |  | TRUE
71 | bus_LV_2527-6_0_2_node_130 | 0.4 | n |  | TRUE
72 | bus_LV_2527-6_0_2_node_125 | 0.4 | n |  | TRUE
73 | bus_LV_2527-6_0_2_node_136 | 0.4 | n |  | TRUE
74 | bus_LV_2527-6_0_2_node_72 | 0.4 | n |  | TRUE
75 | bus_LV_2527-6_0_2_node_73 | 0.4 | n |  | TRUE
76 | bus_LV_2527-6_0_2_node_74 | 0.4 | n |  | TRUE
77 | bus_LV_2527-6_0_2_node_75 | 0.4 | n |  | TRUE
78 | bus_LV_2527-6_0_2_node_76 | 0.4 | n |  | TRUE
79 | bus_LV_2527-6_0_2_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_2527-6_0_2_node_159 | 0.4 | n |  | TRUE
81 | bus_LV_2527-6_0_2_node_160 | 0.4 | n |  | TRUE
82 | bus_LV_2527-6_0_2_node_161 | 0.4 | n |  | TRUE
83 | bus_LV_2527-6_0_2_node_78 | 0.4 | n |  | TRUE
84 | bus_LV_2527-6_0_2_node_79 | 0.4 | n |  | TRUE
85 | bus_LV_2527-6_0_2_node_80 | 0.4 | n |  | TRUE
86 | bus_LV_2527-6_0_2_node_81 | 0.4 | n |  | TRUE
87 | bus_LV_2527-6_0_2_node_82 | 0.4 | n |  | TRUE
88 | bus_LV_2527-6_0_2_node_83 | 0.4 | n |  | TRUE
89 | bus_LV_2527-6_0_2_node_103 | 0.4 | n |  | TRUE
90 | bus_LV_2527-6_0_2_node_114 | 0.4 | n |  | TRUE
91 | bus_LV_2527-6_0_2_node_145 | 0.4 | n |  | TRUE
92 | bus_LV_2527-6_0_2_node_101 | 0.4 | n |  | TRUE
93 | bus_LV_2527-6_0_2_node_115 | 0.4 | n |  | TRUE
94 | bus_LV_2527-6_0_2_node_87 | 0.4 | n |  | TRUE
95 | bus_LV_2527-6_0_2_node_97 | 0.4 | n |  | TRUE
96 | bus_LV_2527-6_0_2_node_94 | 0.4 | n |  | TRUE
97 | bus_LV_2527-6_0_2_node_93 | 0.4 | n |  | TRUE
98 | bus_LV_2527-6_0_2_node_95 | 0.4 | n |  | TRUE
99 | bus_LV_2527-6_0_2_node_92 | 0.4 | n |  | TRUE
100 | bus_LV_2527-6_0_2_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_2527-6_0_2_node_166 | 0.4 | n |  | TRUE
102 | bus_LV_2527-6_0_2_node_167 | 0.4 | n |  | TRUE
103 | bus_LV_2527-6_0_2_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_2527-6_0_2_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_2527-6_0_2_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_2527-6_0_2_node_102 | 0.4 | n |  | TRUE
107 | bus_LV_2527-6_0_2_node_104 | 0.4 | n |  | TRUE
108 | bus_LV_2527-6_0_2_node_105 | 0.4 | n |  | TRUE
109 | bus_LV_2527-6_0_2_node_185 | 0.4 | n |  | TRUE
110 | bus_LV_2527-6_0_2_node_111 | 0.4 | n |  | TRUE
111 | bus_LV_2527-6_0_2_node_146 | 0.4 | n |  | TRUE
112 | bus_LV_2527-6_0_2_node_110 | 0.4 | n |  | TRUE
113 | bus_LV_2527-6_0_2_node_126 | 0.4 | n |  | TRUE
114 | bus_LV_2527-6_0_2_node_128 | 0.4 | n |  | TRUE
115 | bus_LV_2527-6_0_2_node_180 | 0.4 | n |  | TRUE
116 | bus_LV_2527-6_0_2_node_157 | 0.4 | n |  | TRUE
117 | bus_LV_2527-6_0_2_node_131 | 0.4 | n |  | TRUE
118 | bus_LV_2527-6_0_2_node_158 | 0.4 | n |  | TRUE
119 | bus_LV_2527-6_0_2_node_164 | 0.4 | n |  | TRUE
120 | bus_LV_2527-6_0_2_node_168 | 0.4 | n |  | TRUE
121 | bus_LV_2527-6_0_2_node_169 | 0.4 | n |  | TRUE
122 | bus_LV_2527-6_0_2_node_183 | 0.4 | n |  | TRUE
123 | bus_LV_2527-6_0_2_node_184 | 0.4 | n |  | TRUE
124 | bus_LV_2527-6_0_2_node_186 | 0.4 | n |  | TRUE
125 | bus_MV_392_0_node_59 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2527-6_0_2_load_0 | 0 | 0.00097128 | 0.00024343 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2527-6_0_2_load_1 | 1 | 0.0017952 | 0.00044992 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2527-6_0_2_load_6 | 3 | 0.0027227 | 0.00068237 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2527-6_0_2_load_4 | 5 | 0.0013362 | 0.00033488 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2527-6_0_2_load_8 | 6 | 0.00058958 | 0.00014776 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2527-6_0_2_load_5 | 7 | 0.0019437 | 0.00048714 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2527-6_0_2_load_133 | 9 | 0.0029508 | 0.00073953 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2527-6_0_2_load_10 | 11 | 0.0015161 | 0.00037998 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2527-6_0_2_load_31 | 12 | 0.0017469 | 0.00043782 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2527-6_0_2_load_28 | 13 | 0.0027153 | 0.00068052 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2527-6_0_2_load_132 | 14 | 0.0018694 | 0.00046851 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2527-6_0_2_load_138 | 15 | 0.0021257 | 0.00053274 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2527-6_0_2_load_11 | 17 | 0.0045515 | 0.0011407 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2527-6_0_2_load_27 | 18 | 0.0013382 | 0.00033537 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2527-6_0_2_load_155 | 19 | 0.00081917 | 0.0002053 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2527-6_0_2_load_18 | 21 | 0.0011042 | 0.00027675 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2527-6_0_2_load_19 | 22 | 0.0012322 | 0.00030881 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2527-6_0_2_load_21 | 24 | 0.0016962 | 0.0004251 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2527-6_0_2_load_22 | 25 | 0.00036944 | 9.259e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2527-6_0_2_load_24 | 27 | 0.0021325 | 0.00053446 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2527-6_0_2_load_25 | 28 | 0.00083506 | 0.00020929 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2527-6_0_2_load_26 | 29 | 0.00062261 | 0.00015604 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2527-6_0_2_load_162 | 31 | 0.0033951 | 0.00085089 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2527-6_0_2_load_179 | 32 | 0.00099225 | 0.00024868 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2527-6_0_2_load_165 | 33 | 0.003266 | 0.00081854 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2527-6_0_2_load_137 | 34 | 0.0059405 | 0.0014888 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2527-6_0_2_load_163 | 35 | 0.0050511 | 0.0012659 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2527-6_0_2_load_29 | 36 | 0.0019578 | 0.00049067 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2527-6_0_2_load_30 | 37 | 0.00109 | 0.00027318 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2527-6_0_2_load_32 | 38 | 0.0021193 | 0.00053115 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2527-6_0_2_load_113 | 39 | 0.0019145 | 0.00047981 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2527-6_0_2_load_33 | 41 | 0.0036348 | 0.00091096 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2527-6_0_2_load_34 | 42 | 0.0093819 | 0.0023513 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2527-6_0_2_load_35 | 43 | 0.00065047 | 0.00016302 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2527-6_0_2_load_39 | 48 | 0.0055948 | 0.0014022 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2527-6_0_2_load_194 | 49 | 0.00066792 | 0.0001674 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2527-6_0_2_load_40 | 50 | 0.0032924 | 0.00082517 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2527-6_0_2_load_205 | 52 | 0.0036886 | 0.00092444 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2527-6_0_2_load_193 | 53 | 0.0027587 | 0.0006914 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2527-6_0_2_load_88 | 54 | 0.0020157 | 0.00050517 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2527-6_0_2_load_41 | 55 | 0.0012548 | 0.00031448 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2527-6_0_2_load_42 | 56 | 0.0034264 | 0.00085873 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2527-6_0_2_load_45 | 59 | 0.0074935 | 0.0018781 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2527-6_0_2_load_46 | 60 | 0.0027024 | 0.00067729 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2527-6_0_2_load_47 | 61 | 0.0019963 | 0.00050032 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2527-6_0_2_load_49 | 62 | 0.007497 | 0.0018789 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2527-6_0_2_load_50 | 63 | 0.002806 | 0.00070325 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2527-6_0_2_load_124 | 67 | 0.00066683 | 0.00016712 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2527-6_0_2_load_204 | 68 | 0.0017995 | 0.000451 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2527-6_0_2_load_181 | 69 | 0.0019148 | 0.0004799 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2527-6_0_2_load_130 | 71 | 0.0011561 | 0.00028976 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2527-6_0_2_load_125 | 72 | 0.00073638 | 0.00018455 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2527-6_0_2_load_136 | 73 | 0.0054656 | 0.0013698 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2527-6_0_2_load_72 | 74 | 0.0019452 | 0.00048751 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2527-6_0_2_load_73 | 75 | 0.0029057 | 0.00072824 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2527-6_0_2_load_74 | 76 | 0.0018515 | 0.00046402 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2527-6_0_2_load_75 | 77 | 0.0017504 | 0.00043869 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2527-6_0_2_load_76 | 78 | 0.0042997 | 0.0010776 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2527-6_0_2_load_77 | 79 | 0.0022447 | 0.00056258 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2527-6_0_2_load_160 | 81 | 0.002015 | 0.00050499 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2527-6_0_2_load_161 | 82 | 0.001882 | 0.00047166 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2527-6_0_2_load_78 | 83 | 0.0018259 | 0.00045763 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2527-6_0_2_load_79 | 84 | 0.0018321 | 0.00045918 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2527-6_0_2_load_80 | 85 | 0.0028194 | 0.00070662 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2527-6_0_2_load_81 | 86 | 0.0022856 | 0.00057282 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2527-6_0_2_load_82 | 87 | 0.0022424 | 0.00056201 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2527-6_0_2_load_83 | 88 | 0.0010614 | 0.000266 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2527-6_0_2_load_114 | 90 | 0.0026057 | 0.00065304 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2527-6_0_2_load_145 | 91 | 0.0036017 | 0.00090267 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2527-6_0_2_load_115 | 93 | 0.0019625 | 0.00049185 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2527-6_0_2_load_97 | 95 | 0.00092602 | 0.00023208 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2527-6_0_2_load_93 | 97 | 0.0015305 | 0.00038359 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2527-6_0_2_load_95 | 98 | 0.001695 | 0.00042481 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2527-6_0_2_load_92 | 99 | 0.0014358 | 0.00035984 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2527-6_0_2_load_96 | 100 | 0.0065324 | 0.0016372 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2527-6_0_2_load_166 | 101 | 0.0035072 | 0.00087898 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2527-6_0_2_load_167 | 102 | 0.0031009 | 0.00077717 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2527-6_0_2_load_98 | 103 | 0.0010195 | 0.00025551 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2527-6_0_2_load_99 | 104 | 0.0022406 | 0.00056156 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2527-6_0_2_load_100 | 105 | 0.004533 | 0.0011361 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2527-6_0_2_load_102 | 106 | 0.0011897 | 0.00029817 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2527-6_0_2_load_104 | 107 | 0.0027545 | 0.00069033 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2527-6_0_2_load_105 | 108 | 0.0015834 | 0.00039685 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2527-6_0_2_load_185 | 109 | 0.0010759 | 0.00026964 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2527-6_0_2_load_111 | 110 | 0.0038862 | 0.00097396 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2527-6_0_2_load_146 | 111 | 0.0028325 | 0.00070989 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2527-6_0_2_load_110 | 112 | 0.0014636 | 0.00036681 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2527-6_0_2_load_126 | 113 | 0.00054946 | 0.00013771 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2527-6_0_2_load_128 | 114 | 0.0019322 | 0.00048426 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2527-6_0_2_load_180 | 115 | 0.0022121 | 0.0005544 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2527-6_0_2_load_157 | 116 | 0.0018319 | 0.00045911 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2527-6_0_2_load_131 | 117 | 0.0018167 | 0.00045532 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2527-6_0_2_load_158 | 118 | 0.0022706 | 0.00056907 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2527-6_0_2_load_164 | 119 | 0.0025298 | 0.00063403 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2527-6_0_2_load_168 | 120 | 0.0020824 | 0.00052191 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2527-6_0_2_load_169 | 121 | 0.0024036 | 0.00060241 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2527-6_0_2_load_183 | 122 | 0.0022402 | 0.00056145 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2527-6_0_2_load_184 | 123 | 0.0022896 | 0.00057383 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2527-6_0_2_load_186 | 124 | 0.0010161 | 0.00025466 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 62 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2527-6_0_2_line_0 |  | 0 | 1 | 0.0012602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2527-6_0_2_line_1 |  | 1 | 2 | 0.038548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2527-6_0_2_line_2 |  | 2 | 3 | 0.012269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2527-6_0_2_line_3 |  | 2 | 4 | 0.006072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2527-6_0_2_line_4 |  | 4 | 9 | 0.014062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2527-6_0_2_line_5 |  | 4 | 10 | 0.036667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2527-6_0_2_line_6 |  | 5 | 6 | 0.00070354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2527-6_0_2_line_7 |  | 6 | 11 | 0.020527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2527-6_0_2_line_8 |  | 7 | 8 | 0.034948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2527-6_0_2_line_9 |  | 8 | 12 | 0.046561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2527-6_0_2_line_10 |  | 8 | 13 | 0.017412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2527-6_0_2_line_11 |  | 9 | 14 | 0.021344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2527-6_0_2_line_12 |  | 10 | 15 | 0.015245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2527-6_0_2_line_13 |  | 10 | 16 | 0.001634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2527-6_0_2_line_14 |  | 11 | 17 | 0.0020106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2527-6_0_2_line_15 |  | 13 | 18 | 0.029031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2527-6_0_2_line_16 |  | 14 | 117 | 0.0034133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2527-6_0_2_line_17 |  | 16 | 73 | 0.014391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2527-6_0_2_line_18 |  | 16 | 34 | 0.022507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2527-6_0_2_line_19 |  | 16 | 63 | 0.015667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2527-6_0_2_line_20 |  | 17 | 19 | 0.03323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2527-6_0_2_line_21 |  | 18 | 36 | 0.017351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2527-6_0_2_line_22 |  | 19 | 20 | 0.0018359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2527-6_0_2_line_23 |  | 20 | 116 | 0.030479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2527-6_0_2_line_24 |  | 20 | 114 | 0.012423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2527-6_0_2_line_25 |  | 21 | 22 | 0.018096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2527-6_0_2_line_26 |  | 21 | 23 | 0.010312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2527-6_0_2_line_27 |  | 22 | 24 | 0.025129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2527-6_0_2_line_28 |  | 23 | 25 | 0.024408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2527-6_0_2_line_29 |  | 23 | 26 | 0.013865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2527-6_0_2_line_30 |  | 24 | 27 | 0.027133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2527-6_0_2_line_31 |  | 26 | 28 | 0.0019233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2527-6_0_2_line_32 |  | 26 | 29 | 0.018346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2527-6_0_2_line_33 |  | 27 | 30 | 0.030069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2527-6_0_2_line_34 |  | 27 | 31 | 0.014114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2527-6_0_2_line_35 |  | 29 | 32 | 0.015588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2527-6_0_2_line_36 |  | 30 | 33 | 0.028201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2527-6_0_2_line_37 |  | 30 | 34 | 0.017131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2527-6_0_2_line_38 |  | 31 | 35 | 0.019424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2527-6_0_2_line_39 |  | 35 | 119 | 0.004758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2527-6_0_2_line_40 |  | 36 | 37 | 0.0021637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2527-6_0_2_line_41 |  | 37 | 38 | 0.0024729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2527-6_0_2_line_42 |  | 38 | 39 | 0.015787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2527-6_0_2_line_43 |  | 39 | 40 | 0.017965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2527-6_0_2_line_44 |  | 40 | 90 | 0.011711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2527-6_0_2_line_45 |  | 40 | 87 | 0.0023311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2527-6_0_2_line_46 |  | 41 | 42 | 0.039457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2527-6_0_2_line_47 |  | 42 | 43 | 0.031385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2527-6_0_2_line_48 |  | 43 | 44 | 0.0092396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2527-6_0_2_line_49 |  | 44 | 45 | 0.010663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2527-6_0_2_line_50 |  | 45 | 54 | 0.014911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2527-6_0_2_line_51 |  | 46 | 47 | 0.0077275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2527-6_0_2_line_52 |  | 46 | 48 | 0.064324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2527-6_0_2_line_53 |  | 47 | 49 | 0.04931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2527-6_0_2_line_54 |  | 48 | 50 | 0.025152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2527-6_0_2_line_55 |  | 49 | 53 | 0.017125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2527-6_0_2_line_56 |  | 50 | 51 | 0.041647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2527-6_0_2_line_57 |  | 51 | 52 | 0.082465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2527-6_0_2_line_58 |  | 52 | 70 | 0.10569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2527-6_0_2_line_59 |  | 54 | 97 | 0.0062288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2527-6_0_2_line_60 |  | 55 | 56 | 0.019573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2527-6_0_2_line_61 |  | 55 | 57 | 0.008937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2527-6_0_2_line_62 |  | 56 | 58 | 0.020723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2527-6_0_2_line_63 |  | 57 | 59 | 0.017738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_2527-6_0_2_line_64 |  | 57 | 60 | 0.0078814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2527-6_0_2_line_65 |  | 58 | 61 | 0.017443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2527-6_0_2_line_66 |  | 59 | 62 | 0.027106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_2527-6_0_2_line_67 |  | 60 | 63 | 0.028734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2527-6_0_2_line_68 |  | 61 | 64 | 0.013128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2527-6_0_2_line_69 |  | 64 | 68 | 0.01221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2527-6_0_2_line_70 |  | 64 | 69 | 0.0081277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2527-6_0_2_line_71 |  | 65 | 66 | 0.021001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2527-6_0_2_line_72 |  | 65 | 67 | 0.0085566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2527-6_0_2_line_73 |  | 66 | 70 | 0.011811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2527-6_0_2_line_74 |  | 66 | 71 | 0.01524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2527-6_0_2_line_75 |  | 67 | 72 | 0.018287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2527-6_0_2_line_76 |  | 69 | 115 | 0.0033132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2527-6_0_2_line_77 |  | 70 | 82 | 0.031323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2527-6_0_2_line_78 |  | 71 | 115 | 0.015859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2527-6_0_2_line_79 |  | 72 | 113 | 0.0016457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2527-6_0_2_line_80 |  | 73 | 93 | 0.020939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2527-6_0_2_line_81 |  | 74 | 75 | 0.01689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2527-6_0_2_line_82 |  | 74 | 76 | 0.0020362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2527-6_0_2_line_83 |  | 75 | 77 | 0.001155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2527-6_0_2_line_84 |  | 76 | 78 | 0.0083624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2527-6_0_2_line_85 |  | 77 | 79 | 0.026635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2527-6_0_2_line_86 |  | 79 | 80 | 0.012999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2527-6_0_2_line_87 |  | 80 | 81 | 0.015587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2527-6_0_2_line_88 |  | 80 | 82 | 0.033578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2527-6_0_2_line_89 |  | 81 | 95 | 0.028266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2527-6_0_2_line_90 |  | 83 | 84 | 0.010238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2527-6_0_2_line_91 |  | 83 | 85 | 0.0092869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2527-6_0_2_line_92 |  | 84 | 86 | 0.013712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2527-6_0_2_line_93 |  | 85 | 87 | 0.00083705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2527-6_0_2_line_94 |  | 86 | 88 | 0.01519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2527-6_0_2_line_95 |  | 88 | 89 | 0.019657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2527-6_0_2_line_96 |  | 89 | 91 | 0.0246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2527-6_0_2_line_97 |  | 89 | 92 | 0.014776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2527-6_0_2_line_98 |  | 90 | 93 | 0.025062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2527-6_0_2_line_99 |  | 91 | 111 | 0.026909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2527-6_0_2_line_100 |  | 92 | 107 | 0.012652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2527-6_0_2_line_101 |  | 92 | 104 | 0.0086112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2527-6_0_2_line_102 |  | 94 | 95 | 0.007761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2527-6_0_2_line_103 |  | 94 | 96 | 0.006409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2527-6_0_2_line_104 |  | 96 | 98 | 0.012988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2527-6_0_2_line_105 |  | 96 | 99 | 0.014343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2527-6_0_2_line_106 |  | 97 | 99 | 0.01362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2527-6_0_2_line_107 |  | 98 | 100 | 0.012573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2527-6_0_2_line_108 |  | 100 | 101 | 0.0084074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2527-6_0_2_line_109 |  | 101 | 102 | 0.0072021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2527-6_0_2_line_110 |  | 102 | 120 | 0.015675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2527-6_0_2_line_111 |  | 103 | 104 | 0.0082468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2527-6_0_2_line_112 |  | 103 | 105 | 0.018345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2527-6_0_2_line_113 |  | 105 | 106 | 0.015722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2527-6_0_2_line_114 |  | 106 | 108 | 0.01908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2527-6_0_2_line_115 |  | 107 | 109 | 0.02231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2527-6_0_2_line_116 |  | 108 | 110 | 0.015654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2527-6_0_2_line_117 |  | 110 | 112 | 0.0040412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2527-6_0_2_line_118 |  | 113 | 114 | 0.028102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2527-6_0_2_line_119 |  | 116 | 118 | 0.019959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2527-6_0_2_line_120 |  | 120 | 121 | 0.0011512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2527-6_0_2_line_121 |  | 121 | 122 | 0.022473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2527-6_0_2_line_122 |  | 122 | 123 | 0.00081214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2527-6_0_2_line_123 |  | 123 | 124 | 0.011289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2527-6_0_2_trafo_49 | 0.63 MVA 20/0.4 kV | 125 | 62 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2611702.7438 | 1229350.8403 | 2611702.488 | 1229352.0743
1 | 2611694.6621 | 1229389.8194 | 2611702.488 | 1229352.0743
2 | 2611694.6621 | 1229389.8194 | 2611690.6408 | 1229389.289 | 2611688.0052 | 1229388.9836 | 2611682.4463 | 1229388.3391
3 | 2611693.4309 | 1229395.7649 | 2611694.6621 | 1229389.8194
4 | 2611693.4309 | 1229395.7649 | 2611707.1541 | 1229398.8342
5 | 2611693.4309 | 1229395.7649 | 2611686.2324 | 1229431.7167
6 | 2611665.0801 | 1229327.8064 | 2611664.391 | 1229327.9483
7 | 2611664.391 | 1229327.9483 | 2611644.2855 | 1229332.0887
8 | 2611776.9026 | 1229349.0009 | 2611755.7219 | 1229333.8058 | 2611747.3361 | 1229330.8827
9 | 2611776.9026 | 1229349.0009 | 2611786.6552 | 1229354.9904 | 2611816.1813 | 1229373.9985
10 | 2611776.9026 | 1229349.0009 | 2611773.3568 | 1229366.0476
11 | 2611707.1541 | 1229398.8342 | 2611727.9834 | 1229403.4928
12 | 2611686.2324 | 1229431.7167 | 2611682.2502 | 1229430.5638 | 2611680.009 | 1229430.0035 | 2611671.4916 | 1229427.6744
13 | 2611685.9641 | 1229433.3283 | 2611686.2324 | 1229431.7167
14 | 2611642.3162 | 1229332.4942 | 2611644.2855 | 1229332.0887
15 | 2611773.3568 | 1229366.0476 | 2611767.4448 | 1229394.4701
16 | 2611731.3144 | 1229404.2378 | 2611727.9834 | 1229403.4928
17 | 2611685.9641 | 1229433.3283 | 2611700.0706 | 1229436.1782
18 | 2611685.9641 | 1229433.3283 | 2611681.6627 | 1229455.4209
19 | 2611685.9641 | 1229433.3283 | 2611681.8439 | 1229433.0089 | 2611679.58 | 1229432.4931 | 2611670.6384 | 1229430.274
20 | 2611642.3162 | 1229332.4942 | 2611631.085 | 1229334.8071 | 2611621.1832 | 1229339.2349 | 2611612.1576 | 1229345.3749
21 | 2611763.9114 | 1229411.4572 | 2611767.4448 | 1229394.4701
22 | 2611610.6397 | 1229346.4076 | 2611612.1576 | 1229345.3749
23 | 2611610.6397 | 1229346.4076 | 2611606.3945 | 1229340.1845 | 2611607.224 | 1229334.3493 | 2611610.7658 | 1229317.6697
24 | 2611610.6397 | 1229346.4076 | 2611602.6354 | 1229352.8292 | 2611601.3137 | 1229354.5387
25 | 2611661.6822 | 1229571.2564 | 2611664.1916 | 1229554.5024 | 2611664.3827 | 1229553.3633
26 | 2611660.1546 | 1229581.455 | 2611661.6822 | 1229571.2564
27 | 2611668.5398 | 1229528.5806 | 2611664.3827 | 1229553.3633
28 | 2611660.1546 | 1229581.455 | 2611658.2615 | 1229581.1511 | 2611655.7399 | 1229580.7348 | 2611648.3268 | 1229579.3418 | 2611641.4017 | 1229576.3043 | 2611637.9391 | 1229572.851
29 | 2611658.378 | 1229595.2041 | 2611660.1546 | 1229581.455
30 | 2611673.0284 | 1229501.8216 | 2611668.5398 | 1229528.5806
31 | 2611658.378 | 1229595.2041 | 2611658.1321 | 1229597.1116
32 | 2611658.378 | 1229595.2041 | 2611655.9542 | 1229595.1327 | 2611653.4168 | 1229595.0277 | 2611646.8578 | 1229594.6147 | 2611640.337 | 1229592.6512
33 | 2611678.3888 | 1229472.2366 | 2611673.0284 | 1229501.8216
34 | 2611673.0284 | 1229501.8216 | 2611670.3856 | 1229501.4162 | 2611667.6518 | 1229500.9883 | 2611659.1387 | 1229499.3312
35 | 2611625.4114 | 1229588.157 | 2611640.337 | 1229592.6512
36 | 2611678.3888 | 1229472.2366 | 2611675.9129 | 1229471.6537 | 2611672.1041 | 1229470.9125 | 2611652.3666 | 1229461.5462
37 | 2611678.3888 | 1229472.2366 | 2611681.6627 | 1229455.4209
38 | 2611659.1387 | 1229499.3312 | 2611640.0724 | 1229495.6198
39 | 2611635.4021 | 1229494.7107 | 2611640.0724 | 1229495.6198
40 | 2611763.9114 | 1229411.4572 | 2611763.4708 | 1229413.5755
41 | 2611763.4708 | 1229413.5755 | 2611762.9672 | 1229415.9966
42 | 2611759.7522 | 1229431.4531 | 2611762.9672 | 1229415.9966
43 | 2611756.0937 | 1229449.0418 | 2611759.7522 | 1229431.4531
44 | 2611756.0937 | 1229449.0418 | 2611744.593 | 1229446.8327
45 | 2611756.0937 | 1229449.0418 | 2611755.6188 | 1229451.324
46 | 2611436.3441 | 1229523.8791 | 2611399.6322 | 1229509.4189
47 | 2611436.3441 | 1229523.8791 | 2611452.1101 | 1229530.089 | 2611464.8866 | 1229536.8182
48 | 2611470.642 | 1229544.044 | 2611464.9064 | 1229536.8287 | 2611464.8866 | 1229536.8182
49 | 2611481.1747 | 1229542.1964 | 2611478.1285 | 1229542.7353 | 2611470.642 | 1229544.044
50 | 2611481.1747 | 1229542.1964 | 2611483.9078 | 1229546.8822 | 2611492.1251 | 1229551.623
51 | 2611347.4494 | 1229488.865 | 2611345.0807 | 1229487.6486 | 2611342.9585 | 1229492.2474
52 | 2611347.4494 | 1229488.865 | 2611377.8855 | 1229432.1974
53 | 2611342.9585 | 1229492.2474 | 2611359.8071 | 1229499.2946 | 2611380.2906 | 1229506.9048 | 2611388.8695 | 1229510.2152
54 | 2611377.8855 | 1229432.1974 | 2611386.0978 | 1229416.9067 | 2611389.0032 | 1229409.6725
55 | 2611404.8458 | 1229516.3801 | 2611388.8695 | 1229510.2152
56 | 2611404.5247 | 1229371.0256 | 2611389.0032 | 1229409.6725
57 | 2611404.5247 | 1229371.0256 | 2611474.1344 | 1229326.8102
58 | 2611537.5652 | 1229411.3492 | 2611474.1344 | 1229326.8102
59 | 2611497.7351 | 1229549.0306 | 2611497.6746 | 1229549.1878 | 2611492.1251 | 1229551.623
60 | 2611626.5513 | 1229418.8442 | 2611607.7666 | 1229413.3446
61 | 2611635.1283 | 1229421.3553 | 2611626.5513 | 1229418.8442
62 | 2611587.8789 | 1229407.522 | 2611607.7666 | 1229413.3446
63 | 2611635.1283 | 1229421.3553 | 2611629.9295 | 1229438.314
64 | 2611635.1283 | 1229421.3553 | 2611637.4525 | 1229422.038 | 2611642.7508 | 1229423.3529
65 | 2611587.8789 | 1229407.522 | 2611583.3421 | 1229424.3647
66 | 2611621.9848 | 1229464.2295 | 2611629.9295 | 1229438.314
67 | 2611642.7508 | 1229423.3529 | 2611670.6384 | 1229430.274
68 | 2611577.8028 | 1229435.5081 | 2611580.8898 | 1229433.4684 | 2611583.3421 | 1229424.3647
69 | 2611577.8028 | 1229435.5081 | 2611589.1317 | 1229440.0626
70 | 2611577.8028 | 1229435.5081 | 2611570.1129 | 1229432.8767
71 | 2611549.3986 | 1229410.8051 | 2611558.4055 | 1229406.8312 | 2611566.6996 | 1229399.3095
72 | 2611566.6996 | 1229399.3095 | 2611571.9333 | 1229392.5401
73 | 2611537.5652 | 1229411.3492 | 2611549.3986 | 1229410.8051
74 | 2611549.3986 | 1229410.8051 | 2611552.4225 | 1229425.7421 | 2611552.4225 | 1229425.7421
75 | 2611583.1184 | 1229378.073 | 2611571.9333 | 1229392.5401
76 | 2611566.9782 | 1229431.804 | 2611570.1129 | 1229432.8767
77 | 2611537.5652 | 1229411.3492 | 2611535.9212 | 1229419.273 | 2611531.4259 | 1229442.0643
78 | 2611566.9782 | 1229431.804 | 2611556.0086 | 1229428.0504 | 2611552.4225 | 1229425.7421
79 | 2611583.1184 | 1229378.073 | 2611584.125 | 1229376.771
80 | 2611720.0574 | 1229441.7436 | 2611717.3627 | 1229441.1277 | 2611713.6931 | 1229438.9303 | 2611700.0706 | 1229436.1782
81 | 2611579.7238 | 1229492.4593 | 2611563.7535 | 1229486.9606
82 | 2611579.7238 | 1229492.4593 | 2611581.6491 | 1229493.1221
83 | 2611563.7535 | 1229486.9606 | 2611562.6615 | 1229486.5846
84 | 2611589.556 | 1229495.8445 | 2611581.6491 | 1229493.1221
85 | 2611537.4778 | 1229477.9137 | 2611562.6615 | 1229486.5846
86 | 2611524.9283 | 1229475.0072 | 2611529.8062 | 1229475.2723 | 2611537.4778 | 1229477.9137
87 | 2611524.9283 | 1229475.0072 | 2611522.6135 | 1229477.3041 | 2611519.5203 | 1229486.5036 | 2611518.4868 | 1229488.9113
88 | 2611524.9283 | 1229475.0072 | 2611531.4259 | 1229442.0643
89 | 2611518.4868 | 1229488.9113 | 2611513.5928 | 1229500.3116 | 2611505.6372 | 1229514.0314
90 | 2611753.5567 | 1229461.2357 | 2611751.4713 | 1229471.2594
91 | 2611755.4483 | 1229452.1435 | 2611753.5567 | 1229461.2357
92 | 2611751.4713 | 1229471.2594 | 2611748.6783 | 1229484.6841
93 | 2611755.6188 | 1229451.324 | 2611755.4483 | 1229452.1435
94 | 2611748.6783 | 1229484.6841 | 2611745.5843 | 1229499.5554
95 | 2611741.0264 | 1229518.6536 | 2611742.665 | 1229513.5871 | 2611745.5843 | 1229499.5554
96 | 2611741.0264 | 1229518.6536 | 2611722.576 | 1229502.3834
97 | 2611750.4348 | 1229530.0678 | 2611741.0264 | 1229518.6536
98 | 2611744.593 | 1229446.8327 | 2611730.3633 | 1229444.0994 | 2611720.0574 | 1229441.7436
99 | 2611702.393 | 1229484.5854 | 2611722.576 | 1229502.3834
100 | 2611750.4348 | 1229530.0678 | 2611759.6386 | 1229538.7494
101 | 2611750.4348 | 1229530.0678 | 2611749.518 | 1229538.63
102 | 2611501.7441 | 1229520.7454 | 2611505.6372 | 1229514.0314
103 | 2611507.7847 | 1229522.9361 | 2611501.7441 | 1229520.7454
104 | 2611507.7847 | 1229522.9361 | 2611519.9972 | 1229527.3569
105 | 2611507.7847 | 1229522.9361 | 2611502.63 | 1229536.3207
106 | 2611497.7351 | 1229549.0306 | 2611502.63 | 1229536.3207
107 | 2611519.9972 | 1229527.3569 | 2611531.8192 | 1229531.6364
108 | 2611539.7246 | 1229534.4981 | 2611531.8192 | 1229531.6364
109 | 2611546.4967 | 1229536.9495 | 2611539.7246 | 1229534.4981
110 | 2611546.4967 | 1229536.9495 | 2611561.2357 | 1229542.285
111 | 2611748.6399 | 1229546.8299 | 2611749.518 | 1229538.63
112 | 2611746.6867 | 1229565.0708 | 2611748.6399 | 1229546.8299
113 | 2611746.6867 | 1229565.0708 | 2611745.0127 | 1229580.7036
114 | 2611742.9812 | 1229599.6755 | 2611745.0127 | 1229580.7036
115 | 2611759.6386 | 1229538.7494 | 2611775.8676 | 1229554.0577
116 | 2611742.9812 | 1229599.6755 | 2611741.3145 | 1229615.2401
117 | 2611740.8842 | 1229619.2583 | 2611741.3145 | 1229615.2401
118 | 2611584.125 | 1229376.771 | 2611601.3137 | 1229354.5387
119 | 2611602.6476 | 1229303.6222 | 2611609.1894 | 1229305.2692 | 2611610.9567 | 1229307.9965 | 2611612.0404 | 1229311.6674 | 2611610.7658 | 1229317.6697
120 | 2611562.3181 | 1229542.6768 | 2611561.2357 | 1229542.285
121 | 2611583.4495 | 1229550.3262 | 2611562.3181 | 1229542.6768
122 | 2611584.2131 | 1229550.6026 | 2611583.4495 | 1229550.3262
123 | 2611594.8281 | 1229554.4452 | 2611584.2131 | 1229550.6026

## bus_geodata
| x | y | coords
0 | 2611702.7438 | 1229350.8403
1 | 2611702.488 | 1229352.0743
2 | 2611694.6621 | 1229389.8194
3 | 2611682.4463 | 1229388.3391
4 | 2611693.4309 | 1229395.7649
5 | 2611665.0801 | 1229327.8064
6 | 2611664.391 | 1229327.9483
7 | 2611747.3361 | 1229330.8827
8 | 2611776.9026 | 1229349.0009
9 | 2611707.1541 | 1229398.8342
10 | 2611686.2324 | 1229431.7167
11 | 2611644.2855 | 1229332.0887
12 | 2611816.1813 | 1229373.9985
13 | 2611773.3568 | 1229366.0476
14 | 2611727.9834 | 1229403.4928
15 | 2611671.4916 | 1229427.6744
16 | 2611685.9641 | 1229433.3283
17 | 2611642.3162 | 1229332.4942
18 | 2611767.4448 | 1229394.4701
19 | 2611612.1576 | 1229345.3749
20 | 2611610.6397 | 1229346.4076
21 | 2611661.6822 | 1229571.2564
22 | 2611664.3827 | 1229553.3633
23 | 2611660.1546 | 1229581.455
24 | 2611668.5398 | 1229528.5806
25 | 2611637.9391 | 1229572.851
26 | 2611658.378 | 1229595.2041
27 | 2611673.0284 | 1229501.8216
28 | 2611658.1321 | 1229597.1116
29 | 2611640.337 | 1229592.6512
30 | 2611678.3888 | 1229472.2366
31 | 2611659.1387 | 1229499.3312
32 | 2611625.4114 | 1229588.157
33 | 2611652.3666 | 1229461.5462
34 | 2611681.6627 | 1229455.4209
35 | 2611640.0724 | 1229495.6198
36 | 2611763.9114 | 1229411.4572
37 | 2611763.4708 | 1229413.5755
38 | 2611762.9672 | 1229415.9966
39 | 2611759.7522 | 1229431.4531
40 | 2611756.0937 | 1229449.0417
41 | 2611399.6322 | 1229509.4189
42 | 2611436.3441 | 1229523.8791
43 | 2611464.8866 | 1229536.8182
44 | 2611470.642 | 1229544.044
45 | 2611481.1747 | 1229542.1964
46 | 2611347.4494 | 1229488.865
47 | 2611342.9585 | 1229492.2474
48 | 2611377.8855 | 1229432.1974
49 | 2611388.8695 | 1229510.2152
50 | 2611389.0032 | 1229409.6725
51 | 2611404.5247 | 1229371.0256
52 | 2611474.1344 | 1229326.8102
53 | 2611404.8458 | 1229516.3801
54 | 2611492.1251 | 1229551.623
55 | 2611626.5513 | 1229418.8442
56 | 2611607.7666 | 1229413.3446
57 | 2611635.1283 | 1229421.3553
58 | 2611587.8789 | 1229407.522
59 | 2611629.9295 | 1229438.314
60 | 2611642.7508 | 1229423.3529
61 | 2611583.3421 | 1229424.3647
62 | 2611621.9848 | 1229464.2295
63 | 2611670.6384 | 1229430.274
64 | 2611577.8028 | 1229435.5081
65 | 2611566.6996 | 1229399.3095
66 | 2611549.3986 | 1229410.8051
67 | 2611571.9333 | 1229392.5401
68 | 2611589.1317 | 1229440.0626
69 | 2611570.1129 | 1229432.8767
70 | 2611537.5652 | 1229411.3492
71 | 2611552.4225 | 1229425.7421
72 | 2611583.1184 | 1229378.073
73 | 2611700.0706 | 1229436.1782
74 | 2611579.7238 | 1229492.4593
75 | 2611563.7535 | 1229486.9606
76 | 2611581.6491 | 1229493.1221
77 | 2611562.6615 | 1229486.5846
78 | 2611589.556 | 1229495.8445
79 | 2611537.4778 | 1229477.9137
80 | 2611524.9283 | 1229475.0072
81 | 2611518.4868 | 1229488.9113
82 | 2611531.4259 | 1229442.0643
83 | 2611753.5567 | 1229461.2357
84 | 2611751.4713 | 1229471.2594
85 | 2611755.4483 | 1229452.1435
86 | 2611748.6783 | 1229484.6841
87 | 2611755.6188 | 1229451.324
88 | 2611745.5843 | 1229499.5554
89 | 2611741.0264 | 1229518.6536
90 | 2611744.593 | 1229446.8327
91 | 2611722.576 | 1229502.3834
92 | 2611750.4348 | 1229530.0678
93 | 2611720.0574 | 1229441.7436
94 | 2611501.7441 | 1229520.7454
95 | 2611505.6372 | 1229514.0314
96 | 2611507.7847 | 1229522.9361
97 | 2611497.7351 | 1229549.0306
98 | 2611519.9972 | 1229527.3569
99 | 2611502.63 | 1229536.3207
100 | 2611531.8192 | 1229531.6364
101 | 2611539.7246 | 1229534.4981
102 | 2611546.4966 | 1229536.9495
103 | 2611748.6399 | 1229546.8299
104 | 2611749.518 | 1229538.63
105 | 2611746.6867 | 1229565.0708
106 | 2611745.0127 | 1229580.7036
107 | 2611759.6386 | 1229538.7494
108 | 2611742.9812 | 1229599.6755
109 | 2611775.8676 | 1229554.0577
110 | 2611741.3145 | 1229615.2401
111 | 2611702.393 | 1229484.5854
112 | 2611740.8842 | 1229619.2583
113 | 2611584.125 | 1229376.771
114 | 2611601.3137 | 1229354.5387
115 | 2611566.9782 | 1229431.804
116 | 2611610.7658 | 1229317.6697
117 | 2611731.3144 | 1229404.2378
118 | 2611602.6476 | 1229303.6222
119 | 2611635.4021 | 1229494.7107
120 | 2611561.2357 | 1229542.285
121 | 2611562.3181 | 1229542.6768
122 | 2611583.4495 | 1229550.3262
123 | 2611584.2131 | 1229550.6026
124 | 2611594.8281 | 1229554.4452
125 | 2611620.3998 | 1229469.3997

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98952 | -0.20052 | 0.00097128 | 0.00024343
1 | 0.98952 | -0.20049 | 0.0017952 | 0.00044992
2 | 0.98962 | -0.1986 | 0 | 0
3 | 0.98959 | -0.19919 | 0.0027227 | 0.00068237
4 | 0.98965 | -0.198 | 0 | 0
5 | 0.982 | -0.34521 | 0.0013362 | 0.00033488
6 | 0.982 | -0.34519 | 0.00058958 | 0.00014776
7 | 0.98538 | -0.28086 | 0.0019437 | 0.00048714
8 | 0.98545 | -0.27964 | 0 | 0
9 | 0.98957 | -0.19966 | 0.0029508 | 0.00073953
10 | 0.99006 | -0.19009 | 0 | 0
11 | 0.98204 | -0.34447 | 0.0015161 | 0.00037998
12 | 0.98537 | -0.2811 | 0.0017469 | 0.00043782
13 | 0.9855 | -0.27849 | 0.0027153 | 0.00068052
14 | 0.98949 | -0.20106 | 0.0018694 | 0.00046851
15 | 0.99003 | -0.19067 | 0.0021257 | 0.00053274
16 | 0.99008 | -0.18968 | 0 | 0
17 | 0.98204 | -0.34435 | 0.0045515 | 0.0011407
18 | 0.98568 | -0.27515 | 0.0013382 | 0.00033537
19 | 0.98229 | -0.33955 | 0.00081917 | 0.0002053
20 | 0.9823 | -0.33926 | 0 | 0
21 | 0.98821 | -0.22605 | 0.0011042 | 0.00027675
22 | 0.98827 | -0.22478 | 0.0012322 | 0.00030881
23 | 0.98818 | -0.22657 | 0 | 0
24 | 0.98839 | -0.22247 | 0.0016962 | 0.0004251
25 | 0.98817 | -0.22673 | 0.00036944 | 9.259e-05
26 | 0.98815 | -0.22718 | 0 | 0
27 | 0.98856 | -0.21915 | 0.0021325 | 0.00053446
28 | 0.98815 | -0.2272 | 0.00083506 | 0.00020929
29 | 0.98812 | -0.22771 | 0.00062261 | 0.00015604
30 | 0.98911 | -0.20845 | 0 | 0
31 | 0.98842 | -0.22191 | 0.0033951 | 0.00085089
32 | 0.98811 | -0.22798 | 0.00099225 | 0.00024868
33 | 0.98903 | -0.21009 | 0.003266 | 0.00081854
34 | 0.98948 | -0.20136 | 0.0059405 | 0.0014888
35 | 0.98829 | -0.22454 | 0.0050511 | 0.0012659
36 | 0.9858 | -0.27274 | 0.0019578 | 0.00049067
37 | 0.98582 | -0.27236 | 0.00109 | 0.00027318
38 | 0.98584 | -0.27188 | 0.0021193 | 0.00053115
39 | 0.98603 | -0.26823 | 0.0019145 | 0.00047981
40 | 0.98628 | -0.26345 | 0 | 0
41 | 0.97503 | -0.48149 | 0.0036348 | 0.00091096
42 | 0.97517 | -0.47886 | 0.0093819 | 0.0023513
43 | 0.97555 | -0.47137 | 0.00065047 | 0.00016302
44 | 0.97567 | -0.46906 | 0 | 0
45 | 0.9758 | -0.46639 | 0 | 0
46 | 0.97933 | -0.39745 | 0 | 0
47 | 0.9793 | -0.39793 | 0 | 0
48 | 0.97953 | -0.39344 | 0.0055948 | 0.0014022
49 | 0.97915 | -0.401 | 0.00066792 | 0.0001674
50 | 0.97974 | -0.38931 | 0.0032924 | 0.00082517
51 | 0.98022 | -0.38 | 0 | 0
52 | 0.98116 | -0.36159 | 0.0036886 | 0.00092444
53 | 0.9791 | -0.40186 | 0.0027587 | 0.0006914
54 | 0.97599 | -0.46266 | 0.0020157 | 0.00050517
55 | 0.9944 | -0.10625 | 0.0012548 | 0.00031448
56 | 0.99243 | -0.14382 | 0.0034264 | 0.00085873
57 | 0.99531 | -0.088946 | 0 | 0
58 | 0.99041 | -0.18249 | 0 | 0
59 | 0.99713 | -0.054368 | 0.0074935 | 0.0018781
60 | 0.9945 | -0.1045 | 0.0027024 | 0.00067729
61 | 0.98871 | -0.21517 | 0.0019963 | 0.00050032
62 | 1 | 0 | -0.23455 | -0.059692
63 | 0.99161 | -0.16004 | 0.002806 | 0.00070325
64 | 0.98745 | -0.23937 | 0 | 0
65 | 0.98326 | -0.32045 | 0 | 0
66 | 0.98359 | -0.31409 | 0 | 0
67 | 0.98313 | -0.32304 | 0.00066683 | 0.00016712
68 | 0.98743 | -0.23977 | 0.0017995 | 0.000451
69 | 0.98669 | -0.25412 | 0.0019148 | 0.0004799
70 | 0.98272 | -0.33099 | 0 | 0
71 | 0.98495 | -0.28772 | 0.0011561 | 0.00028976
72 | 0.98286 | -0.32837 | 0.00073638 | 0.00018455
73 | 0.98924 | -0.20584 | 0.0054656 | 0.0013698
74 | 0.97833 | -0.41679 | 0.0019452 | 0.00048751
75 | 0.97845 | -0.4143 | 0.0029057 | 0.00072824
76 | 0.97832 | -0.41701 | 0.0018515 | 0.00046402
77 | 0.97847 | -0.41406 | 0.0017504 | 0.00043869
78 | 0.97828 | -0.41767 | 0.0042997 | 0.0010776
79 | 0.97878 | -0.40788 | 0.0022447 | 0.00056258
80 | 0.97896 | -0.40434 | 0 | 0
81 | 0.97829 | -0.41752 | 0.002015 | 0.00050499
82 | 0.98088 | -0.36687 | 0.001882 | 0.00047166
83 | 0.98588 | -0.27111 | 0.0018259 | 0.00045763
84 | 0.98559 | -0.27688 | 0.0018321 | 0.00045918
85 | 0.98617 | -0.26559 | 0.0028194 | 0.00070662
86 | 0.98521 | -0.28414 | 0.0022856 | 0.00057282
87 | 0.98619 | -0.26505 | 0.0022424 | 0.00056201
88 | 0.98483 | -0.29158 | 0.0010614 | 0.000266
89 | 0.98436 | -0.30083 | 0 | 0
90 | 0.98685 | -0.25232 | 0.0026057 | 0.00065304
91 | 0.98421 | -0.30368 | 0.0036017 | 0.00090267
92 | 0.98409 | -0.30609 | 0 | 0
93 | 0.98813 | -0.22737 | 0.0019625 | 0.00049185
94 | 0.97681 | -0.44659 | 0 | 0
95 | 0.97712 | -0.44043 | 0.00092602 | 0.00023208
96 | 0.97655 | -0.45169 | 0 | 0
97 | 0.97608 | -0.46087 | 0.0015305 | 0.00038359
98 | 0.97625 | -0.4576 | 0.001695 | 0.00042481
99 | 0.9763 | -0.45658 | 0.0014358 | 0.00035984
100 | 0.97598 | -0.46293 | 0.0065324 | 0.0016372
101 | 0.97585 | -0.46549 | 0.0035072 | 0.00087898
102 | 0.97576 | -0.46722 | 0.0031009 | 0.00077717
103 | 0.98386 | -0.31058 | 0.0010195 | 0.00025551
104 | 0.98396 | -0.30855 | 0.0022406 | 0.00056156
105 | 0.98364 | -0.31477 | 0.004533 | 0.0011361
106 | 0.98353 | -0.31707 | 0.0011897 | 0.00029817
107 | 0.98404 | -0.30696 | 0.0027545 | 0.00069033
108 | 0.9834 | -0.31945 | 0.0015834 | 0.00039685
109 | 0.98402 | -0.30739 | 0.0010759 | 0.00026964
110 | 0.98333 | -0.32096 | 0.0038862 | 0.00097396
111 | 0.98414 | -0.30505 | 0.0028325 | 0.00070989
112 | 0.98332 | -0.32107 | 0.0014636 | 0.00036681
113 | 0.98284 | -0.32882 | 0.00054946 | 0.00013771
114 | 0.98245 | -0.33636 | 0.0019322 | 0.00048426
115 | 0.98638 | -0.26003 | 0.0022121 | 0.0005544
116 | 0.98219 | -0.34152 | 0.0018319 | 0.00045911
117 | 0.98949 | -0.20117 | 0.0018167 | 0.00045532
118 | 0.98215 | -0.34234 | 0.0022706 | 0.00056907
119 | 0.98827 | -0.22476 | 0.0025298 | 0.00063403
120 | 0.97561 | -0.4701 | 0.0020824 | 0.00052191
121 | 0.9756 | -0.47027 | 0.0024036 | 0.00060241
122 | 0.97549 | -0.47255 | 0.0022402 | 0.00056145
123 | 0.97549 | -0.4726 | 0.0022896 | 0.00057383
124 | 0.97548 | -0.47281 | 0.0010161 | 0.00025466
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00097128 | -0.00024343 | 0.00097129 | 0.00024341 | 1.0082e-09 | -1.5543e-08 | 0.0014606 | 0.0014606 | 0.0014606 | 0.98952 | -0.20052 | 0.98952 | -0.20049 | 0.40126
1 | -0.0027665 | -0.00069333 | 0.0027667 | 0.00069299 | 2.5017e-07 | -3.3512e-07 | 0.0041601 | 0.00416 | 0.0041601 | 0.98952 | -0.20049 | 0.98962 | -0.1986 | 1.1429
2 | 0.0027227 | 0.00068226 | -0.0027227 | -0.00068237 | 7.7113e-08 | -1.0828e-07 | 0.0040939 | 0.004094 | 0.004094 | 0.98962 | -0.1986 | 0.98959 | -0.19919 | 1.1247
3 | -0.0054895 | -0.0013752 | 0.0054896 | 0.0013753 | 1.5512e-07 | 2.1262e-08 | 0.0082539 | 0.0082539 | 0.0082539 | 0.98962 | -0.1986 | 0.98965 | -0.198 | 2.2676
4 | 0.0066377 | 0.0016634 | -0.0066371 | -0.0016632 | 5.2525e-07 | 1.5549e-07 | 0.0099802 | 0.0099802 | 0.0099802 | 0.98965 | -0.198 | 0.98957 | -0.19966 | 2.7418
5 | -0.012127 | -0.0030386 | 0.012132 | 0.0030411 | 4.5716e-06 | 2.4545e-06 | 0.018234 | 0.018234 | 0.018234 | 0.98965 | -0.198 | 0.99006 | -0.19009 | 5.0094
6 | -0.0013362 | -0.00033488 | 0.0013362 | 0.00033487 | 1.0815e-09 | -8.2085e-09 | 0.0020247 | 0.0020247 | 0.0020247 | 0.982 | -0.34521 | 0.982 | -0.34519 | 0.55623
7 | -0.0019258 | -0.00048263 | 0.0019258 | 0.00048241 | 6.5546e-08 | -2.1776e-07 | 0.0029181 | 0.002918 | 0.0029181 | 0.982 | -0.34519 | 0.98204 | -0.34447 | 0.80167
8 | -0.0019437 | -0.00048714 | 0.0019438 | 0.00048676 | 1.129e-07 | -3.7296e-07 | 0.0029351 | 0.002935 | 0.0029351 | 0.98538 | -0.28086 | 0.98545 | -0.27964 | 0.80636
9 | 0.001747 | 0.0004373 | -0.0017469 | -0.00043782 | 1.215e-07 | -5.1538e-07 | 0.0026378 | 0.002638 | 0.002638 | 0.98545 | -0.27964 | 0.98537 | -0.2811 | 0.72474
10 | -0.0036908 | -0.00092407 | 0.003691 | 0.00092397 | 2.0277e-07 | -9.2064e-08 | 0.0055728 | 0.0055727 | 0.0055728 | 0.98545 | -0.27964 | 0.9855 | -0.27849 | 1.531
11 | 0.0036864 | 0.00092368 | -0.0036861 | -0.00092379 | 2.4594e-07 | -1.1678e-07 | 0.0055432 | 0.0055433 | 0.0055433 | 0.98957 | -0.19966 | 0.98949 | -0.20106 | 1.5229
12 | 0.0021257 | 0.00053258 | -0.0021257 | -0.00053274 | 5.8352e-08 | -1.587e-07 | 0.0031948 | 0.0031949 | 0.0031949 | 0.99006 | -0.19009 | 0.99003 | -0.19067 | 0.87771
13 | -0.014258 | -0.0035737 | 0.014258 | 0.0035738 | 2.8137e-07 | 1.5906e-07 | 0.021429 | 0.021429 | 0.021429 | 0.99006 | -0.19009 | 0.99008 | -0.18968 | 5.887
14 | -0.003442 | -0.00086239 | 0.003442 | 0.00086238 | 2.0508e-08 | -1.2314e-08 | 0.0052153 | 0.0052153 | 0.0052153 | 0.98204 | -0.34447 | 0.98204 | -0.34435 | 1.4328
15 | -0.0064063 | -0.0016045 | 0.0064074 | 0.0016048 | 1.0185e-06 | 2.8189e-07 | 0.0096726 | 0.0096724 | 0.0096726 | 0.9855 | -0.27849 | 0.98568 | -0.27515 | 2.6573
16 | 0.0018168 | 0.00045528 | -0.0018167 | -0.00045532 | 9.5538e-09 | -3.7729e-08 | 0.002732 | 0.0027321 | 0.0027321 | 0.98949 | -0.20106 | 0.98949 | -0.20117 | 0.75057
17 | 0.063385 | 0.015988 | -0.063336 | -0.015956 | 4.9014e-05 | 3.1184e-05 | 0.0953 | 0.0953 | 0.0953 | 0.99008 | -0.18968 | 0.98924 | -0.20584 | 26.1812
18 | 0.029206 | 0.0073312 | -0.02919 | -0.0073211 | 1.6265e-05 | 1.012e-05 | 0.043899 | 0.043899 | 0.043899 | 0.99008 | -0.18968 | 0.98948 | -0.20136 | 12.0601
19 | -0.10685 | -0.026893 | 0.107 | 0.02699 | 0.00015159 | 9.6814e-05 | 0.16063 | 0.16063 | 0.16063 | 0.99008 | -0.18968 | 0.99161 | -0.16004 | 44.1283
20 | -0.0079934 | -0.0020031 | 0.0079953 | 0.0020038 | 1.828e-06 | 7.4936e-07 | 0.012112 | 0.012112 | 0.012112 | 0.98204 | -0.34435 | 0.98229 | -0.33955 | 3.3274
21 | -0.0077455 | -0.0019401 | 0.0077464 | 0.0019405 | 8.8954e-07 | 3.4812e-07 | 0.011693 | 0.011693 | 0.011693 | 0.98568 | -0.27515 | 0.9858 | -0.27274 | 3.2122
22 | -0.0088144 | -0.0022091 | 0.0088146 | 0.0022092 | 1.2275e-07 | 5.5318e-08 | 0.013353 | 0.013353 | 0.013353 | 0.98229 | -0.33955 | 0.9823 | -0.33926 | 3.6683
23 | 0.004103 | 0.0010279 | -0.0041025 | -0.001028 | 4.4151e-07 | -1.0322e-07 | 0.0062151 | 0.0062153 | 0.0062153 | 0.9823 | -0.33926 | 0.98219 | -0.34152 | 1.7075
24 | -0.012918 | -0.0032371 | 0.012919 | 0.0032381 | 1.7837e-06 | 9.8429e-07 | 0.019568 | 0.019568 | 0.019568 | 0.9823 | -0.33926 | 0.98245 | -0.33636 | 5.3757
25 | -0.0039238 | -0.00098239 | 0.003924 | 0.00098231 | 2.3686e-07 | -8.0267e-08 | 0.005908 | 0.0059079 | 0.005908 | 0.98821 | -0.22605 | 0.98827 | -0.22478 | 1.6231
26 | 0.0028196 | 0.00070564 | -0.0028195 | -0.00070573 | 6.9695e-08 | -8.751e-08 | 0.0042453 | 0.0042453 | 0.0042453 | 0.98821 | -0.22605 | 0.98818 | -0.22657 | 1.1663
27 | -0.0051562 | -0.0012911 | 0.0051568 | 0.0012912 | 5.679e-07 | 4.1431e-08 | 0.0077631 | 0.007763 | 0.0077631 | 0.98827 | -0.22478 | 0.98839 | -0.22247 | 2.1327
28 | 0.00036944 | 9.228e-05 | -0.00036944 | -9.259e-05 | 2.8321e-09 | -3.1088e-07 | 0.0005562 | 0.00055631 | 0.00055631 | 0.98818 | -0.22657 | 0.98817 | -0.22673 | 0.15283
29 | 0.00245 | 0.00061345 | -0.00245 | -0.00061358 | 7.0762e-08 | -1.3233e-07 | 0.0036891 | 0.0036892 | 0.0036892 | 0.98818 | -0.22657 | 0.98815 | -0.22718 | 1.0135
30 | -0.0068529 | -0.0017163 | 0.006854 | 0.0017166 | 1.0829e-06 | 3.4525e-07 | 0.010317 | 0.010316 | 0.010317 | 0.98839 | -0.22247 | 0.98856 | -0.21915 | 2.8342
31 | 0.00083507 | 0.00020926 | -0.00083506 | -0.00020929 | 1.1405e-09 | -2.3908e-08 | 0.0012575 | 0.0012575 | 0.0012575 | 0.98815 | -0.22718 | 0.98815 | -0.2272 | 0.34546
32 | 0.0016149 | 0.00040432 | -0.0016149 | -0.00040453 | 4.0683e-08 | -2.0898e-07 | 0.0024317 | 0.0024318 | 0.0024318 | 0.98815 | -0.22718 | 0.98812 | -0.22771 | 0.66807
33 | -0.019965 | -0.005003 | 0.019975 | 0.0050091 | 1.0183e-05 | 6.1315e-06 | 0.030052 | 0.030051 | 0.030052 | 0.98856 | -0.21915 | 0.98911 | -0.20845 | 8.2559
34 | 0.010978 | 0.0027519 | -0.010977 | -0.0027512 | 1.4453e-06 | 7.4409e-07 | 0.016525 | 0.016525 | 0.016525 | 0.98856 | -0.21915 | 0.98842 | -0.22191 | 4.5399
35 | 0.00099226 | 0.00024849 | -0.00099225 | -0.00024868 | 1.3051e-08 | -1.9131e-07 | 0.0014942 | 0.0014942 | 0.0014942 | 0.98812 | -0.22771 | 0.98811 | -0.22798 | 0.41051
36 | 0.0032663 | 0.00081834 | -0.003266 | -0.00081854 | 2.5534e-07 | -1.9852e-07 | 0.0049137 | 0.0049138 | 0.0049138 | 0.98911 | -0.20845 | 0.98903 | -0.21009 | 1.3499
37 | -0.023241 | -0.0058274 | 0.023249 | 0.0058322 | 7.8541e-06 | 4.8066e-06 | 0.034965 | 0.034965 | 0.034965 | 0.98911 | -0.20845 | 0.98948 | -0.20136 | 9.6058
38 | 0.0075819 | 0.0019003 | -0.0075809 | -0.0018999 | 9.4899e-07 | 3.5842e-07 | 0.011414 | 0.011414 | 0.011414 | 0.98842 | -0.22191 | 0.98829 | -0.22454 | 3.1358
39 | 0.0025298 | 0.00063399 | -0.0025298 | -0.00063403 | 2.5887e-08 | -4.4399e-08 | 0.003809 | 0.0038091 | 0.0038091 | 0.98829 | -0.22454 | 0.98827 | -0.22476 | 1.0464
40 | -0.0097042 | -0.0024312 | 0.0097044 | 0.0024312 | 1.7409e-07 | 8.3831e-08 | 0.014648 | 0.014648 | 0.014648 | 0.9858 | -0.27274 | 0.98582 | -0.27236 | 4.0241
41 | -0.010794 | -0.0027044 | 0.010795 | 0.0027046 | 2.4617e-07 | 1.2602e-07 | 0.016293 | 0.016293 | 0.016293 | 0.98582 | -0.27236 | 0.98584 | -0.27188 | 4.4761
42 | -0.012914 | -0.0032357 | 0.012916 | 0.0032369 | 2.2493e-06 | 1.2382e-06 | 0.019492 | 0.019492 | 0.019492 | 0.98584 | -0.27188 | 0.98603 | -0.26823 | 5.3549
43 | -0.014831 | -0.0037168 | 0.014834 | 0.0037187 | 3.3745e-06 | 1.9305e-06 | 0.022381 | 0.022381 | 0.022381 | 0.98603 | -0.26823 | 0.98628 | -0.26345 | 6.1486
44 | -0.053148 | -0.013344 | 0.053176 | 0.013362 | 2.8243e-05 | 1.7926e-05 | 0.080194 | 0.080194 | 0.080194 | 0.98628 | -0.26345 | 0.98685 | -0.25232 | 22.0314
45 | 0.038314 | 0.0096251 | -0.038311 | -0.0096232 | 2.9218e-06 | 1.8402e-06 | 0.057814 | 0.057814 | 0.057814 | 0.98628 | -0.26345 | 0.98619 | -0.26505 | 15.8829
46 | -0.0036348 | -0.00091096 | 0.0036352 | 0.00091076 | 4.5527e-07 | -2.0082e-07 | 0.0055471 | 0.0055469 | 0.0055471 | 0.97503 | -0.48149 | 0.97517 | -0.47886 | 1.5239
47 | -0.013017 | -0.0032621 | 0.013022 | 0.0032647 | 4.6434e-06 | 2.58e-06 | 0.019863 | 0.019863 | 0.019863 | 0.97517 | -0.47886 | 0.97555 | -0.47137 | 5.4568
48 | -0.013672 | -0.0034277 | 0.013674 | 0.0034285 | 1.5069e-06 | 8.4906e-07 | 0.020855 | 0.020855 | 0.020855 | 0.97555 | -0.47137 | 0.97567 | -0.46906 | 5.7293
49 | -0.013674 | -0.0034285 | 0.013675 | 0.0034295 | 1.7391e-06 | 9.7983e-07 | 0.020855 | 0.020855 | 0.020855 | 0.97567 | -0.46906 | 0.9758 | -0.46639 | 5.7293
50 | -0.013675 | -0.0034295 | 0.013678 | 0.0034309 | 2.432e-06 | 1.3701e-06 | 0.020855 | 0.020855 | 0.020855 | 0.9758 | -0.46639 | 0.97599 | -0.46266 | 5.7293
51 | 0.0034274 | 0.00085831 | -0.0034273 | -0.00085836 | 7.8579e-08 | -4.6937e-08 | 0.0052074 | 0.0052074 | 0.0052074 | 0.97933 | -0.39745 | 0.9793 | -0.39793 | 1.4306
52 | -0.0034274 | -0.00085831 | 0.003428 | 0.00085792 | 6.5406e-07 | -3.9092e-07 | 0.0052074 | 0.0052071 | 0.0052074 | 0.97933 | -0.39745 | 0.97953 | -0.39344 | 1.4306
53 | 0.0034273 | 0.00085836 | -0.0034268 | -0.00085866 | 5.0145e-07 | -2.9938e-07 | 0.0052074 | 0.0052076 | 0.0052076 | 0.9793 | -0.39793 | 0.97915 | -0.401 | 1.4307
54 | -0.0090228 | -0.0022601 | 0.0090246 | 0.0022609 | 1.7719e-06 | 8.1735e-07 | 0.013706 | 0.013706 | 0.013706 | 0.97953 | -0.39344 | 0.97974 | -0.38931 | 3.7655
55 | 0.0027588 | 0.00069126 | -0.0027587 | -0.0006914 | 1.1288e-07 | -1.4314e-07 | 0.0041926 | 0.0041927 | 0.0041927 | 0.97915 | -0.401 | 0.9791 | -0.40186 | 1.1518
56 | -0.012317 | -0.0030861 | 0.012323 | 0.0030891 | 5.4652e-06 | 2.973e-06 | 0.018707 | 0.018706 | 0.018707 | 0.97974 | -0.38931 | 0.98022 | -0.38 | 5.1392
57 | -0.012323 | -0.0030891 | 0.012333 | 0.003095 | 1.0821e-05 | 5.8851e-06 | 0.018706 | 0.018706 | 0.018706 | 0.98022 | -0.38 | 0.98116 | -0.36159 | 5.1391
58 | -0.016022 | -0.0040194 | 0.016045 | 0.004033 | 2.3403e-05 | 1.3641e-05 | 0.0243 | 0.0243 | 0.0243 | 0.98116 | -0.36159 | 0.98272 | -0.33099 | 6.6759
59 | -0.015694 | -0.003936 | 0.015695 | 0.0039368 | 1.3373e-06 | 7.7804e-07 | 0.023928 | 0.023928 | 0.023928 | 0.97599 | -0.46266 | 0.97608 | -0.46087 | 6.5736
60 | 0.11018 | 0.028198 | -0.10998 | -0.02807 | 0.00020003 | 0.00012777 | 0.16508 | 0.16508 | 0.16508 | 0.9944 | -0.10625 | 0.99243 | -0.14382 | 45.3522
61 | -0.11144 | -0.028512 | 0.11153 | 0.028572 | 9.3422e-05 | 5.9674e-05 | 0.16696 | 0.16696 | 0.16696 | 0.9944 | -0.10625 | 0.99531 | -0.088946 | 45.868
62 | 0.10655 | 0.027211 | -0.10636 | -0.027084 | 0.0001988 | 0.00012696 | 0.15994 | 0.15994 | 0.15994 | 0.99243 | -0.14382 | 0.99041 | -0.18249 | 43.9409
63 | -0.22442 | -0.057183 | 0.22479 | 0.057422 | 0.00037511 | 0.00023961 | 0.33584 | 0.33584 | 0.33584 | 0.99531 | -0.088946 | 0.99713 | -0.054368 | 46.1319
64 | 0.11289 | 0.028611 | -0.1128 | -0.028557 | 8.4293e-05 | 5.3845e-05 | 0.16888 | 0.16888 | 0.16888 | 0.99531 | -0.088946 | 0.9945 | -0.1045 | 46.3958
65 | 0.10636 | 0.027084 | -0.10619 | -0.026977 | 0.00016734 | 0.00010687 | 0.15994 | 0.15994 | 0.15994 | 0.99041 | -0.18249 | 0.98871 | -0.21517 | 43.9409
66 | -0.23228 | -0.0593 | 0.2329 | 0.059691 | 0.00061204 | 0.000391 | 0.34702 | 0.34702 | 0.34702 | 0.99713 | -0.054368 | 1 | 0 | 47.6679
67 | 0.1101 | 0.02788 | -0.10981 | -0.027693 | 0.00029277 | 0.000187 | 0.16484 | 0.16484 | 0.16484 | 0.9945 | -0.1045 | 0.99161 | -0.16004 | 45.285
68 | 0.10419 | 0.026477 | -0.10407 | -0.0264 | 0.00012126 | 7.7436e-05 | 0.15694 | 0.15694 | 0.15694 | 0.98871 | -0.21517 | 0.98745 | -0.23937 | 43.1155
69 | 0.0017995 | 0.00045087 | -0.0017995 | -0.000451 | 3.3671e-08 | -1.3464e-07 | 0.0027117 | 0.0027118 | 0.0027118 | 0.98745 | -0.23937 | 0.98743 | -0.23977 | 0.745
70 | 0.10227 | 0.025949 | -0.1022 | -0.025902 | 7.2498e-05 | 4.6295e-05 | 0.15423 | 0.15423 | 0.15423 | 0.98745 | -0.23937 | 0.98669 | -0.25412 | 42.3706
71 | -0.016816 | -0.0042186 | 0.016821 | 0.0042216 | 5.1009e-06 | 2.9981e-06 | 0.02545 | 0.02545 | 0.02545 | 0.98326 | -0.32045 | 0.98359 | -0.31409 | 6.9917
72 | 0.016816 | 0.0042186 | -0.016814 | -0.0042173 | 2.0783e-06 | 1.2216e-06 | 0.02545 | 0.02545 | 0.02545 | 0.98326 | -0.32045 | 0.98313 | -0.32304 | 6.9918
73 | 0.079814 | 0.020177 | -0.079749 | -0.020136 | 6.4641e-05 | 4.122e-05 | 0.12081 | 0.12081 | 0.12081 | 0.98359 | -0.31409 | 0.98272 | -0.33099 | 33.189
74 | -0.096635 | -0.024399 | 0.096757 | 0.024477 | 0.00012225 | 7.8047e-05 | 0.14626 | 0.14626 | 0.14626 | 0.98359 | -0.31409 | 0.98495 | -0.28772 | 40.1807
75 | 0.016147 | 0.0040502 | -0.016143 | -0.0040478 | 4.0963e-06 | 2.3898e-06 | 0.024441 | 0.024441 | 0.024441 | 0.98313 | -0.32304 | 0.98286 | -0.32837 | 6.7145
76 | 0.10028 | 0.025423 | -0.10026 | -0.025404 | 2.8457e-05 | 1.817e-05 | 0.15134 | 0.15134 | 0.15134 | 0.98669 | -0.25412 | 0.98638 | -0.26003 | 41.5772
77 | 0.063704 | 0.016103 | -0.063594 | -0.016034 | 0.0001094 | 6.9621e-05 | 0.096508 | 0.096508 | 0.096508 | 0.98272 | -0.33099 | 0.98088 | -0.36687 | 26.5133
78 | -0.097913 | -0.024767 | 0.098043 | 0.02485 | 0.00013027 | 8.3172e-05 | 0.148 | 0.148 | 0.148 | 0.98495 | -0.28772 | 0.98638 | -0.26003 | 40.6605
79 | 0.015407 | 0.0038633 | -0.015406 | -0.0038631 | 3.3579e-07 | 1.9405e-07 | 0.023326 | 0.023326 | 0.023326 | 0.98286 | -0.32837 | 0.98284 | -0.32882 | 6.4082
80 | 0.057871 | 0.014587 | -0.057811 | -0.014549 | 5.954e-05 | 3.7837e-05 | 0.087078 | 0.087078 | 0.087078 | 0.98924 | -0.20584 | 0.98813 | -0.22737 | 23.9227
81 | -0.0080966 | -0.0020291 | 0.0080975 | 0.0020295 | 9.6055e-07 | 4.0263e-07 | 0.012315 | 0.012315 | 0.012315 | 0.97833 | -0.41679 | 0.97845 | -0.4143 | 3.3832
82 | 0.0061514 | 0.0015416 | -0.0061513 | -0.0015416 | 6.684e-08 | 1.721e-08 | 0.0093561 | 0.0093561 | 0.0093561 | 0.97833 | -0.41679 | 0.97832 | -0.41701 | 2.5704
83 | -0.011003 | -0.0027578 | 0.011003 | 0.0027578 | 1.2128e-07 | 6.3112e-08 | 0.016734 | 0.016734 | 0.016734 | 0.97845 | -0.4143 | 0.97847 | -0.41406 | 4.5971
84 | 0.0042998 | 0.0010776 | -0.0042997 | -0.0010776 | 1.3413e-07 | -1.9157e-08 | 0.00654 | 0.00654 | 0.00654 | 0.97832 | -0.41701 | 0.97828 | -0.41767 | 1.7967
85 | -0.012754 | -0.0031965 | 0.012758 | 0.0031986 | 3.7573e-06 | 2.07e-06 | 0.019396 | 0.019395 | 0.019396 | 0.97847 | -0.41406 | 0.97878 | -0.40788 | 5.3285
86 | -0.015002 | -0.0037612 | 0.015005 | 0.0037626 | 2.5357e-06 | 1.4595e-06 | 0.022808 | 0.022808 | 0.022808 | 0.97878 | -0.40788 | 0.97896 | -0.40434 | 6.2659
87 | 0.046597 | 0.011729 | -0.046568 | -0.01171 | 2.9337e-05 | 1.858e-05 | 0.070845 | 0.070846 | 0.070846 | 0.97896 | -0.40434 | 0.97829 | -0.41752 | 19.4631
88 | -0.061602 | -0.015492 | 0.061712 | 0.015562 | 0.00011044 | 7.0259e-05 | 0.093653 | 0.093653 | 0.093653 | 0.97896 | -0.40434 | 0.98088 | -0.36687 | 25.729
89 | 0.044553 | 0.011205 | -0.044504 | -0.011175 | 4.8698e-05 | 3.0812e-05 | 0.067781 | 0.067781 | 0.067781 | 0.97829 | -0.41752 | 0.97712 | -0.44043 | 18.6211
90 | 0.031414 | 0.0078909 | -0.031405 | -0.0078855 | 8.6334e-06 | 5.3949e-06 | 0.04742 | 0.04742 | 0.04742 | 0.98588 | -0.27111 | 0.98559 | -0.27688 | 13.0275
91 | -0.03324 | -0.0083485 | 0.033248 | 0.008354 | 8.7678e-06 | 5.493e-06 | 0.050176 | 0.050176 | 0.050176 | 0.98588 | -0.27111 | 0.98617 | -0.26559 | 13.7846
92 | 0.029573 | 0.0074263 | -0.029563 | -0.00742 | 1.0253e-05 | 6.3873e-06 | 0.044654 | 0.044654 | 0.044654 | 0.98559 | -0.27688 | 0.98521 | -0.28414 | 12.2676
93 | -0.036068 | -0.0090607 | 0.036069 | 0.0090612 | 9.2995e-07 | 5.8449e-07 | 0.05443 | 0.05443 | 0.05443 | 0.98617 | -0.26559 | 0.98619 | -0.26505 | 14.9533
94 | 0.027277 | 0.0068471 | -0.027267 | -0.0068411 | 9.6698e-06 | 5.9953e-06 | 0.041202 | 0.041202 | 0.041202 | 0.98521 | -0.28414 | 0.98483 | -0.29158 | 11.3192
95 | 0.026206 | 0.0065751 | -0.026195 | -0.006568 | 1.1559e-05 | 7.1475e-06 | 0.039598 | 0.039598 | 0.039598 | 0.98483 | -0.29158 | 0.98436 | -0.30083 | 10.8787
96 | 0.0064353 | 0.0016126 | -0.0064344 | -0.0016123 | 8.7297e-07 | 2.4604e-07 | 0.0097279 | 0.009728 | 0.009728 | 0.98436 | -0.30083 | 0.98421 | -0.30368 | 2.6725
97 | 0.019759 | 0.0049554 | -0.019754 | -0.0049524 | 4.944e-06 | 2.9764e-06 | 0.029871 | 0.029871 | 0.029871 | 0.98436 | -0.30083 | 0.98409 | -0.30609 | 8.2062
98 | -0.055782 | -0.014015 | 0.055849 | 0.014057 | 6.6508e-05 | 4.2244e-05 | 0.084123 | 0.084123 | 0.084123 | 0.98685 | -0.25232 | 0.98813 | -0.22737 | 23.1108
99 | 0.0028327 | 0.00070967 | -0.0028325 | -0.00070989 | 1.8508e-07 | -2.235e-07 | 0.0042826 | 0.0042827 | 0.0042827 | 0.98421 | -0.30368 | 0.98414 | -0.30505 | 1.1766
100 | 0.0038305 | 0.00095965 | -0.0038304 | -0.00095971 | 1.5917e-07 | -5.8875e-08 | 0.0057919 | 0.005792 | 0.005792 | 0.98409 | -0.30609 | 0.98404 | -0.30696 | 1.5912
101 | 0.015924 | 0.0039928 | -0.015922 | -0.0039917 | 1.8722e-06 | 1.0888e-06 | 0.024079 | 0.024079 | 0.024079 | 0.98409 | -0.30609 | 0.98396 | -0.30855 | 6.615
102 | -0.043565 | -0.010934 | 0.043578 | 0.010943 | 1.282e-05 | 8.1079e-06 | 0.066371 | 0.066371 | 0.066371 | 0.97681 | -0.44659 | 0.97712 | -0.44043 | 18.2337
103 | 0.043565 | 0.010934 | -0.043555 | -0.010928 | 1.0587e-05 | 6.6955e-06 | 0.066371 | 0.066371 | 0.066371 | 0.97681 | -0.44659 | 0.97655 | -0.45169 | 18.2337
104 | 0.024886 | 0.0062428 | -0.024879 | -0.0062385 | 7.004e-06 | 4.3201e-06 | 0.037922 | 0.037922 | 0.037922 | 0.97655 | -0.45169 | 0.97625 | -0.4576 | 10.418
105 | 0.018669 | 0.0046849 | -0.018665 | -0.0046823 | 4.3532e-06 | 2.6067e-06 | 0.028449 | 0.028449 | 0.028449 | 0.97655 | -0.45169 | 0.9763 | -0.45658 | 7.8157
106 | -0.017225 | -0.0043204 | 0.017229 | 0.0043225 | 3.5223e-06 | 2.084e-06 | 0.026261 | 0.026261 | 0.026261 | 0.97608 | -0.46087 | 0.9763 | -0.45658 | 7.2146
107 | 0.023184 | 0.0058137 | -0.023178 | -0.00581 | 5.8877e-06 | 3.611e-06 | 0.035338 | 0.035338 | 0.035338 | 0.97625 | -0.4576 | 0.97598 | -0.46293 | 9.7083
108 | 0.016645 | 0.0041729 | -0.016643 | -0.0041717 | 2.0306e-06 | 1.1946e-06 | 0.025379 | 0.025379 | 0.025379 | 0.97598 | -0.46293 | 0.97585 | -0.46549 | 6.9721
109 | 0.013136 | 0.0032927 | -0.013135 | -0.0032921 | 1.0836e-06 | 6.0356e-07 | 0.020031 | 0.020031 | 0.020031 | 0.97585 | -0.46549 | 0.97576 | -0.46722 | 5.5029
110 | 0.010034 | 0.0025149 | -0.010033 | -0.0025142 | 1.3763e-06 | 6.851e-07 | 0.015302 | 0.015302 | 0.015302 | 0.97576 | -0.46722 | 0.97561 | -0.4701 | 4.2038
111 | -0.01368 | -0.0034294 | 0.013681 | 0.0034301 | 1.3239e-06 | 7.4254e-07 | 0.02069 | 0.02069 | 0.02069 | 0.98386 | -0.31058 | 0.98396 | -0.30855 | 5.6841
112 | 0.01266 | 0.0031739 | -0.012658 | -0.0031725 | 2.5224e-06 | 1.3814e-06 | 0.019148 | 0.019148 | 0.019148 | 0.98386 | -0.31058 | 0.98364 | -0.31477 | 5.2606
113 | 0.008125 | 0.0020364 | -0.0081241 | -0.0020361 | 8.907e-07 | 3.705e-07 | 0.012291 | 0.012291 | 0.012291 | 0.98364 | -0.31477 | 0.98353 | -0.31707 | 3.3767
114 | 0.0069344 | 0.0017379 | -0.0069336 | -0.0017376 | 7.8756e-07 | 2.6192e-07 | 0.010491 | 0.010491 | 0.010491 | 0.98353 | -0.31707 | 0.9834 | -0.31945 | 2.8822
115 | 0.0010759 | 0.00026938 | -0.0010759 | -0.00026964 | 2.2143e-08 | -2.6924e-07 | 0.0016268 | 0.0016269 | 0.0016269 | 0.98404 | -0.30696 | 0.98402 | -0.30739 | 0.44696
116 | 0.0053502 | 0.0013408 | -0.0053498 | -0.0013407 | 3.8471e-07 | 4.7624e-08 | 0.0080954 | 0.0080955 | 0.0080955 | 0.9834 | -0.31945 | 0.98333 | -0.32096 | 2.224
117 | 0.0014636 | 0.00036677 | -0.0014636 | -0.00036681 | 7.4337e-09 | -4.6506e-08 | 0.0022148 | 0.0022148 | 0.0022148 | 0.98333 | -0.32096 | 0.98332 | -0.32107 | 0.60846
118 | 0.014857 | 0.0037254 | -0.014852 | -0.0037223 | 5.3322e-06 | 3.0566e-06 | 0.022494 | 0.022494 | 0.022494 | 0.98284 | -0.32882 | 0.98245 | -0.33636 | 6.1797
119 | 0.0022707 | 0.00056887 | -0.0022706 | -0.00056907 | 8.8576e-08 | -1.9591e-07 | 0.00344 | 0.0034401 | 0.0034401 | 0.98219 | -0.34152 | 0.98215 | -0.34234 | 0.94509
120 | 0.0079502 | 0.0019923 | -0.0079502 | -0.0019923 | 6.3474e-08 | 2.6248e-08 | 0.012126 | 0.012126 | 0.012126 | 0.97561 | -0.4701 | 0.9756 | -0.47027 | 3.3313
121 | 0.0055465 | 0.0013899 | -0.0055459 | -0.0013898 | 6.0313e-07 | 1.0541e-07 | 0.0084597 | 0.0084598 | 0.0084598 | 0.9756 | -0.47027 | 0.97549 | -0.47255 | 2.3241
122 | 0.0033057 | 0.00082835 | -0.0033057 | -0.00082835 | 7.7441e-09 | -5.1826e-09 | 0.0050425 | 0.0050425 | 0.0050425 | 0.97549 | -0.47255 | 0.97549 | -0.4726 | 1.3853
123 | 0.0010161 | 0.00025453 | -0.0010161 | -0.00025466 | 1.0171e-08 | -1.3442e-07 | 0.00155 | 0.00155 | 0.00155 | 0.97549 | -0.4726 | 0.97548 | -0.47281 | 0.42583

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.24204 | 0.061571

## res_load
| p_mw | q_mvar
0 | 0.00097128 | 0.00024343
1 | 0.0017952 | 0.00044992
2 | 0.0027227 | 0.00068237
3 | 0.0013362 | 0.00033488
4 | 0.00058958 | 0.00014776
5 | 0.0019437 | 0.00048714
6 | 0.0029508 | 0.00073953
7 | 0.0015161 | 0.00037998
8 | 0.0017469 | 0.00043782
9 | 0.0027153 | 0.00068052
10 | 0.0018694 | 0.00046851
11 | 0.0021257 | 0.00053274
12 | 0.0045515 | 0.0011407
13 | 0.0013382 | 0.00033537
14 | 0.00081917 | 0.0002053
15 | 0.0011042 | 0.00027675
16 | 0.0012322 | 0.00030881
17 | 0.0016962 | 0.0004251
18 | 0.00036944 | 9.259e-05
19 | 0.0021325 | 0.00053446
20 | 0.00083506 | 0.00020929
21 | 0.00062261 | 0.00015604
22 | 0.0033951 | 0.00085089
23 | 0.00099225 | 0.00024868
24 | 0.003266 | 0.00081854
25 | 0.0059405 | 0.0014888
26 | 0.0050511 | 0.0012659
27 | 0.0019578 | 0.00049067
28 | 0.00109 | 0.00027318
29 | 0.0021193 | 0.00053115
30 | 0.0019145 | 0.00047981
31 | 0.0036348 | 0.00091096
32 | 0.0093819 | 0.0023513
33 | 0.00065047 | 0.00016302
34 | 0.0055948 | 0.0014022
35 | 0.00066792 | 0.0001674
36 | 0.0032924 | 0.00082517
37 | 0.0036886 | 0.00092444
38 | 0.0027587 | 0.0006914
39 | 0.0020157 | 0.00050517
40 | 0.0012548 | 0.00031448
41 | 0.0034264 | 0.00085873
42 | 0.0074935 | 0.0018781
43 | 0.0027024 | 0.00067729
44 | 0.0019963 | 0.00050032
45 | 0.007497 | 0.0018789
46 | 0.002806 | 0.00070325
47 | 0.00066683 | 0.00016712
48 | 0.0017995 | 0.000451
49 | 0.0019148 | 0.0004799
50 | 0.0011561 | 0.00028976
51 | 0.00073638 | 0.00018455
52 | 0.0054656 | 0.0013698
53 | 0.0019452 | 0.00048751
54 | 0.0029057 | 0.00072824
55 | 0.0018515 | 0.00046402
56 | 0.0017504 | 0.00043869
57 | 0.0042997 | 0.0010776
58 | 0.0022447 | 0.00056258
59 | 0.002015 | 0.00050499
60 | 0.001882 | 0.00047166
61 | 0.0018259 | 0.00045763
62 | 0.0018321 | 0.00045918
63 | 0.0028194 | 0.00070662
64 | 0.0022856 | 0.00057282
65 | 0.0022424 | 0.00056201
66 | 0.0010614 | 0.000266
67 | 0.0026057 | 0.00065304
68 | 0.0036017 | 0.00090267
69 | 0.0019625 | 0.00049185
70 | 0.00092602 | 0.00023208
71 | 0.0015305 | 0.00038359
72 | 0.001695 | 0.00042481
73 | 0.0014358 | 0.00035984
74 | 0.0065324 | 0.0016372
75 | 0.0035072 | 0.00087898
76 | 0.0031009 | 0.00077717
77 | 0.0010195 | 0.00025551
78 | 0.0022406 | 0.00056156
79 | 0.004533 | 0.0011361
80 | 0.0011897 | 0.00029817
81 | 0.0027545 | 0.00069033
82 | 0.0015834 | 0.00039685
83 | 0.0010759 | 0.00026964
84 | 0.0038862 | 0.00097396
85 | 0.0028325 | 0.00070989
86 | 0.0014636 | 0.00036681
87 | 0.00054946 | 0.00013771
88 | 0.0019322 | 0.00048426
89 | 0.0022121 | 0.0005544
90 | 0.0018319 | 0.00045911
91 | 0.0018167 | 0.00045532
92 | 0.0022706 | 0.00056907
93 | 0.0025298 | 0.00063403
94 | 0.0020824 | 0.00052191
95 | 0.0024036 | 0.00060241
96 | 0.0022402 | 0.00056145
97 | 0.0022896 | 0.00057383
98 | 0.0010161 | 0.00025466

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1