## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2530-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2530-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2530-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2530-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2530-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2530-4_0_4_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_2530-4_0_4_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_2530-4_0_4_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_2530-4_0_4_node_99 | 0.4 | n |  | TRUE
9 | bus_LV_2530-4_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2530-4_0_4_node_59 | 0.4 | n |  | TRUE
11 | bus_LV_2530-4_0_4_node_42 | 0.4 | n |  | TRUE
12 | bus_LV_2530-4_0_4_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_2530-4_0_4_node_90 | 0.4 | n |  | TRUE
14 | bus_LV_2530-4_0_4_node_96 | 0.4 | n |  | TRUE
15 | bus_LV_2530-4_0_4_node_128 | 0.4 | n |  | TRUE
16 | bus_LV_2530-4_0_4_node_57 | 0.4 | n |  | TRUE
17 | bus_LV_2530-4_0_4_node_6 | 0.4 | n |  | TRUE
18 | bus_LV_2530-4_0_4_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_2530-4_0_4_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_2530-4_0_4_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_2530-4_0_4_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2530-4_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2530-4_0_4_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_2530-4_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_2530-4_0_4_node_52 | 0.4 | n |  | TRUE
26 | bus_LV_2530-4_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_2530-4_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2530-4_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_2530-4_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2530-4_0_4_node_112 | 0.4 | n |  | TRUE
31 | bus_LV_2530-4_0_4_node_109 | 0.4 | n |  | TRUE
32 | bus_LV_2530-4_0_4_node_108 | 0.4 | n |  | TRUE
33 | bus_LV_2530-4_0_4_node_53 | 0.4 | n |  | TRUE
34 | bus_LV_2530-4_0_4_node_121 | 0.4 | n |  | TRUE
35 | bus_LV_2530-4_0_4_node_110 | 0.4 | n |  | TRUE
36 | bus_LV_2530-4_0_4_node_93 | 0.4 | n |  | TRUE
37 | bus_LV_2530-4_0_4_node_40 | 0.4 | n |  | TRUE
38 | bus_LV_2530-4_0_4_node_88 | 0.4 | n |  | TRUE
39 | bus_LV_2530-4_0_4_node_95 | 0.4 | n |  | TRUE
40 | bus_LV_2530-4_0_4_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_2530-4_0_4_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_2530-4_0_4_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_2530-4_0_4_node_133 | 0.4 | n |  | TRUE
44 | bus_LV_2530-4_0_4_node_134 | 0.4 | n |  | TRUE
45 | bus_LV_2530-4_0_4_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_2530-4_0_4_node_24 | 0.4 | n |  | TRUE
47 | bus_LV_2530-4_0_4_node_130 | 0.4 | n |  | TRUE
48 | bus_LV_2530-4_0_4_node_84 | 0.4 | n |  | TRUE
49 | bus_LV_2530-4_0_4_node_129 | 0.4 | n |  | TRUE
50 | bus_LV_2530-4_0_4_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_2530-4_0_4_node_25 | 0.4 | n |  | TRUE
52 | bus_LV_2530-4_0_4_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_2530-4_0_4_node_29 | 0.4 | n |  | TRUE
54 | bus_LV_2530-4_0_4_node_28 | 0.4 | n |  | TRUE
55 | bus_LV_2530-4_0_4_node_135 | 0.4 | n |  | TRUE
56 | bus_LV_2530-4_0_4_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_2530-4_0_4_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_2530-4_0_4_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_2530-4_0_4_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_2530-4_0_4_node_136 | 0.4 | n |  | TRUE
61 | bus_LV_2530-4_0_4_node_33 | 0.4 | n |  | TRUE
62 | bus_LV_2530-4_0_4_node_34 | 0.4 | n |  | TRUE
63 | bus_LV_2530-4_0_4_node_35 | 0.4 | n |  | TRUE
64 | bus_LV_2530-4_0_4_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_2530-4_0_4_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_2530-4_0_4_node_38 | 0.4 | n |  | TRUE
67 | bus_LV_2530-4_0_4_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_2530-4_0_4_node_43 | 0.4 | n |  | TRUE
69 | bus_LV_2530-4_0_4_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_2530-4_0_4_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_2530-4_0_4_node_50 | 0.4 | n |  | TRUE
72 | bus_LV_2530-4_0_4_node_94 | 0.4 | n |  | TRUE
73 | bus_LV_2530-4_0_4_node_45 | 0.4 | n |  | TRUE
74 | bus_LV_2530-4_0_4_node_47 | 0.4 | n |  | TRUE
75 | bus_LV_2530-4_0_4_node_48 | 0.4 | n |  | TRUE
76 | bus_LV_2530-4_0_4_node_49 | 0.4 | n |  | TRUE
77 | bus_LV_2530-4_0_4_node_55 | 0.4 | n |  | TRUE
78 | bus_LV_2530-4_0_4_node_56 | 0.4 | n |  | TRUE
79 | bus_LV_2530-4_0_4_node_58 | 0.4 | n |  | TRUE
80 | bus_LV_2530-4_0_4_node_127 | 0.4 | n |  | TRUE
81 | bus_LV_2530-4_0_4_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_2530-4_0_4_node_61 | 0.4 | n |  | TRUE
83 | bus_LV_2530-4_0_4_node_62 | 0.4 | n |  | TRUE
84 | bus_LV_2530-4_0_4_node_63 | 0.4 | n |  | TRUE
85 | bus_LV_2530-4_0_4_node_64 | 0.4 | n |  | TRUE
86 | bus_LV_2530-4_0_4_node_74 | 0.4 | n |  | TRUE
87 | bus_LV_2530-4_0_4_node_75 | 0.4 | n |  | TRUE
88 | bus_LV_2530-4_0_4_node_89 | 0.4 | n |  | TRUE
89 | bus_LV_2530-4_0_4_node_100 | 0.4 | n |  | TRUE
90 | bus_LV_2530-4_0_4_node_106 | 0.4 | n |  | TRUE
91 | bus_LV_2530-4_0_4_node_87 | 0.4 | n |  | TRUE
92 | bus_LV_2530-4_0_4_node_65 | 0.4 | n |  | TRUE
93 | bus_LV_2530-4_0_4_node_66 | 0.4 | n |  | TRUE
94 | bus_LV_2530-4_0_4_node_67 | 0.4 | n |  | TRUE
95 | bus_LV_2530-4_0_4_node_68 | 0.4 | n |  | TRUE
96 | bus_LV_2530-4_0_4_node_69 | 0.4 | n |  | TRUE
97 | bus_LV_2530-4_0_4_node_70 | 0.4 | n |  | TRUE
98 | bus_LV_2530-4_0_4_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_2530-4_0_4_node_138 | 0.4 | n |  | TRUE
100 | bus_LV_2530-4_0_4_node_80 | 0.4 | n |  | TRUE
101 | bus_LV_2530-4_0_4_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_2530-4_0_4_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_2530-4_0_4_node_131 | 0.4 | n |  | TRUE
104 | bus_LV_2530-4_0_4_node_132 | 0.4 | n |  | TRUE
105 | bus_LV_2530-4_0_4_node_137 | 0.4 | n |  | TRUE
106 | bus_LV_2530-4_0_4_node_71 | 0.4 | n |  | TRUE
107 | bus_LV_2530-4_0_4_node_72 | 0.4 | n |  | TRUE
108 | bus_LV_2530-4_0_4_node_73 | 0.4 | n |  | TRUE
109 | bus_LV_2530-4_0_4_node_98 | 0.4 | n |  | TRUE
110 | bus_LV_2530-4_0_4_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_2530-4_0_4_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_2530-4_0_4_node_79 | 0.4 | n |  | TRUE
113 | bus_LV_2530-4_0_4_node_101 | 0.4 | n |  | TRUE
114 | bus_LV_2530-4_0_4_node_76 | 0.4 | n |  | TRUE
115 | bus_LV_2530-4_0_4_node_77 | 0.4 | n |  | TRUE
116 | bus_LV_2530-4_0_4_node_78 | 0.4 | n |  | TRUE
117 | bus_LV_2530-4_0_4_node_103 | 0.4 | n |  | TRUE
118 | bus_LV_2530-4_0_4_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_2530-4_0_4_node_81 | 0.4 | n |  | TRUE
120 | bus_LV_2530-4_0_4_node_83 | 0.4 | n |  | TRUE
121 | bus_LV_2530-4_0_4_node_97 | 0.4 | n |  | TRUE
122 | bus_LV_2530-4_0_4_node_139 | 0.4 | n |  | TRUE
123 | bus_LV_2530-4_0_4_node_111 | 0.4 | n |  | TRUE
124 | bus_LV_2530-4_0_4_node_114 | 0.4 | n |  | TRUE
125 | bus_LV_2530-4_0_4_node_113 | 0.4 | n |  | TRUE
126 | bus_LV_2530-4_0_4_node_120 | 0.4 | n |  | TRUE
127 | bus_LV_2530-4_0_4_node_122 | 0.4 | n |  | TRUE
128 | bus_LV_2530-4_0_4_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_2530-4_0_4_node_116 | 0.4 | n |  | TRUE
130 | bus_LV_2530-4_0_4_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_2530-4_0_4_node_118 | 0.4 | n |  | TRUE
132 | bus_LV_2530-4_0_4_node_119 | 0.4 | n |  | TRUE
133 | bus_LV_2530-4_0_4_node_125 | 0.4 | n |  | TRUE
134 | bus_LV_2530-4_0_4_node_123 | 0.4 | n |  | TRUE
135 | bus_LV_2530-4_0_4_node_126 | 0.4 | n |  | TRUE
136 | bus_LV_2530-4_0_4_node_124 | 0.4 | n |  | TRUE
137 | bus_MV_386_0_node_41 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2530-4_0_4_load_0 | 0 | 0.050077 | 0.012551 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2530-4_0_4_load_1 | 1 | 0.071223 | 0.01785 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2530-4_0_4_load_4 | 4 | 0.058205 | 0.014587 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2530-4_0_4_load_17 | 6 | 0.09328 | 0.023378 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2530-4_0_4_load_18 | 7 | 0.00099148 | 0.00024849 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2530-4_0_4_load_99 | 8 | 0.0028457 | 0.0007132 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2530-4_0_4_load_5 | 9 | 0.0023005 | 0.00057655 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2530-4_0_4_load_42 | 11 | 0.00095966 | 0.00024051 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2530-4_0_4_load_39 | 12 | 0.0029801 | 0.0007469 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2530-4_0_4_load_90 | 13 | 0.03704 | 0.0092831 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2530-4_0_4_load_96 | 14 | 0.003267 | 0.0008188 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2530-4_0_4_load_128 | 15 | 0.0032739 | 0.00082053 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2530-4_0_4_load_57 | 16 | 0.0023908 | 0.00059919 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2530-4_0_4_load_6 | 17 | 0.010264 | 0.0025723 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2530-4_0_4_load_7 | 18 | 0.00090778 | 0.00022751 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2530-4_0_4_load_10 | 21 | 0.00070796 | 0.00017743 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2530-4_0_4_load_13 | 22 | 0.003902 | 0.00097795 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2530-4_0_4_load_11 | 23 | 0.0038017 | 0.00095279 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2530-4_0_4_load_22 | 24 | 0.00063888 | 0.00016012 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2530-4_0_4_load_52 | 25 | 0.003654 | 0.00091578 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2530-4_0_4_load_23 | 27 | 0.00063898 | 0.00016014 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2530-4_0_4_load_15 | 29 | 0.0024617 | 0.00061697 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2530-4_0_4_load_112 | 30 | 0.00081511 | 0.00020429 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2530-4_0_4_load_109 | 31 | 0.0018001 | 0.00045115 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2530-4_0_4_load_108 | 32 | 0.0028806 | 0.00072194 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2530-4_0_4_load_53 | 33 | 0.0012895 | 0.00032319 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2530-4_0_4_load_121 | 34 | 0.0010289 | 0.00025785 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2530-4_0_4_load_110 | 35 | 0.0015441 | 0.00038699 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2530-4_0_4_load_93 | 36 | 0.00075505 | 0.00018923 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2530-4_0_4_load_40 | 37 | 0.0012509 | 0.0003135 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2530-4_0_4_load_88 | 38 | 0.00070373 | 0.00017637 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2530-4_0_4_load_19 | 40 | 0.0003494 | 8.7568e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2530-4_0_4_load_20 | 41 | 0.00069538 | 0.00017428 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2530-4_0_4_load_133 | 43 | 0.0038636 | 0.00096832 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2530-4_0_4_load_134 | 44 | 0.0045391 | 0.0011376 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2530-4_0_4_load_24 | 46 | 0.0043799 | 0.0010977 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2530-4_0_4_load_84 | 48 | 0.0025781 | 0.00064613 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2530-4_0_4_load_129 | 49 | 0.0068016 | 0.0017046 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2530-4_0_4_load_32 | 50 | 0.0010322 | 0.0002587 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2530-4_0_4_load_25 | 51 | 0.00029947 | 7.5054e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2530-4_0_4_load_27 | 52 | 0.0012992 | 0.0003256 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2530-4_0_4_load_29 | 53 | 0.0010921 | 0.00027369 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2530-4_0_4_load_28 | 54 | 0.0010135 | 0.00025401 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2530-4_0_4_load_31 | 57 | 0.00018833 | 4.72e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2530-4_0_4_load_46 | 58 | 0.0003048 | 7.6389e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2530-4_0_4_load_44 | 59 | 0.00013185 | 3.3044e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2530-4_0_4_load_136 | 60 | 0.0027743 | 0.00069532 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2530-4_0_4_load_33 | 61 | 0.0040892 | 0.0010249 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2530-4_0_4_load_34 | 62 | 0.0034864 | 0.00087377 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2530-4_0_4_load_35 | 63 | 0.0020584 | 0.00051588 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2530-4_0_4_load_36 | 64 | 0.0006765 | 0.00016955 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2530-4_0_4_load_38 | 66 | 0.0010929 | 0.00027392 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2530-4_0_4_load_54 | 67 | 0.0012181 | 0.00030528 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2530-4_0_4_load_43 | 68 | 0.00016779 | 4.2051e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2530-4_0_4_load_51 | 70 | 0.001568 | 0.00039298 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2530-4_0_4_load_50 | 71 | 0.00014963 | 3.75e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2530-4_0_4_load_94 | 72 | 0.0012756 | 0.0003197 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2530-4_0_4_load_45 | 73 | 0.00053611 | 0.00013436 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2530-4_0_4_load_47 | 74 | 0.00015934 | 3.9934e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2530-4_0_4_load_48 | 75 | 0.00017587 | 4.4078e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2530-4_0_4_load_49 | 76 | 0.00013123 | 3.289e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2530-4_0_4_load_55 | 77 | 0.044305 | 0.011104 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2530-4_0_4_load_56 | 78 | 0.0023266 | 0.0005831 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2530-4_0_4_load_58 | 79 | 0.0018323 | 0.00045921 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2530-4_0_4_load_127 | 80 | 0.001399 | 0.00035062 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2530-4_0_4_load_60 | 81 | 0.0033459 | 0.00083856 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2530-4_0_4_load_61 | 82 | 0.0011819 | 0.00029622 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2530-4_0_4_load_62 | 83 | 0.0012618 | 0.00031624 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2530-4_0_4_load_64 | 85 | 0.0016458 | 0.00041248 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2530-4_0_4_load_89 | 88 | 0.0022049 | 0.00055259 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2530-4_0_4_load_100 | 89 | 0.0012441 | 0.0003118 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2530-4_0_4_load_106 | 90 | 0.00071284 | 0.00017865 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2530-4_0_4_load_87 | 91 | 0.029773 | 0.0074619 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2530-4_0_4_load_65 | 92 | 0.00072197 | 0.00018094 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2530-4_0_4_load_66 | 93 | 0.0035387 | 0.00088688 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2530-4_0_4_load_69 | 96 | 0.00174 | 0.00043608 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2530-4_0_4_load_138 | 99 | 0.0037848 | 0.00094855 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2530-4_0_4_load_80 | 100 | 0.00082338 | 0.00020636 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2530-4_0_4_load_91 | 101 | 0.00045132 | 0.00011311 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2530-4_0_4_load_137 | 105 | 0.0069955 | 0.0017532 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2530-4_0_4_load_71 | 106 | 0.0042254 | 0.001059 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2530-4_0_4_load_72 | 107 | 0.0011254 | 0.00028206 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2530-4_0_4_load_107 | 110 | 0.00089505 | 0.00022432 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2530-4_0_4_load_105 | 111 | 0.00079461 | 0.00019915 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2530-4_0_4_load_79 | 112 | 0.0022996 | 0.00057633 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2530-4_0_4_load_101 | 113 | 0.0042172 | 0.0010569 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2530-4_0_4_load_76 | 114 | 0.0017203 | 0.00043114 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2530-4_0_4_load_77 | 115 | 0.000441 | 0.00011053 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2530-4_0_4_load_103 | 117 | 0.0019988 | 0.00050095 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2530-4_0_4_load_102 | 118 | 0.0020819 | 0.00052179 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2530-4_0_4_load_81 | 119 | 0.0063269 | 0.0015857 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2530-4_0_4_load_97 | 121 | 0.0026518 | 0.00066462 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2530-4_0_4_load_114 | 124 | 0.0015132 | 0.00037925 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2530-4_0_4_load_113 | 125 | 0.0011731 | 0.000294 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2530-4_0_4_load_120 | 126 | 0.0014612 | 0.00036621 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2530-4_0_4_load_122 | 127 | 0.001169 | 0.00029299 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2530-4_0_4_load_115 | 128 | 0.0008193 | 0.00020534 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2530-4_0_4_load_116 | 129 | 0.0021792 | 0.00054615 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2530-4_0_4_load_118 | 131 | 0.0015924 | 0.00039908 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2530-4_0_4_load_125 | 133 | 0.0017925 | 0.00044924 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2530-4_0_4_load_123 | 134 | 0.0019606 | 0.00049136 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2530-4_0_4_load_126 | 135 | 0.00086656 | 0.00021718 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2530-4_0_4_load_124 | 136 | 0.0015119 | 0.00037892 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2530-4_0_4_line_0 |  | 0 | 1 | 0.026537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2530-4_0_4_line_1 |  | 0 | 2 | 0.0047354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2530-4_0_4_line_2 |  | 1 | 3 | 0.033196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2530-4_0_4_line_3 |  | 2 | 4 | 0.012438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2530-4_0_4_line_4 |  | 3 | 5 | 0.007581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_2530-4_0_4_line_5 |  | 3 | 6 | 0.028115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2530-4_0_4_line_6 |  | 3 | 7 | 0.026562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2530-4_0_4_line_7 |  | 4 | 8 | 0.031569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2530-4_0_4_line_8 |  | 5 | 11 | 0.019068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2530-4_0_4_line_9 |  | 5 | 12 | 0.028772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2530-4_0_4_line_10 |  | 6 | 13 | 0.017809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2530-4_0_4_line_11 |  | 7 | 14 | 0.023693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2530-4_0_4_line_12 |  | 9 | 10 | 0.010141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2530-4_0_4_line_13 |  | 10 | 15 | 0.0092218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2530-4_0_4_line_14 |  | 10 | 16 | 0.017001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2530-4_0_4_line_15 |  | 11 | 36 | 0.011334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2530-4_0_4_line_16 |  | 12 | 37 | 0.020307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2530-4_0_4_line_17 |  | 13 | 38 | 0.010909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2530-4_0_4_line_18 |  | 14 | 39 | 0.0035817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2530-4_0_4_line_19 |  | 15 | 80 | 0.021409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2530-4_0_4_line_20 |  | 16 | 77 | 0.0018207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2530-4_0_4_line_21 |  | 17 | 18 | 0.0085175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2530-4_0_4_line_22 |  | 17 | 19 | 0.023986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2530-4_0_4_line_23 |  | 19 | 20 | 0.040098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2530-4_0_4_line_24 |  | 19 | 21 | 0.014535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2530-4_0_4_line_25 |  | 20 | 22 | 0.01911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2530-4_0_4_line_26 |  | 20 | 23 | 0.015249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2530-4_0_4_line_27 |  | 21 | 24 | 0.015553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2530-4_0_4_line_28 |  | 22 | 25 | 0.010784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2530-4_0_4_line_29 |  | 23 | 26 | 0.020233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2530-4_0_4_line_30 |  | 24 | 27 | 0.005245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2530-4_0_4_line_31 |  | 25 | 33 | 0.026168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2530-4_0_4_line_32 |  | 26 | 28 | 0.034984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2530-4_0_4_line_33 |  | 26 | 29 | 0.023519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2530-4_0_4_line_34 |  | 27 | 50 | 0.0094471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2530-4_0_4_line_35 |  | 28 | 30 | 0.0066728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2530-4_0_4_line_36 |  | 28 | 31 | 0.01177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2530-4_0_4_line_37 |  | 29 | 32 | 0.023477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2530-4_0_4_line_38 |  | 30 | 34 | 0.0096106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2530-4_0_4_line_39 |  | 31 | 35 | 0.025899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2530-4_0_4_line_40 |  | 33 | 65 | 0.020387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_2530-4_0_4_line_41 |  | 34 | 127 | 0.0020844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2530-4_0_4_line_42 |  | 35 | 123 | 0.0057954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2530-4_0_4_line_43 |  | 36 | 72 | 0.0027779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2530-4_0_4_line_44 |  | 37 | 69 | 0.0037836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2530-4_0_4_line_45 |  | 38 | 91 | 0.00094637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2530-4_0_4_line_46 |  | 39 | 121 | 0.033573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2530-4_0_4_line_47 |  | 39 | 102 | 0.015667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2530-4_0_4_line_48 |  | 40 | 41 | 0.036772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2530-4_0_4_line_49 |  | 41 | 42 | 0.039345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2530-4_0_4_line_50 |  | 42 | 45 | 0.006799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2530-4_0_4_line_51 |  | 43 | 44 | 0.010813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2530-4_0_4_line_52 |  | 44 | 55 | 0.014236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2530-4_0_4_line_53 |  | 45 | 46 | 0.033107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2530-4_0_4_line_54 |  | 46 | 51 | 0.02657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2530-4_0_4_line_55 |  | 47 | 48 | 0.022911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2530-4_0_4_line_56 |  | 47 | 49 | 0.020543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2530-4_0_4_line_57 |  | 48 | 120 | 0.019332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2530-4_0_4_line_58 |  | 49 | 103 | 0.026523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2530-4_0_4_line_59 |  | 51 | 52 | 0.02049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2530-4_0_4_line_60 |  | 52 | 53 | 0.020757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2530-4_0_4_line_61 |  | 53 | 54 | 0.020808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2530-4_0_4_line_62 |  | 54 | 56 | 0.012156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2530-4_0_4_line_63 |  | 55 | 60 | 0.0084209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2530-4_0_4_line_64 |  | 56 | 57 | 0.037979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2530-4_0_4_line_65 |  | 57 | 58 | 0.047921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2530-4_0_4_line_66 |  | 58 | 59 | 0.011278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2530-4_0_4_line_67 |  | 59 | 73 | 0.019308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2530-4_0_4_line_68 |  | 60 | 122 | 0.023734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2530-4_0_4_line_69 |  | 61 | 62 | 0.017104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2530-4_0_4_line_70 |  | 61 | 63 | 0.0075487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2530-4_0_4_line_71 |  | 62 | 64 | 0.0032232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2530-4_0_4_line_72 |  | 63 | 65 | 0.014336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2530-4_0_4_line_73 |  | 64 | 66 | 0.011656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2530-4_0_4_line_74 |  | 65 | 67 | 0.005743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_2530-4_0_4_line_75 |  | 66 | 68 | 0.038371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2530-4_0_4_line_76 |  | 67 | 69 | 0.022569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_2530-4_0_4_line_77 |  | 69 | 70 | 0.017336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2530-4_0_4_line_78 |  | 70 | 71 | 0.030043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2530-4_0_4_line_79 |  | 71 | 76 | 0.012767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2530-4_0_4_line_80 |  | 73 | 74 | 0.00064969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2530-4_0_4_line_81 |  | 74 | 75 | 0.01789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2530-4_0_4_line_82 |  | 75 | 76 | 0.0089415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2530-4_0_4_line_83 |  | 77 | 78 | 0.023268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2530-4_0_4_line_84 |  | 78 | 79 | 0.017964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2530-4_0_4_line_85 |  | 80 | 135 | 0.0060722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2530-4_0_4_line_86 |  | 81 | 82 | 0.0040073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2530-4_0_4_line_87 |  | 81 | 83 | 0.012585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2530-4_0_4_line_88 |  | 82 | 84 | 0.028695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2530-4_0_4_line_89 |  | 83 | 85 | 0.0042114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2530-4_0_4_line_90 |  | 84 | 86 | 0.03316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2530-4_0_4_line_91 |  | 84 | 87 | 0.028888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2530-4_0_4_line_92 |  | 85 | 88 | 0.02489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2530-4_0_4_line_93 |  | 86 | 89 | 0.043489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2530-4_0_4_line_94 |  | 87 | 90 | 0.0090107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2530-4_0_4_line_95 |  | 88 | 91 | 0.027441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_2530-4_0_4_line_96 |  | 89 | 113 | 0.0066156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2530-4_0_4_line_97 |  | 90 | 111 | 0.0080546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2530-4_0_4_line_98 |  | 92 | 93 | 0.020298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2530-4_0_4_line_99 |  | 92 | 94 | 0.017317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2530-4_0_4_line_100 |  | 93 | 95 | 0.013416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2530-4_0_4_line_101 |  | 94 | 96 | 0.0078841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2530-4_0_4_line_102 |  | 94 | 97 | 0.040595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2530-4_0_4_line_103 |  | 95 | 98 | 0.035082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2530-4_0_4_line_104 |  | 97 | 99 | 0.015865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2530-4_0_4_line_105 |  | 98 | 100 | 0.0099739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2530-4_0_4_line_106 |  | 99 | 105 | 0.023479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2530-4_0_4_line_107 |  | 100 | 116 | 0.015684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2530-4_0_4_line_108 |  | 101 | 102 | 0.00358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2530-4_0_4_line_109 |  | 103 | 104 | 0.028681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2530-4_0_4_line_110 |  | 104 | 105 | 0.015274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2530-4_0_4_line_111 |  | 104 | 122 | 0.031562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2530-4_0_4_line_112 |  | 106 | 107 | 0.00092048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2530-4_0_4_line_113 |  | 107 | 108 | 0.016486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2530-4_0_4_line_114 |  | 108 | 109 | 0.023121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2530-4_0_4_line_115 |  | 108 | 110 | 0.005923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2530-4_0_4_line_116 |  | 109 | 111 | 0.030096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2530-4_0_4_line_117 |  | 109 | 112 | 0.0016337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2530-4_0_4_line_118 |  | 112 | 115 | 0.017693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2530-4_0_4_line_119 |  | 114 | 115 | 0.011383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2530-4_0_4_line_120 |  | 114 | 116 | 0.031281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2530-4_0_4_line_121 |  | 116 | 117 | 0.064894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2530-4_0_4_line_122 |  | 117 | 118 | 0.01097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2530-4_0_4_line_123 |  | 119 | 120 | 0.013015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2530-4_0_4_line_124 |  | 123 | 124 | 0.014471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2530-4_0_4_line_125 |  | 123 | 125 | 0.01524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2530-4_0_4_line_126 |  | 124 | 126 | 0.0034478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2530-4_0_4_line_127 |  | 127 | 136 | 0.021378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2530-4_0_4_line_128 |  | 128 | 129 | 0.0050176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2530-4_0_4_line_129 |  | 128 | 130 | 0.018128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2530-4_0_4_line_130 |  | 129 | 131 | 0.011074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2530-4_0_4_line_131 |  | 130 | 132 | 0.024733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2530-4_0_4_line_132 |  | 132 | 133 | 0.011837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2530-4_0_4_line_133 |  | 132 | 134 | 0.031477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2530-4_0_4_line_134 |  | 133 | 135 | 0.011682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2530-4_0_4_line_135 |  | 134 | 136 | 0.0081057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2530-4_0_4_trafo_1 | 0.63 MVA 20/0.4 kV | 137 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2611963.251 | 1223426.3452 | 2611937.4055 | 1223432.363
1 | 2611967.863 | 1223425.2714 | 2611963.251 | 1223426.3452
2 | 2611904.7383 | 1223432.0383 | 2611909.891 | 1223433.8608 | 2611913.7494 | 1223434.4466 | 2611921.1726 | 1223434.6059 | 2611927.0274 | 1223434.1284 | 2611936.5696 | 1223432.5576 | 2611937.4055 | 1223432.363
3 | 2611967.863 | 1223425.2714 | 2611969.5978 | 1223433.702 | 2611970.7518 | 1223437.3547
4 | 2611904.7383 | 1223432.0383 | 2611908.4443 | 1223425.4196
5 | 2611904.7383 | 1223432.0383 | 2611905.6985 | 1223441.1011 | 2611905.6011 | 1223444.3027 | 2611904.6391 | 1223460.0721
6 | 2611904.7383 | 1223432.0383 | 2611899.7356 | 1223434.8856 | 2611896.8063 | 1223436.0916 | 2611891.1695 | 1223437.5145 | 2611879.4616 | 1223439.1724
7 | 2611993.0975 | 1223456.0065 | 2611986.1028 | 1223453.9023 | 2611981.5033 | 1223452.3033 | 2611978.1017 | 1223450.7956 | 2611975.8004 | 1223448.901 | 2611973.6004 | 1223445.6058 | 2611971.9035 | 1223440.9997 | 2611970.7518 | 1223437.3547
8 | 2611908.4443 | 1223425.4196 | 2611891.3984 | 1223416.8733
9 | 2611908.4443 | 1223425.4196 | 2611911.4151 | 1223418.6105 | 2611916.7987 | 1223403.5013 | 2611918.8211 | 1223398.5982
10 | 2611904.6391 | 1223460.0721 | 2611904.198 | 1223467.3022 | 2611903.7667 | 1223477.8585
11 | 2611856.0027 | 1223442.4943 | 2611879.4616 | 1223439.1724
12 | 2612013.2588 | 1223418.8141 | 2612003.2191 | 1223420.2422
13 | 2612013.2588 | 1223418.8141 | 2612022.4207 | 1223417.7646
14 | 2612013.2588 | 1223418.8141 | 2612011.6808 | 1223411.6513 | 2612007.5938 | 1223402.8914
15 | 2611882.5763 | 1223410.102 | 2611886.2262 | 1223414.2801 | 2611891.3984 | 1223416.8733
16 | 2611918.8211 | 1223398.5982 | 2611922.902 | 1223388.7048 | 2611926.8471 | 1223379.9473
17 | 2611903.5293 | 1223488.7646 | 2611903.7038 | 1223479.3972 | 2611903.7667 | 1223477.8585
18 | 2611852.4564 | 1223442.9965 | 2611856.0027 | 1223442.4943
19 | 2612022.4207 | 1223417.7646 | 2612043.6906 | 1223415.3282
20 | 2612007.5938 | 1223402.8914 | 2612006.824 | 1223401.2414
21 | 2611987.5622 | 1223226.6907 | 2611990.2367 | 1223218.604
22 | 2611982.8032 | 1223250.0994 | 2611983.8016 | 1223240.0066 | 2611986.1019 | 1223231.106 | 2611987.5622 | 1223226.6907
23 | 2611982.8032 | 1223250.0994 | 2611982.9864 | 1223257.0593 | 2611984.2206 | 1223265.5334 | 2611985.7287 | 1223273.53 | 2611986.8158 | 1223279.7469 | 2611987.1483 | 1223284.1167 | 2611986.7956 | 1223289.8416
24 | 2611982.8032 | 1223250.0994 | 2611968.5843 | 1223247.0843
25 | 2611986.7956 | 1223289.8416 | 2611984.4583 | 1223294.5063 | 2611981.7046 | 1223298.8255 | 2611976.3389 | 1223305.7627
26 | 2611986.7956 | 1223289.8416 | 2611991.4644 | 1223290.9516 | 2611994.7602 | 1223292.3701 | 2611999.1604 | 1223295.0583 | 2612000.5445 | 1223296.0546
27 | 2611954.1452 | 1223241.5251 | 2611964.1191 | 1223246.1375 | 2611968.5843 | 1223247.0843
28 | 2611969.7411 | 1223314.293 | 2611976.3389 | 1223305.7627
29 | 2612015.4495 | 1223309.6773 | 2612004.2715 | 1223298.7374 | 2612000.5445 | 1223296.0546
30 | 2611954.1452 | 1223241.5251 | 2611950.308 | 1223239.7506 | 2611949.325 | 1223239.4881
31 | 2611969.7411 | 1223314.293 | 2611958.6004 | 1223328.6967 | 2611953.8542 | 1223335.0852
32 | 2612015.4495 | 1223309.6773 | 2612022.6026 | 1223319.8086 | 2612026.6129 | 1223327.8436 | 2612031.7439 | 1223340.4612
33 | 2612015.4495 | 1223309.6773 | 2612016.8998 | 1223308.7018 | 2612018.0989 | 1223308.2039 | 2612019.5023 | 1223307.9066 | 2612021.3981 | 1223307.8993 | 2612038.5381 | 1223308.2172
34 | 2611940.1977 | 1223237.0511 | 2611949.325 | 1223239.4881
35 | 2612031.7439 | 1223340.4612 | 2612033.9638 | 1223346.7539
36 | 2612031.7439 | 1223340.4612 | 2612034.2037 | 1223338.9987 | 2612035.7971 | 1223338.5016 | 2612039.4983 | 1223338.0977 | 2612043.0142 | 1223338.1581
37 | 2612038.5381 | 1223308.2172 | 2612062.0113 | 1223308.6527
38 | 2612033.9638 | 1223346.7539 | 2612037.1611 | 1223355.8172
39 | 2612043.0142 | 1223338.1581 | 2612068.9098 | 1223338.6028
40 | 2611942.198 | 1223351.7996 | 2611947.5984 | 1223343.5056 | 2611953.8542 | 1223335.0852
41 | 2612037.1611 | 1223355.8172 | 2612037.5722 | 1223356.9826 | 2612037.8811 | 1223357.773
42 | 2612074.7043 | 1223338.7023 | 2612068.9098 | 1223338.6028
43 | 2611880.7488 | 1223408.01 | 2611882.5763 | 1223410.102
44 | 2611928.4011 | 1223376.4976 | 2611926.8471 | 1223379.9473
45 | 2611903.5117 | 1223489.7108 | 2611903.5293 | 1223488.7646
46 | 2611852.4564 | 1223442.9965 | 2611832.0203 | 1223416.3601
47 | 2611852.4564 | 1223442.9965 | 2611836.8998 | 1223445.2003
48 | 2611655.0233 | 1223258.7019 | 2611654.4366 | 1223266.2493 | 2611654.3784 | 1223276.6663 | 2611654.9969 | 1223286.1286 | 2611656.3146 | 1223295.3373
49 | 2611666.6966 | 1223333.1899 | 2611663.8609 | 1223325.2575 | 2611660.566 | 1223315.601 | 2611658.0457 | 1223305.3679 | 2611656.3734 | 1223295.748 | 2611656.3146 | 1223295.3373
50 | 2611666.6966 | 1223333.1899 | 2611669.6875 | 1223339.2993
51 | 2611766.1592 | 1223369.755 | 2611775.309 | 1223363.9927
52 | 2611787.3549 | 1223356.4064 | 2611775.309 | 1223363.9927
53 | 2611669.6875 | 1223339.2993 | 2611673.1869 | 1223337.405 | 2611698.7956 | 1223323.5257
54 | 2611722.1553 | 1223310.8653 | 2611698.7956 | 1223323.5257
55 | 2611728.1431 | 1223440.1722 | 2611717.6886 | 1223419.7732
56 | 2611717.6886 | 1223419.7732 | 2611735.4254 | 1223409.4092
57 | 2611737.3379 | 1223457.189 | 2611728.1431 | 1223440.1722
58 | 2611758.3257 | 1223396.028 | 2611735.4254 | 1223409.4092
59 | 2611740.1696 | 1223301.1019 | 2611722.1553 | 1223310.8653
60 | 2611740.1696 | 1223301.1019 | 2611758.4189 | 1223291.2113
61 | 2611776.7131 | 1223281.2963 | 2611758.4189 | 1223291.2113
62 | 2611787.4006 | 1223275.5039 | 2611776.7131 | 1223281.2963
63 | 2611787.3549 | 1223356.4064 | 2611792.2584 | 1223363.2525
64 | 2611787.4006 | 1223275.5039 | 2611801.1741 | 1223266.3146 | 2611819.7638 | 1223255.6694
65 | 2611840.6929 | 1223298.7782 | 2611819.7638 | 1223255.6694
66 | 2611840.6929 | 1223298.7782 | 2611849.4365 | 1223305.9013
67 | 2611864.4061 | 1223318.0966 | 2611849.4365 | 1223305.9013
68 | 2611806.0784 | 1223382.5474 | 2611792.2584 | 1223363.2525
69 | 2611925.1155 | 1223338.1461 | 2611920.8034 | 1223334.5024 | 2611914.2995 | 1223329.5977 | 2611911.6351 | 1223327.6293
70 | 2611925.1155 | 1223338.1461 | 2611930.8814 | 1223343.0183
71 | 2611911.6351 | 1223327.6293 | 2611909.0427 | 1223325.7139
72 | 2611942.198 | 1223351.7996 | 2611936.2994 | 1223347.5965 | 2611930.8814 | 1223343.0183
73 | 2611899.6676 | 1223318.7874 | 2611909.0427 | 1223325.7139
74 | 2611942.198 | 1223351.7996 | 2611939.2106 | 1223356.7044
75 | 2611869.0972 | 1223295.5993 | 2611889.4036 | 1223311.2042 | 2611899.6676 | 1223318.7874
76 | 2611928.4011 | 1223376.4976 | 2611929.8025 | 1223373.3986 | 2611936.1042 | 1223361.8044 | 2611939.2106 | 1223356.7044
77 | 2611928.4011 | 1223376.4976 | 2611924.304 | 1223373.899 | 2611914.1781 | 1223366.5966
78 | 2611890.9078 | 1223347.6702 | 2611892.0734 | 1223349.0093 | 2611894.9346 | 1223351.6054 | 2611898.1295 | 1223354.1354 | 2611907.1005 | 1223361.502 | 2611913.9001 | 1223366.3961 | 2611914.1781 | 1223366.5966
79 | 2611884.0511 | 1223336.9242 | 2611888.4807 | 1223344.4106 | 2611890.1442 | 1223346.793 | 2611890.9078 | 1223347.6702
80 | 2611864.4061 | 1223318.0966 | 2611864.9098 | 1223318.507
81 | 2611864.9098 | 1223318.507 | 2611875.9873 | 1223327.5315 | 2611878.7867 | 1223329.7981
82 | 2611884.0511 | 1223336.9242 | 2611882.6917 | 1223334.6267 | 2611881.3541 | 1223332.3227 | 2611879.6213 | 1223330.4738 | 2611878.7867 | 1223329.7981
83 | 2612006.824 | 1223401.2414 | 2612004.4174 | 1223396.0832 | 2612000.7938 | 1223384.2579 | 2612000.0628 | 1223379.1016
84 | 2611997.5413 | 1223361.3158 | 2612000.0628 | 1223379.1016
85 | 2612049.7233 | 1223414.6371 | 2612043.6906 | 1223415.3282
86 | 2611904.3736 | 1223558.8117 | 2611904.4937 | 1223562.8173
87 | 2611904.3736 | 1223558.8117 | 2611904.3013 | 1223556.3988 | 2611903.9297 | 1223546.2349
88 | 2611905.3536 | 1223591.4991 | 2611904.4937 | 1223562.8173
89 | 2611903.9297 | 1223546.2349 | 2611903.7759 | 1223542.0262
90 | 2611905.3536 | 1223591.4991 | 2611938.6107 | 1223591.4764
91 | 2611878.302 | 1223597.7045 | 2611882.5639 | 1223593.6328 | 2611886.4414 | 1223592.173 | 2611905.3536 | 1223591.4991
92 | 2611903.1462 | 1223517.147 | 2611903.201 | 1223526.3013 | 2611903.7759 | 1223542.0262
93 | 2611938.6107 | 1223591.4764 | 2611937.4601 | 1223548.0023
94 | 2611878.302 | 1223597.7045 | 2611870.3686 | 1223593.432
95 | 2611903.5117 | 1223489.7108 | 2611903.3982 | 1223495.8061 | 2611903.0986 | 1223509.2022 | 2611903.1462 | 1223517.147
96 | 2611937.2851 | 1223541.389 | 2611937.4601 | 1223548.0023
97 | 2611863.277 | 1223589.6129 | 2611870.3686 | 1223593.432
98 | 2611785.6144 | 1223488.4971 | 2611772.526 | 1223504.0112
99 | 2611796.781 | 1223475.2608 | 2611785.6144 | 1223488.4971
100 | 2611761.9117 | 1223512.0581 | 2611765.199 | 1223510.0189 | 2611768.9267 | 1223507.6916 | 2611769.6031 | 1223506.9035 | 2611772.2013 | 1223504.3961 | 2611772.526 | 1223504.0112
101 | 2611796.781 | 1223475.2608 | 2611801.9368 | 1223469.2962
102 | 2611782.0589 | 1223438.8662 | 2611780.6136 | 1223445.0225 | 2611796.781 | 1223475.2608
103 | 2611770.4283 | 1223546.0724 | 2611768.1065 | 1223535.306 | 2611766.7314 | 1223528.9441 | 2611761.9117 | 1223512.0581
104 | 2611782.0589 | 1223438.8662 | 2611795.9963 | 1223431.2874
105 | 2611770.4283 | 1223546.0724 | 2611772.704 | 1223555.7832
106 | 2611787.0331 | 1223412.0986 | 2611798.0301 | 1223430.1815 | 2611795.9963 | 1223431.2874
107 | 2611776.2784 | 1223571.054 | 2611773.955 | 1223561.1214 | 2611772.704 | 1223555.7832
108 | 2611836.8998 | 1223445.2003 | 2611833.4266 | 1223446.0683
109 | 2611758.3257 | 1223396.028 | 2611771.8007 | 1223388.1499 | 2611779.0966 | 1223399.0483
110 | 2611779.0966 | 1223399.0483 | 2611787.0331 | 1223412.0986
111 | 2611779.0966 | 1223399.0483 | 2611806.0784 | 1223382.5474
112 | 2611852.0049 | 1223548.3122 | 2611852.2441 | 1223549.201
113 | 2611856.5289 | 1223565.1201 | 2611852.2441 | 1223549.201
114 | 2611856.5289 | 1223565.1201 | 2611841.7649 | 1223569.3155 | 2611836.7788 | 1223575.3425
115 | 2611856.5289 | 1223565.1201 | 2611862.2269 | 1223563.5032
116 | 2611836.7788 | 1223575.3425 | 2611863.277 | 1223589.6129
117 | 2611836.7788 | 1223575.3425 | 2611835.3399 | 1223574.5689
118 | 2611818.8066 | 1223568.4474 | 2611818.8066 | 1223568.4474 | 2611831.1131 | 1223572.2962 | 2611835.3399 | 1223574.5689
119 | 2611807.4238 | 1223568.4918 | 2611818.8066 | 1223568.4474
120 | 2611776.2784 | 1223571.054 | 2611780.8289 | 1223570.5627 | 2611784.4693 | 1223570.1696 | 2611791.1358 | 1223569.4601 | 2611799.8728 | 1223568.5212 | 2611807.4238 | 1223568.4918
121 | 2611776.2784 | 1223571.054 | 2611793.1908 | 1223633.7059
122 | 2611796.5415 | 1223644.1516 | 2611793.1908 | 1223633.7059
123 | 2611737.3379 | 1223457.189 | 2611742.7599 | 1223469.0208
124 | 2612074.7043 | 1223338.7023 | 2612076.2675 | 1223353.0889
125 | 2612074.7043 | 1223338.7023 | 2612089.9383 | 1223339.1299
126 | 2612076.6399 | 1223356.5166 | 2612076.2675 | 1223353.0889
127 | 2612047.0801 | 1223377.0348 | 2612045.9751 | 1223375.2323 | 2612043.2631 | 1223370.1461 | 2612039.8203 | 1223362.7349 | 2612037.8811 | 1223357.773
128 | 2612098.104 | 1223404.3412 | 2612099.4913 | 1223399.5192
129 | 2612092.1749 | 1223421.4079 | 2612094.6189 | 1223416.4544 | 2612098.104 | 1223404.3412
130 | 2612102.5532 | 1223388.8766 | 2612099.4913 | 1223399.5192
131 | 2612071.6603 | 1223407.9809 | 2612078.138 | 1223410.7512 | 2612082.8946 | 1223413.3845 | 2612086.9833 | 1223416.3501 | 2612092.1749 | 1223421.4079
132 | 2612071.6603 | 1223407.9809 | 2612068.6753 | 1223410.4208 | 2612066.557 | 1223411.7617 | 2612064.3258 | 1223412.68 | 2612061.3294 | 1223413.3076
133 | 2612071.6603 | 1223407.9809 | 2612064.1575 | 1223398.3713 | 2612057.2955 | 1223390.6641 | 2612053.1345 | 1223385.9419 | 2612051.5667 | 1223383.7783
134 | 2612049.7233 | 1223414.6371 | 2612061.3294 | 1223413.3076
135 | 2612051.5667 | 1223383.7783 | 2612049.278 | 1223380.6199 | 2612047.0801 | 1223377.0348

## bus_geodata
| x | y | coords
0 | 2611963.251 | 1223426.3452
1 | 2611937.4055 | 1223432.363
2 | 2611967.863 | 1223425.2714
3 | 2611904.7383 | 1223432.0383
4 | 2611970.7518 | 1223437.3547
5 | 2611908.4443 | 1223425.4196
6 | 2611904.6391 | 1223460.0721
7 | 2611879.4616 | 1223439.1724
8 | 2611993.0975 | 1223456.0065
9 | 2612003.2191 | 1223420.2422
10 | 2612013.2588 | 1223418.8142
11 | 2611891.3984 | 1223416.8733
12 | 2611918.8211 | 1223398.5982
13 | 2611903.7667 | 1223477.8585
14 | 2611856.0027 | 1223442.4943
15 | 2612022.4207 | 1223417.7646
16 | 2612007.5938 | 1223402.8914
17 | 2611987.5622 | 1223226.6907
18 | 2611990.2367 | 1223218.604
19 | 2611982.8032 | 1223250.0994
20 | 2611986.7956 | 1223289.8416
21 | 2611968.5843 | 1223247.0843
22 | 2611976.3389 | 1223305.7627
23 | 2612000.5445 | 1223296.0546
24 | 2611954.1452 | 1223241.5251
25 | 2611969.7411 | 1223314.293
26 | 2612015.4495 | 1223309.6773
27 | 2611949.325 | 1223239.4881
28 | 2612031.7439 | 1223340.4612
29 | 2612038.5381 | 1223308.2172
30 | 2612033.9638 | 1223346.7539
31 | 2612043.0142 | 1223338.1581
32 | 2612062.0113 | 1223308.6527
33 | 2611953.8542 | 1223335.0852
34 | 2612037.1611 | 1223355.8172
35 | 2612068.9098 | 1223338.6028
36 | 2611882.5763 | 1223410.102
37 | 2611926.8471 | 1223379.9473
38 | 2611903.5293 | 1223488.7646
39 | 2611852.4564 | 1223442.9965
40 | 2611655.0233 | 1223258.7019
41 | 2611656.3146 | 1223295.3373
42 | 2611666.6966 | 1223333.1899
43 | 2611766.1592 | 1223369.755
44 | 2611775.309 | 1223363.9927
45 | 2611669.6875 | 1223339.2993
46 | 2611698.7956 | 1223323.5257
47 | 2611717.6886 | 1223419.7732
48 | 2611728.1431 | 1223440.1722
49 | 2611735.4254 | 1223409.4092
50 | 2611940.1977 | 1223237.0511
51 | 2611722.1553 | 1223310.8653
52 | 2611740.1696 | 1223301.1019
53 | 2611758.4189 | 1223291.2113
54 | 2611776.7131 | 1223281.2963
55 | 2611787.3549 | 1223356.4064
56 | 2611787.4006 | 1223275.5039
57 | 2611819.7638 | 1223255.6694
58 | 2611840.6929 | 1223298.7782
59 | 2611849.4365 | 1223305.9013
60 | 2611792.2584 | 1223363.2525
61 | 2611925.1155 | 1223338.1461
62 | 2611911.6351 | 1223327.6293
63 | 2611930.8814 | 1223343.0183
64 | 2611909.0427 | 1223325.7139
65 | 2611942.198 | 1223351.7996
66 | 2611899.6676 | 1223318.7875
67 | 2611939.2106 | 1223356.7044
68 | 2611869.0972 | 1223295.5993
69 | 2611928.4011 | 1223376.4976
70 | 2611914.1781 | 1223366.5966
71 | 2611890.9078 | 1223347.6702
72 | 2611880.7488 | 1223408.01
73 | 2611864.4061 | 1223318.0966
74 | 2611864.9098 | 1223318.507
75 | 2611878.7867 | 1223329.7981
76 | 2611884.0511 | 1223336.9242
77 | 2612006.824 | 1223401.2414
78 | 2612000.0628 | 1223379.1016
79 | 2611997.5413 | 1223361.3158
80 | 2612043.6906 | 1223415.3282
81 | 2611904.3736 | 1223558.8117
82 | 2611904.4937 | 1223562.8173
83 | 2611903.9297 | 1223546.2349
84 | 2611905.3536 | 1223591.4991
85 | 2611903.7759 | 1223542.0262
86 | 2611938.6107 | 1223591.4764
87 | 2611878.302 | 1223597.7045
88 | 2611903.1462 | 1223517.147
89 | 2611937.4601 | 1223548.0023
90 | 2611870.3686 | 1223593.432
91 | 2611903.5117 | 1223489.7108
92 | 2611785.6144 | 1223488.4971
93 | 2611772.526 | 1223504.0112
94 | 2611796.781 | 1223475.2608
95 | 2611761.9117 | 1223512.0581
96 | 2611801.9368 | 1223469.2962
97 | 2611782.0589 | 1223438.8662
98 | 2611770.4283 | 1223546.0724
99 | 2611795.9963 | 1223431.2874
100 | 2611772.704 | 1223555.7832
101 | 2611833.4266 | 1223446.0683
102 | 2611836.8998 | 1223445.2003
103 | 2611758.3257 | 1223396.028
104 | 2611779.0966 | 1223399.0483
105 | 2611787.0331 | 1223412.0986
106 | 2611852.0049 | 1223548.3122
107 | 2611852.2441 | 1223549.201
108 | 2611856.5289 | 1223565.1201
109 | 2611836.7788 | 1223575.3425
110 | 2611862.2269 | 1223563.5032
111 | 2611863.277 | 1223589.6129
112 | 2611835.3399 | 1223574.5689
113 | 2611937.2851 | 1223541.389
114 | 2611807.4238 | 1223568.4918
115 | 2611818.8066 | 1223568.4474
116 | 2611776.2784 | 1223571.054
117 | 2611793.1908 | 1223633.7059
118 | 2611796.5415 | 1223644.1516
119 | 2611742.7599 | 1223469.0208
120 | 2611737.3379 | 1223457.189
121 | 2611832.0203 | 1223416.3601
122 | 2611806.0784 | 1223382.5474
123 | 2612074.7043 | 1223338.7023
124 | 2612076.2675 | 1223353.0889
125 | 2612089.9383 | 1223339.1299
126 | 2612076.6399 | 1223356.5166
127 | 2612037.8811 | 1223357.773
128 | 2612098.104 | 1223404.3412
129 | 2612099.4913 | 1223399.5192
130 | 2612092.1749 | 1223421.4079
131 | 2612102.5532 | 1223388.8766
132 | 2612071.6603 | 1223407.9809
133 | 2612061.3294 | 1223413.3076
134 | 2612051.5667 | 1223383.7783
135 | 2612049.7233 | 1223414.6371
136 | 2612047.0801 | 1223377.0348
137 | 2611967.863 | 1223425.2714

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99732 | -0.051538 | 0.050077 | 0.012551
1 | 1 | 0 | -0.50608 | -0.12854
2 | 0.99705 | -0.056606 | 0 | 0
3 | 0.99605 | -0.075099 | 0 | 0
4 | 0.99636 | -0.069928 | 0.058205 | 0.014587
5 | 0.99571 | -0.081483 | 0 | 0
6 | 0.99401 | -0.11415 | 0.09328 | 0.023378
7 | 0.99587 | -0.078536 | 0.00099148 | 0.00024849
8 | 0.99628 | -0.071506 | 0.0028457 | 0.0007132
9 | 0.97207 | -0.53873 | 0.0023005 | 0.00057655
10 | 0.97209 | -0.5383 | 0 | 0
11 | 0.99566 | -0.082486 | 0.00095966 | 0.00024051
12 | 0.99446 | -0.10525 | 0.0029801 | 0.0007469
13 | 0.99323 | -0.12918 | 0.03704 | 0.0092831
14 | 0.99573 | -0.08119 | 0.003267 | 0.0008188
15 | 0.97255 | -0.52926 | 0.0032739 | 0.00082053
16 | 0.97128 | -0.55426 | 0.0023908 | 0.00059919
17 | 0.98497 | -0.2872 | 0.010264 | 0.0025723
18 | 0.98496 | -0.28734 | 0.00090778 | 0.00022751
19 | 0.98521 | -0.28239 | 0 | 0
20 | 0.98574 | -0.27217 | 0 | 0
21 | 0.98517 | -0.28318 | 0.00070796 | 0.00017743
22 | 0.98756 | -0.23714 | 0.003902 | 0.00097795
23 | 0.98448 | -0.29633 | 0.0038017 | 0.00095279
24 | 0.98514 | -0.28382 | 0.00063888 | 0.00016012
25 | 0.98862 | -0.21667 | 0.003654 | 0.00091578
26 | 0.98289 | -0.3271 | 0 | 0
27 | 0.98513 | -0.28398 | 0.00063898 | 0.00016014
28 | 0.98031 | -0.37713 | 0 | 0
29 | 0.98278 | -0.32936 | 0.0024617 | 0.00061697
30 | 0.97987 | -0.3858 | 0.00081511 | 0.00020429
31 | 0.98023 | -0.37873 | 0.0018001 | 0.00045115
32 | 0.98271 | -0.33058 | 0.0028806 | 0.00072194
33 | 0.9913 | -0.16549 | 0.0012895 | 0.00032319
34 | 0.97923 | -0.39815 | 0.0010289 | 0.00025785
35 | 0.98009 | -0.38141 | 0.0015441 | 0.00038699
36 | 0.99564 | -0.082891 | 0.00075505 | 0.00018923
37 | 0.9936 | -0.1217 | 0.0012509 | 0.0003135
38 | 0.99287 | -0.13602 | 0.00070373 | 0.00017637
39 | 0.99572 | -0.081385 | 0 | 0
40 | 0.99084 | -0.17513 | 0.0003494 | 8.7568e-05
41 | 0.99085 | -0.1749 | 0.00069538 | 0.00017428
42 | 0.99089 | -0.17417 | 0 | 0
43 | 0.97159 | -0.54902 | 0.0038636 | 0.00096832
44 | 0.97163 | -0.54825 | 0.0045391 | 0.0011376
45 | 0.99089 | -0.17404 | 0 | 0
46 | 0.99092 | -0.17343 | 0.0043799 | 0.0010977
47 | 0.9714 | -0.55271 | 0 | 0
48 | 0.97121 | -0.55648 | 0.0025781 | 0.00064613
49 | 0.97157 | -0.54933 | 0.0068016 | 0.0017046
50 | 0.98512 | -0.28415 | 0.0010322 | 0.0002587
51 | 0.99106 | -0.17087 | 0.00029947 | 7.5054e-05
52 | 0.99116 | -0.16878 | 0.0012992 | 0.0003256
53 | 0.9913 | -0.16619 | 0.0010921 | 0.00027369
54 | 0.99145 | -0.1632 | 0.0010135 | 0.00025401
55 | 0.97174 | -0.54604 | 0 | 0
56 | 0.99155 | -0.16123 | 0 | 0
57 | 0.99187 | -0.15508 | 0.00018833 | 4.72e-05
58 | 0.99228 | -0.14716 | 0.0003048 | 7.6389e-05
59 | 0.99238 | -0.14524 | 0.00013185 | 3.3044e-05
60 | 0.9718 | -0.54473 | 0.0027743 | 0.00069532
61 | 0.99214 | -0.14961 | 0.0040892 | 0.0010249
62 | 0.99205 | -0.15125 | 0.0034864 | 0.00087377
63 | 0.9922 | -0.14834 | 0.0020584 | 0.00051588
64 | 0.99204 | -0.15136 | 0.0006765 | 0.00016955
65 | 0.99235 | -0.1454 | 0 | 0
66 | 0.99203 | -0.15162 | 0.0010929 | 0.00027392
67 | 0.99257 | -0.14124 | 0.0012181 | 0.00030528
68 | 0.99203 | -0.15174 | 0.00016779 | 4.2051e-05
69 | 0.99344 | -0.12474 | 0 | 0
70 | 0.99324 | -0.12857 | 0.001568 | 0.00039298
71 | 0.99294 | -0.13436 | 0.00014963 | 3.75e-05
72 | 0.99564 | -0.082953 | 0.0012756 | 0.0003197
73 | 0.99255 | -0.1419 | 0.00053611 | 0.00013436
74 | 0.99256 | -0.14179 | 0.00015934 | 3.9934e-05
75 | 0.99273 | -0.13848 | 0.00017587 | 4.4078e-05
76 | 0.99281 | -0.13679 | 0.00013123 | 3.289e-05
77 | 0.9712 | -0.55589 | 0.044305 | 0.011104
78 | 0.97111 | -0.55768 | 0.0023266 | 0.0005831
79 | 0.97108 | -0.55829 | 0.0018323 | 0.00045921
80 | 0.97367 | -0.50703 | 0.001399 | 0.00035062
81 | 0.98906 | -0.20886 | 0.0033459 | 0.00083856
82 | 0.98881 | -0.21368 | 0.0011819 | 0.00029622
83 | 0.98989 | -0.193 | 0.0012618 | 0.00031624
84 | 0.98704 | -0.24764 | 0 | 0
85 | 0.99017 | -0.1876 | 0.0016458 | 0.00041248
86 | 0.98687 | -0.25088 | 0 | 0
87 | 0.98541 | -0.27911 | 0 | 0
88 | 0.99187 | -0.15505 | 0.0022049 | 0.00055259
89 | 0.98666 | -0.25513 | 0.0012441 | 0.0003118
90 | 0.9849 | -0.28895 | 0.00071284 | 0.00017865
91 | 0.99284 | -0.13661 | 0.029773 | 0.0074619
92 | 0.97613 | -0.45959 | 0.00072197 | 0.00018094
93 | 0.97689 | -0.4447 | 0.0035387 | 0.00088688
94 | 0.97549 | -0.47208 | 0 | 0
95 | 0.97743 | -0.434 | 0 | 0
96 | 0.97548 | -0.47233 | 0.00174 | 0.00043608
97 | 0.97406 | -0.50013 | 0 | 0
98 | 0.97886 | -0.40609 | 0 | 0
99 | 0.97351 | -0.51112 | 0.0037848 | 0.00094855
100 | 0.97927 | -0.39817 | 0.00082338 | 0.00020636
101 | 0.99571 | -0.081538 | 0.00045132 | 0.00011311
102 | 0.99572 | -0.08151 | 0 | 0
103 | 0.97196 | -0.54164 | 0 | 0
104 | 0.97238 | -0.53333 | 0 | 0
105 | 0.97276 | -0.52576 | 0.0069955 | 0.0017532
106 | 0.98257 | -0.33407 | 0.0042254 | 0.001059
107 | 0.98257 | -0.334 | 0.0011254 | 0.00028206
108 | 0.98265 | -0.33241 | 0 | 0
109 | 0.98279 | -0.3298 | 0 | 0
110 | 0.98265 | -0.3325 | 0.00089505 | 0.00022432
111 | 0.98445 | -0.29765 | 0.00079461 | 0.00019915
112 | 0.9827 | -0.33137 | 0.0022996 | 0.00057633
113 | 0.98663 | -0.25563 | 0.0042172 | 0.0010569
114 | 0.98133 | -0.35794 | 0.0017203 | 0.00043114
115 | 0.98187 | -0.34759 | 0.000441 | 0.00011053
116 | 0.97992 | -0.38549 | 0 | 0
117 | 0.97967 | -0.3903 | 0.0019988 | 0.00050095
118 | 0.97965 | -0.39071 | 0.0020819 | 0.00052179
119 | 0.97102 | -0.56026 | 0.0063269 | 0.0015857
120 | 0.9711 | -0.55874 | 0 | 0
121 | 0.99564 | -0.082951 | 0.0026518 | 0.00066462
122 | 0.97205 | -0.53984 | 0 | 0
123 | 0.98007 | -0.38184 | 0 | 0
124 | 0.98003 | -0.38262 | 0.0015132 | 0.00037925
125 | 0.98006 | -0.38217 | 0.0011731 | 0.000294
126 | 0.98003 | -0.38272 | 0.0014612 | 0.00036621
127 | 0.9791 | -0.40079 | 0.001169 | 0.00029299
128 | 0.97513 | -0.47846 | 0.0008193 | 0.00020534
129 | 0.97511 | -0.47881 | 0.0021792 | 0.00054615
130 | 0.9752 | -0.47694 | 0 | 0
131 | 0.97509 | -0.47913 | 0.0015924 | 0.00039908
132 | 0.97531 | -0.47485 | 0 | 0
133 | 0.97464 | -0.48798 | 0.0017925 | 0.00044924
134 | 0.97722 | -0.43739 | 0.0019606 | 0.00049136
135 | 0.974 | -0.50057 | 0.00086656 | 0.00021718
136 | 0.97773 | -0.42748 | 0.0015119 | 0.00037892
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.11118 | -0.027885 | 0.11146 | 0.02806 | 0.00027386 | 0.00017492 | 0.16589 | 0.16589 | 0.16589 | 0.99732 | -0.051538 | 1 | 0 | 45.5747
1 | 0.061104 | 0.015334 | -0.061089 | -0.015325 | 1.4762e-05 | 9.3859e-06 | 0.091176 | 0.091176 | 0.091176 | 0.99732 | -0.051538 | 0.99705 | -0.056606 | 25.0483
2 | 0.39297 | 0.10048 | -0.39155 | -0.099572 | 0.0014223 | 0.00090895 | 0.58545 | 0.58546 | 0.58546 | 1 | 0 | 0.99605 | -0.075099 | 53.6131
3 | 0.061089 | 0.015325 | -0.061051 | -0.0153 | 3.8774e-05 | 2.4653e-05 | 0.091176 | 0.091176 | 0.091176 | 0.99705 | -0.056606 | 0.99636 | -0.069928 | 25.0483
4 | 0.14585 | 0.037362 | -0.1458 | -0.037333 | 4.5106e-05 | 2.8572e-05 | 0.21817 | 0.21817 | 0.21817 | 0.99605 | -0.075099 | 0.99571 | -0.081483 | 19.9791
5 | 0.23834 | 0.060365 | -0.23789 | -0.060081 | 0.00044611 | 0.00028442 | 0.35628 | 0.35628 | 0.35628 | 0.99605 | -0.075099 | 0.99401 | -0.11415 | 32.6267
6 | 0.0073639 | 0.0018451 | -0.0073627 | -0.0018446 | 1.2055e-06 | 4.2584e-07 | 0.011001 | 0.011001 | 0.011001 | 0.99605 | -0.075099 | 0.99587 | -0.078536 | 3.0223
7 | 0.0028459 | 0.00071293 | -0.0028457 | -0.0007132 | 2.1385e-07 | -2.7426e-07 | 0.0042501 | 0.0042503 | 0.0042503 | 0.99636 | -0.069928 | 0.99628 | -0.071506 | 1.1677
8 | 0.0029905 | 0.00074914 | -0.0029904 | -0.0007493 | 1.4282e-07 | -1.5661e-07 | 0.004469 | 0.0044691 | 0.0044691 | 0.99571 | -0.081483 | 0.99566 | -0.082486 | 1.2278
9 | 0.14281 | 0.036584 | -0.14265 | -0.03648 | 0.00016425 | 0.000104 | 0.2137 | 0.2137 | 0.2137 | 0.99571 | -0.081483 | 0.99446 | -0.10525 | 19.5699
10 | 0.14461 | 0.036703 | -0.14451 | -0.036636 | 0.00010448 | 6.6177e-05 | 0.21665 | 0.21665 | 0.21665 | 0.99401 | -0.11415 | 0.99323 | -0.12918 | 19.8394
11 | 0.0063712 | 0.0015961 | -0.0063704 | -0.0015959 | 8.0518e-07 | 2.0708e-07 | 0.0095196 | 0.0095197 | 0.0095197 | 0.99587 | -0.078536 | 0.99573 | -0.08119 | 2.6153
12 | -0.0023005 | -0.00057655 | 0.0023005 | 0.00057645 | 4.7157e-08 | -9.5532e-08 | 0.0035215 | 0.0035214 | 0.0035215 | 0.97207 | -0.53873 | 0.97209 | -0.5383 | 0.96744
13 | -0.053198 | -0.013349 | 0.053221 | 0.013363 | 2.2935e-05 | 1.4564e-05 | 0.081438 | 0.081438 | 0.081438 | 0.97209 | -0.5383 | 0.97255 | -0.52926 | 22.3732
14 | 0.050898 | 0.012772 | -0.050859 | -0.012748 | 3.8705e-05 | 2.4561e-05 | 0.077917 | 0.077917 | 0.077917 | 0.97209 | -0.5383 | 0.97128 | -0.55426 | 21.4058
15 | 0.0020307 | 0.00050878 | -0.0020307 | -0.0005089 | 3.9146e-08 | -1.2234e-07 | 0.0030349 | 0.0030349 | 0.0030349 | 0.99566 | -0.082486 | 0.99564 | -0.082891 | 0.83377
16 | 0.13967 | 0.035733 | -0.13956 | -0.035663 | 0.00011114 | 7.0339e-05 | 0.20924 | 0.20924 | 0.20924 | 0.99446 | -0.10525 | 0.9936 | -0.1217 | 19.1616
17 | 0.10747 | 0.027353 | -0.10743 | -0.027331 | 3.5414e-05 | 2.2242e-05 | 0.16115 | 0.16115 | 0.16115 | 0.99323 | -0.12918 | 0.99287 | -0.13602 | 14.7578
18 | 0.0031034 | 0.00077714 | -0.0031034 | -0.00077717 | 2.8886e-08 | -2.8102e-08 | 0.0046375 | 0.0046375 | 0.0046375 | 0.99573 | -0.08119 | 0.99572 | -0.081385 | 1.274
19 | -0.056495 | -0.014184 | 0.056555 | 0.014222 | 5.9997e-05 | 3.8132e-05 | 0.086448 | 0.086447 | 0.086448 | 0.97255 | -0.52926 | 0.97367 | -0.50703 | 23.7493
20 | 0.048468 | 0.012148 | -0.048464 | -0.012146 | 3.7646e-06 | 2.3868e-06 | 0.074254 | 0.074254 | 0.074254 | 0.97128 | -0.55426 | 0.9712 | -0.55589 | 20.3995
21 | 0.00090778 | 0.00022741 | -0.00090778 | -0.00022751 | 6.0071e-09 | -1.0456e-07 | 0.0013714 | 0.0013714 | 0.0013714 | 0.98497 | -0.2872 | 0.98496 | -0.28734 | 0.37676
22 | -0.011171 | -0.0027997 | 0.011174 | 0.002801 | 2.5619e-06 | 1.3343e-06 | 0.016877 | 0.016877 | 0.016877 | 0.98497 | -0.2872 | 0.98521 | -0.28239 | 4.6365
23 | -0.014192 | -0.003557 | 0.014199 | 0.0035609 | 6.9088e-06 | 3.9108e-06 | 0.021435 | 0.021435 | 0.021435 | 0.98521 | -0.28239 | 0.98574 | -0.27217 | 5.8888
24 | 0.0030183 | 0.00075596 | -0.0030181 | -0.00075607 | 1.1326e-07 | -1.126e-07 | 0.0045585 | 0.0045585 | 0.0045585 | 0.98521 | -0.28239 | 0.98517 | -0.28318 | 1.2523
25 | -0.10336 | -0.026275 | 0.10353 | 0.026386 | 0.00017475 | 0.0001116 | 0.15616 | 0.15616 | 0.15616 | 0.98574 | -0.27217 | 0.98756 | -0.23714 | 42.9006
26 | 0.08916 | 0.022714 | -0.089056 | -0.022648 | 0.00010379 | 6.6231e-05 | 0.13472 | 0.13472 | 0.13472 | 0.98574 | -0.27217 | 0.98448 | -0.29633 | 37.0119
27 | 0.0023102 | 0.00057864 | -0.0023101 | -0.00057879 | 7.101e-08 | -1.5259e-07 | 0.0034892 | 0.0034893 | 0.0034893 | 0.98517 | -0.28318 | 0.98514 | -0.28382 | 0.95859
28 | -0.10744 | -0.027364 | 0.10754 | 0.027432 | 0.00010618 | 6.7817e-05 | 0.16204 | 0.16204 | 0.16204 | 0.98756 | -0.23714 | 0.98862 | -0.21667 | 44.5158
29 | 0.085255 | 0.021695 | -0.085128 | -0.021614 | 0.00012622 | 8.0522e-05 | 0.12898 | 0.12898 | 0.12898 | 0.98448 | -0.29633 | 0.98289 | -0.3271 | 35.4334
30 | 0.0016712 | 0.00041867 | -0.0016712 | -0.00041873 | 1.2533e-08 | -5.876e-08 | 0.0025243 | 0.0025243 | 0.0025243 | 0.98514 | -0.28382 | 0.98513 | -0.28398 | 0.69349
31 | -0.1112 | -0.028348 | 0.11147 | 0.028524 | 0.00027544 | 0.00017594 | 0.16754 | 0.16754 | 0.16754 | 0.98862 | -0.21667 | 0.9913 | -0.16549 | 46.0267
32 | 0.079785 | 0.020276 | -0.079594 | -0.020153 | 0.00019172 | 0.00012226 | 0.12089 | 0.12089 | 0.12089 | 0.98289 | -0.3271 | 0.98031 | -0.37713 | 33.2112
33 | 0.0053431 | 0.0013388 | -0.0053425 | -0.0013387 | 5.7708e-07 | 7.1277e-08 | 0.0080889 | 0.008089 | 0.008089 | 0.98289 | -0.3271 | 0.98278 | -0.32936 | 2.2222
34 | 0.0010323 | 0.00025859 | -0.0010322 | -0.0002587 | 8.6122e-09 | -1.1477e-07 | 0.0015591 | 0.0015592 | 0.0015592 | 0.98513 | -0.28398 | 0.98512 | -0.28415 | 0.42835
35 | 0.0721 | 0.018276 | -0.07207 | -0.018257 | 3.0011e-05 | 1.9123e-05 | 0.10951 | 0.10952 | 0.10952 | 0.98031 | -0.37713 | 0.97987 | -0.3858 | 30.0865
36 | 0.0074933 | 0.0018776 | -0.0074927 | -0.0018774 | 5.7101e-07 | 2.1706e-07 | 0.011374 | 0.011374 | 0.011374 | 0.98031 | -0.37713 | 0.98023 | -0.37873 | 3.1247
37 | 0.0028807 | 0.00072175 | -0.0028806 | -0.00072194 | 1.6749e-07 | -1.9027e-07 | 0.0043616 | 0.0043617 | 0.0043617 | 0.98278 | -0.32936 | 0.98271 | -0.33058 | 1.1983
38 | 0.071255 | 0.018052 | -0.071213 | -0.018025 | 4.2253e-05 | 2.6921e-05 | 0.10828 | 0.10828 | 0.10828 | 0.97987 | -0.3858 | 0.97923 | -0.39815 | 29.7465
39 | 0.0056926 | 0.0014262 | -0.0056919 | -0.0014261 | 7.2525e-07 | 1.3773e-07 | 0.0086413 | 0.0086415 | 0.0086415 | 0.98023 | -0.37873 | 0.98009 | -0.38141 | 2.374
40 | -0.11276 | -0.028847 | 0.11287 | 0.028917 | 0.00010979 | 6.9738e-05 | 0.16947 | 0.16947 | 0.16947 | 0.9913 | -0.16549 | 0.99235 | -0.1454 | 23.2792
41 | 0.070184 | 0.017768 | -0.070175 | -0.017762 | 8.9014e-06 | 5.6707e-06 | 0.10671 | 0.10671 | 0.10671 | 0.97923 | -0.39815 | 0.9791 | -0.40079 | 29.317
42 | 0.0041477 | 0.0010391 | -0.0041477 | -0.0010391 | 8.6179e-08 | -1.7879e-08 | 0.0062971 | 0.0062971 | 0.0062971 | 0.98009 | -0.38141 | 0.98007 | -0.38184 | 1.73
43 | 0.0012756 | 0.00031967 | -0.0012756 | -0.0003197 | 3.7862e-09 | -3.3703e-08 | 0.0019065 | 0.0019065 | 0.0019065 | 0.99564 | -0.082891 | 0.99564 | -0.082953 | 0.52376
44 | 0.1383 | 0.03535 | -0.13828 | -0.035337 | 2.0338e-05 | 1.2869e-05 | 0.20737 | 0.20737 | 0.20737 | 0.9936 | -0.1217 | 0.99344 | -0.12474 | 18.99
45 | 0.10673 | 0.027155 | -0.10673 | -0.027153 | 3.0322e-06 | 1.9039e-06 | 0.1601 | 0.1601 | 0.1601 | 0.99287 | -0.13602 | 0.99284 | -0.13661 | 14.6612
46 | 0.002652 | 0.0006643 | -0.0026518 | -0.00066462 | 1.9775e-07 | -3.101e-07 | 0.0039631 | 0.0039633 | 0.0039633 | 0.99572 | -0.081385 | 0.99564 | -0.082951 | 1.0888
47 | 0.00045132 | 0.00011286 | -0.00045132 | -0.00011306 | 2.6721e-09 | -2.0207e-07 | 0.00067437 | 0.00067444 | 0.00067444 | 0.99572 | -0.081385 | 0.99572 | -0.08151 | 0.18529
48 | -0.0003494 | -8.7568e-05 | 0.00034941 | 8.7097e-05 | 3.7956e-09 | -4.712e-07 | 0.00052472 | 0.00052456 | 0.00052472 | 0.99084 | -0.17513 | 0.99085 | -0.1749 | 0.14415
49 | -0.0010448 | -0.00026137 | 0.0010448 | 0.00026089 | 3.6311e-08 | -4.8356e-07 | 0.0015688 | 0.0015687 | 0.0015688 | 0.99085 | -0.1749 | 0.99089 | -0.17417 | 0.431
50 | -0.0010448 | -0.00026089 | 0.0010448 | 0.00026081 | 6.2738e-09 | -8.3565e-08 | 0.0015687 | 0.0015686 | 0.0015687 | 0.99089 | -0.17417 | 0.99089 | -0.17404 | 0.43095
51 | -0.0038636 | -0.00096832 | 0.0038638 | 0.00096827 | 1.4198e-07 | -4.3053e-08 | 0.0059173 | 0.0059172 | 0.0059173 | 0.97159 | -0.54902 | 0.97163 | -0.54825 | 1.6256
52 | -0.0084029 | -0.0021059 | 0.0084038 | 0.0021063 | 8.8406e-07 | 3.8946e-07 | 0.012869 | 0.012869 | 0.012869 | 0.97163 | -0.54825 | 0.97174 | -0.54604 | 3.5354
53 | -0.0010448 | -0.00026081 | 0.0010449 | 0.0002604 | 3.0546e-08 | -4.0693e-07 | 0.0015686 | 0.0015685 | 0.0015686 | 0.99089 | -0.17404 | 0.99092 | -0.17343 | 0.43094
54 | -0.0054248 | -0.0013581 | 0.0054255 | 0.0013582 | 6.6109e-07 | 8.0771e-08 | 0.0081456 | 0.0081455 | 0.0081456 | 0.99092 | -0.17343 | 0.99106 | -0.17087 | 2.2378
55 | 0.0089077 | 0.0022329 | -0.0089061 | -0.0022321 | 1.5997e-06 | 7.4023e-07 | 0.013645 | 0.013645 | 0.013645 | 0.9714 | -0.55271 | 0.97121 | -0.55648 | 3.7487
56 | -0.0089077 | -0.0022329 | 0.0089091 | 0.0022335 | 1.4343e-06 | 6.6361e-07 | 0.013645 | 0.013645 | 0.013645 | 0.9714 | -0.55271 | 0.97157 | -0.54933 | 3.7487
57 | 0.006328 | 0.001586 | -0.0063273 | -0.0015858 | 6.8145e-07 | 1.9693e-07 | 0.0096953 | 0.0096954 | 0.0096954 | 0.97121 | -0.55648 | 0.9711 | -0.55874 | 2.6636
58 | -0.015711 | -0.0039382 | 0.015716 | 0.0039415 | 5.7587e-06 | 3.357e-06 | 0.024062 | 0.024062 | 0.024062 | 0.97157 | -0.54933 | 0.97196 | -0.54164 | 6.6105
59 | -0.0057249 | -0.0014333 | 0.0057255 | 0.0014333 | 5.6764e-07 | 9.9232e-08 | 0.0085951 | 0.008595 | 0.0085951 | 0.99106 | -0.17087 | 0.99116 | -0.16878 | 2.3613
60 | -0.0070247 | -0.001759 | 0.0070255 | 0.0017592 | 8.6562e-07 | 2.8643e-07 | 0.010545 | 0.010545 | 0.010545 | 0.99116 | -0.16878 | 0.9913 | -0.16619 | 2.8971
61 | -0.0081176 | -0.0020329 | 0.0081187 | 0.0020334 | 1.1585e-06 | 4.7312e-07 | 0.012185 | 0.012185 | 0.012185 | 0.9913 | -0.16619 | 0.99145 | -0.1632 | 3.3474
62 | -0.0091322 | -0.0022874 | 0.0091331 | 0.0022878 | 8.563e-07 | 3.9125e-07 | 0.013706 | 0.013706 | 0.013706 | 0.99145 | -0.1632 | 0.99155 | -0.16123 | 3.7653
63 | -0.0084038 | -0.0021063 | 0.0084043 | 0.0021065 | 5.2295e-07 | 2.3036e-07 | 0.012869 | 0.012869 | 0.012869 | 0.97174 | -0.54604 | 0.9718 | -0.54473 | 3.5354
64 | -0.0091331 | -0.0022878 | 0.0091358 | 0.002289 | 2.6753e-06 | 1.2221e-06 | 0.013706 | 0.013705 | 0.013706 | 0.99155 | -0.16123 | 0.99187 | -0.15508 | 3.7653
65 | -0.0093241 | -0.0023362 | 0.0093276 | 0.0023379 | 3.516e-06 | 1.6315e-06 | 0.013988 | 0.013988 | 0.013988 | 0.99187 | -0.15508 | 0.99228 | -0.14716 | 3.8428
66 | -0.0096324 | -0.0024142 | 0.0096333 | 0.0024147 | 8.8242e-07 | 4.1906e-07 | 0.014445 | 0.014445 | 0.014445 | 0.99228 | -0.14716 | 0.99238 | -0.14524 | 3.9683
67 | -0.0097651 | -0.0024477 | 0.0097667 | 0.0024485 | 1.5524e-06 | 7.4402e-07 | 0.014642 | 0.014642 | 0.014642 | 0.99238 | -0.14524 | 0.99255 | -0.1419 | 4.0226
68 | -0.011179 | -0.0028018 | 0.011181 | 0.0028032 | 2.6076e-06 | 1.3747e-06 | 0.017117 | 0.017117 | 0.017117 | 0.9718 | -0.54473 | 0.97205 | -0.53984 | 4.7024
69 | 0.0054241 | 0.0013587 | -0.0054236 | -0.0013586 | 4.2445e-07 | 5.0792e-08 | 0.0081348 | 0.0081349 | 0.0081349 | 0.99214 | -0.14961 | 0.99205 | -0.15125 | 2.2349
70 | -0.0095133 | -0.0023835 | 0.0095139 | 0.0023838 | 5.7627e-07 | 2.7132e-07 | 0.014268 | 0.014268 | 0.014268 | 0.99214 | -0.14961 | 0.9922 | -0.14834 | 3.9198
71 | 0.0019373 | 0.00048485 | -0.0019372 | -0.00048488 | 1.0204e-08 | -3.5086e-08 | 0.0029055 | 0.0029055 | 0.0029055 | 0.99205 | -0.15125 | 0.99204 | -0.15136 | 0.79823
72 | -0.011572 | -0.0028997 | 0.011574 | 0.0029005 | 1.6192e-06 | 8.5112e-07 | 0.017355 | 0.017355 | 0.017355 | 0.9922 | -0.14834 | 0.99235 | -0.1454 | 4.7678
73 | 0.0012607 | 0.00031533 | -0.0012607 | -0.00031547 | 1.5628e-08 | -1.4049e-07 | 0.0018908 | 0.0018909 | 0.0018909 | 0.99204 | -0.15136 | 0.99203 | -0.15162 | 0.51947
74 | -0.12444 | -0.031817 | 0.12447 | 0.031833 | 2.5057e-05 | 1.5814e-05 | 0.18683 | 0.18683 | 0.18683 | 0.99235 | -0.1454 | 0.99257 | -0.14124 | 17.1087
75 | 0.00016779 | 4.1556e-05 | -0.00016779 | -4.2051e-05 | 9.1079e-10 | -4.9483e-07 | 0.0002515 | 0.00025168 | 0.00025168 | 0.99203 | -0.15162 | 0.99203 | -0.15174 | 0.069142
76 | -0.12569 | -0.032138 | 0.12579 | 0.032202 | 0.0001004 | 6.3382e-05 | 0.18865 | 0.18865 | 0.18865 | 0.99257 | -0.14124 | 0.99344 | -0.12474 | 17.2759
77 | 0.012496 | 0.0031349 | -0.012494 | -0.0031337 | 2.2778e-06 | 1.2333e-06 | 0.018718 | 0.018718 | 0.018718 | 0.99344 | -0.12474 | 0.99324 | -0.12857 | 5.1424
78 | 0.010926 | 0.0027407 | -0.010923 | -0.0027391 | 3.0187e-06 | 1.5433e-06 | 0.016369 | 0.016369 | 0.016369 | 0.99324 | -0.12857 | 0.99294 | -0.13436 | 4.4971
79 | 0.010773 | 0.0027016 | -0.010772 | -0.002701 | 1.248e-06 | 6.336e-07 | 0.016145 | 0.016145 | 0.016145 | 0.99294 | -0.13436 | 0.99281 | -0.13679 | 4.4355
80 | -0.010303 | -0.0025828 | 0.010303 | 0.0025828 | 5.8126e-08 | 2.8804e-08 | 0.015446 | 0.015446 | 0.015446 | 0.99255 | -0.1419 | 0.99256 | -0.14179 | 4.2434
81 | -0.010462 | -0.0026228 | 0.010464 | 0.0026236 | 1.6505e-06 | 8.2504e-07 | 0.015685 | 0.015685 | 0.015685 | 0.99256 | -0.14179 | 0.99273 | -0.13848 | 4.309
82 | -0.01064 | -0.0026677 | 0.010641 | 0.0026681 | 8.5286e-07 | 4.3021e-07 | 0.015948 | 0.015948 | 0.015948 | 0.99273 | -0.13848 | 0.99281 | -0.13679 | 4.3814
83 | 0.0041593 | 0.0010421 | -0.0041589 | -0.0010421 | 3.5433e-07 | -6.113e-08 | 0.0063725 | 0.0063726 | 0.0063726 | 0.9712 | -0.55589 | 0.97111 | -0.55768 | 1.7507
84 | 0.0018323 | 0.00045902 | -0.0018323 | -0.00045921 | 5.31e-08 | -1.8826e-07 | 0.0028076 | 0.0028076 | 0.0028076 | 0.97111 | -0.55768 | 0.97108 | -0.55829 | 0.77133
85 | -0.057954 | -0.014572 | 0.057972 | 0.014584 | 1.7869e-05 | 1.1361e-05 | 0.088585 | 0.088585 | 0.088585 | 0.97367 | -0.50703 | 0.974 | -0.50057 | 24.3367
86 | 0.068235 | 0.017406 | -0.068219 | -0.017396 | 1.5871e-05 | 1.0106e-05 | 0.10277 | 0.10277 | 0.10277 | 0.98906 | -0.20886 | 0.98881 | -0.21368 | 28.2326
87 | -0.071581 | -0.018245 | 0.071636 | 0.018279 | 5.4842e-05 | 3.4937e-05 | 0.1078 | 0.1078 | 0.1078 | 0.98906 | -0.20886 | 0.98989 | -0.193 | 29.6155
88 | 0.067037 | 0.0171 | -0.066927 | -0.01703 | 0.00010974 | 6.9868e-05 | 0.10099 | 0.10099 | 0.10099 | 0.98881 | -0.21368 | 0.98704 | -0.24764 | 27.744
89 | -0.072897 | -0.018596 | 0.072916 | 0.018608 | 1.9004e-05 | 1.2109e-05 | 0.1097 | 0.1097 | 0.1097 | 0.98989 | -0.193 | 0.99017 | -0.1876 | 30.1366
90 | 0.0054633 | 0.001369 | -0.0054625 | -0.0013689 | 8.4353e-07 | 1.161e-07 | 0.0082361 | 0.0082363 | 0.0082363 | 0.98704 | -0.24764 | 0.98687 | -0.25088 | 2.2627
91 | 0.061464 | 0.015661 | -0.061371 | -0.015602 | 9.3196e-05 | 5.9277e-05 | 0.092752 | 0.092752 | 0.092752 | 0.98704 | -0.24764 | 0.98541 | -0.27911 | 25.4814
92 | -0.074562 | -0.01902 | 0.07468 | 0.019095 | 0.00011744 | 7.484e-05 | 0.11217 | 0.11217 | 0.11217 | 0.99017 | -0.1876 | 0.99187 | -0.15505 | 30.816
93 | 0.0054625 | 0.0013689 | -0.0054614 | -0.0013687 | 1.1063e-06 | 1.5251e-07 | 0.0082363 | 0.0082365 | 0.0082365 | 0.98687 | -0.25088 | 0.98666 | -0.25513 | 2.2628
94 | 0.061371 | 0.015602 | -0.061342 | -0.015583 | 2.907e-05 | 1.849e-05 | 0.092752 | 0.092752 | 0.092752 | 0.98541 | -0.27911 | 0.9849 | -0.28895 | 25.4814
95 | -0.076884 | -0.019648 | 0.076953 | 0.019691 | 6.8611e-05 | 4.3202e-05 | 0.11548 | 0.11548 | 0.11548 | 0.99187 | -0.15505 | 0.99284 | -0.13661 | 15.8624
96 | 0.0042173 | 0.0010569 | -0.0042172 | -0.0010569 | 1.0036e-07 | -2.0261e-08 | 0.0063602 | 0.0063602 | 0.0063602 | 0.98666 | -0.25513 | 0.98663 | -0.25563 | 1.7473
97 | 0.060629 | 0.015404 | -0.060603 | -0.015388 | 2.5385e-05 | 1.6144e-05 | 0.091675 | 0.091675 | 0.091675 | 0.9849 | -0.28895 | 0.98445 | -0.29765 | 25.1855
98 | -0.040277 | -0.010149 | 0.040306 | 0.010167 | 2.8713e-05 | 1.8122e-05 | 0.061418 | 0.061418 | 0.061418 | 0.97613 | -0.45959 | 0.97689 | -0.4447 | 16.8732
99 | 0.039555 | 0.0099681 | -0.039531 | -0.0099532 | 2.3627e-05 | 1.4905e-05 | 0.060318 | 0.060318 | 0.060318 | 0.97613 | -0.45959 | 0.97549 | -0.47208 | 16.5709
100 | -0.043845 | -0.011054 | 0.043867 | 0.011068 | 2.2455e-05 | 1.4203e-05 | 0.066809 | 0.066809 | 0.066809 | 0.97689 | -0.4447 | 0.97743 | -0.434 | 18.354
101 | 0.00174 | 0.00043599 | -0.00174 | -0.00043608 | 2.0828e-08 | -8.5094e-08 | 0.0026541 | 0.0026542 | 0.0026542 | 0.97549 | -0.47208 | 0.97548 | -0.47233 | 0.72917
102 | 0.037792 | 0.0095172 | -0.037741 | -0.0094853 | 5.0619e-05 | 3.189e-05 | 0.057664 | 0.057664 | 0.057664 | 0.97549 | -0.47208 | 0.97406 | -0.50013 | 15.8418
103 | -0.043867 | -0.011068 | 0.043926 | 0.011105 | 5.8719e-05 | 3.714e-05 | 0.066809 | 0.066808 | 0.066809 | 0.97743 | -0.434 | 0.97886 | -0.40609 | 18.354
104 | 0.037741 | 0.0094853 | -0.037721 | -0.0094729 | 1.9782e-05 | 1.2463e-05 | 0.057664 | 0.057664 | 0.057664 | 0.97406 | -0.50013 | 0.97351 | -0.51112 | 15.8418
105 | -0.043926 | -0.011105 | 0.043942 | 0.011116 | 1.6694e-05 | 1.0559e-05 | 0.066808 | 0.066808 | 0.066808 | 0.97886 | -0.40609 | 0.97927 | -0.39817 | 18.354
106 | 0.033936 | 0.0085243 | -0.033913 | -0.0085094 | 2.3697e-05 | 1.4875e-05 | 0.051879 | 0.051879 | 0.051879 | 0.97351 | -0.51112 | 0.97276 | -0.52576 | 14.2525
107 | -0.044766 | -0.011322 | 0.044793 | 0.01134 | 2.7243e-05 | 1.7238e-05 | 0.068059 | 0.068059 | 0.068059 | 0.97927 | -0.39817 | 0.97992 | -0.38549 | 18.6977
108 | -0.00045132 | -0.00011311 | 0.00045132 | 0.00011306 | 6.1064e-10 | -4.6175e-08 | 0.00067445 | 0.00067444 | 0.00067445 | 0.99571 | -0.081538 | 0.99572 | -0.08151 | 0.18529
109 | -0.015716 | -0.0039415 | 0.015723 | 0.0039452 | 6.2271e-06 | 3.6297e-06 | 0.024062 | 0.024062 | 0.024062 | 0.97196 | -0.54164 | 0.97238 | -0.53333 | 6.6104
110 | -0.026907 | -0.0067502 | 0.026917 | 0.0067562 | 9.7123e-06 | 6.0263e-06 | 0.041178 | 0.041178 | 0.041178 | 0.97238 | -0.53333 | 0.97276 | -0.52576 | 11.3127
111 | 0.011185 | 0.002805 | -0.011181 | -0.0028032 | 3.4676e-06 | 1.8279e-06 | 0.017116 | 0.017117 | 0.017117 | 0.97238 | -0.53333 | 0.97205 | -0.53984 | 4.7024
112 | -0.0042254 | -0.001059 | 0.0042254 | 0.001059 | 1.4134e-08 | -2.6128e-09 | 0.006399 | 0.006399 | 0.006399 | 0.98257 | -0.33407 | 0.98257 | -0.334 | 1.758
113 | -0.0053509 | -0.001341 | 0.0053513 | 0.0013411 | 4.0595e-07 | 5.0982e-08 | 0.0081034 | 0.0081033 | 0.0081034 | 0.98257 | -0.334 | 0.98265 | -0.33241 | 2.2262
114 | -0.0062463 | -0.0015653 | 0.0062471 | 0.0015655 | 7.757e-07 | 2.0351e-07 | 0.0094587 | 0.0094586 | 0.0094587 | 0.98265 | -0.33241 | 0.98279 | -0.3298 | 2.5985
115 | 0.00089505 | 0.00022425 | -0.00089505 | -0.00022432 | 4.0802e-09 | -7.2422e-08 | 0.0013553 | 0.0013554 | 0.0013554 | 0.98265 | -0.33241 | 0.98265 | -0.3325 | 0.37235
116 | -0.059716 | -0.01513 | 0.059809 | 0.015189 | 9.2384e-05 | 5.8744e-05 | 0.090474 | 0.090474 | 0.090474 | 0.98279 | -0.3298 | 0.98445 | -0.29765 | 24.8556
117 | 0.053469 | 0.013565 | -0.053465 | -0.013562 | 4.0212e-06 | 2.5528e-06 | 0.081016 | 0.081016 | 0.081016 | 0.98279 | -0.3298 | 0.9827 | -0.33137 | 22.2571
118 | 0.051166 | 0.012986 | -0.051126 | -0.012961 | 3.9886e-05 | 2.5303e-05 | 0.077534 | 0.077534 | 0.077534 | 0.9827 | -0.33137 | 0.98187 | -0.34759 | 21.3005
119 | -0.05066 | -0.012834 | 0.050685 | 0.01285 | 2.522e-05 | 1.5997e-05 | 0.076866 | 0.076866 | 0.076866 | 0.98133 | -0.35794 | 0.98187 | -0.34759 | 21.1169
120 | 0.048939 | 0.012403 | -0.048875 | -0.012362 | 6.4683e-05 | 4.1002e-05 | 0.074257 | 0.074257 | 0.074257 | 0.98133 | -0.35794 | 0.97992 | -0.38549 | 20.4004
121 | 0.0040817 | 0.0010224 | -0.0040808 | -0.0010226 | 9.3487e-07 | -2.19e-07 | 0.0061979 | 0.0061982 | 0.0061982 | 0.97992 | -0.38549 | 0.97967 | -0.3903 | 1.7028
122 | 0.002082 | 0.00052167 | -0.0020819 | -0.00052179 | 4.1138e-08 | -1.118e-07 | 0.0031623 | 0.0031623 | 0.0031623 | 0.97967 | -0.3903 | 0.97965 | -0.39071 | 0.86877
123 | -0.0063269 | -0.0015857 | 0.0063273 | 0.0015858 | 4.5878e-07 | 1.3262e-07 | 0.0096955 | 0.0096954 | 0.0096955 | 0.97102 | -0.56026 | 0.9711 | -0.55874 | 2.6636
124 | 0.0029746 | 0.00074531 | -0.0029744 | -0.00074543 | 1.1068e-07 | -1.1152e-07 | 0.0045161 | 0.0045162 | 0.0045162 | 0.98007 | -0.38184 | 0.98003 | -0.38262 | 1.2407
125 | 0.0011731 | 0.00029382 | -0.0011731 | -0.000294 | 1.8129e-08 | -1.8044e-07 | 0.001781 | 0.0017811 | 0.0017811 | 0.98007 | -0.38184 | 0.98006 | -0.38217 | 0.48931
126 | 0.0014612 | 0.00036617 | -0.0014612 | -0.00036621 | 6.3639e-09 | -3.9372e-08 | 0.0022186 | 0.0022186 | 0.0022186 | 0.98003 | -0.38262 | 0.98003 | -0.38272 | 0.6095
127 | 0.069006 | 0.017469 | -0.068918 | -0.017413 | 8.8277e-05 | 5.6229e-05 | 0.10494 | 0.10494 | 0.10494 | 0.9791 | -0.40079 | 0.97773 | -0.42748 | 28.8289
128 | 0.0037716 | 0.00094509 | -0.0037716 | -0.00094511 | 6.2326e-08 | -2.2704e-08 | 0.0057553 | 0.0057553 | 0.0057553 | 0.97513 | -0.47846 | 0.97511 | -0.47881 | 1.5811
129 | -0.0045909 | -0.0011504 | 0.0045912 | 0.0011504 | 3.3363e-07 | -1.2641e-08 | 0.0070055 | 0.0070055 | 0.0070055 | 0.97513 | -0.47846 | 0.9752 | -0.47694 | 1.9246
130 | 0.0015924 | 0.00039896 | -0.0015924 | -0.00039908 | 2.4521e-08 | -1.2245e-07 | 0.0024299 | 0.00243 | 0.00243 | 0.97511 | -0.47881 | 0.97509 | -0.47913 | 0.66758
131 | -0.0045912 | -0.0011504 | 0.0045917 | 0.0011504 | 4.5517e-07 | -1.7312e-08 | 0.0070055 | 0.0070053 | 0.0070055 | 0.9752 | -0.47694 | 0.97531 | -0.47485 | 1.9246
132 | 0.060704 | 0.015297 | -0.060666 | -0.015273 | 3.8098e-05 | 2.4235e-05 | 0.092646 | 0.092646 | 0.092646 | 0.97531 | -0.47485 | 0.97464 | -0.48798 | 25.4522
133 | -0.065296 | -0.016447 | 0.065413 | 0.016522 | 0.00011722 | 7.4624e-05 | 0.099651 | 0.099651 | 0.099651 | 0.97531 | -0.47485 | 0.97722 | -0.43739 | 27.3767
134 | 0.058874 | 0.014823 | -0.058838 | -0.014801 | 3.5413e-05 | 2.2519e-05 | 0.089909 | 0.089909 | 0.089909 | 0.97464 | -0.48798 | 0.974 | -0.50057 | 24.7003
135 | -0.067374 | -0.017013 | 0.067406 | 0.017034 | 3.202e-05 | 2.0391e-05 | 0.10264 | 0.10264 | 0.10264 | 0.97722 | -0.43739 | 0.97773 | -0.42748 | 28.1968

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.5773 | 0.14639

## res_load
| p_mw | q_mvar
0 | 0.050077 | 0.012551
1 | 0.071223 | 0.01785
2 | 0.058205 | 0.014587
3 | 0.09328 | 0.023378
4 | 0.00099148 | 0.00024849
5 | 0.0028457 | 0.0007132
6 | 0.0023005 | 0.00057655
7 | 0.00095966 | 0.00024051
8 | 0.0029801 | 0.0007469
9 | 0.03704 | 0.0092831
10 | 0.003267 | 0.0008188
11 | 0.0032739 | 0.00082053
12 | 0.0023908 | 0.00059919
13 | 0.010264 | 0.0025723
14 | 0.00090778 | 0.00022751
15 | 0.00070796 | 0.00017743
16 | 0.003902 | 0.00097795
17 | 0.0038017 | 0.00095279
18 | 0.00063888 | 0.00016012
19 | 0.003654 | 0.00091578
20 | 0.00063898 | 0.00016014
21 | 0.0024617 | 0.00061697
22 | 0.00081511 | 0.00020429
23 | 0.0018001 | 0.00045115
24 | 0.0028806 | 0.00072194
25 | 0.0012895 | 0.00032319
26 | 0.0010289 | 0.00025785
27 | 0.0015441 | 0.00038699
28 | 0.00075505 | 0.00018923
29 | 0.0012509 | 0.0003135
30 | 0.00070373 | 0.00017637
31 | 0.0003494 | 8.7568e-05
32 | 0.00069538 | 0.00017428
33 | 0.0038636 | 0.00096832
34 | 0.0045391 | 0.0011376
35 | 0.0043799 | 0.0010977
36 | 0.0025781 | 0.00064613
37 | 0.0068016 | 0.0017046
38 | 0.0010322 | 0.0002587
39 | 0.00029947 | 7.5054e-05
40 | 0.0012992 | 0.0003256
41 | 0.0010921 | 0.00027369
42 | 0.0010135 | 0.00025401
43 | 0.00018833 | 4.72e-05
44 | 0.0003048 | 7.6389e-05
45 | 0.00013185 | 3.3044e-05
46 | 0.0027743 | 0.00069532
47 | 0.0040892 | 0.0010249
48 | 0.0034864 | 0.00087377
49 | 0.0020584 | 0.00051588
50 | 0.0006765 | 0.00016955
51 | 0.0010929 | 0.00027392
52 | 0.0012181 | 0.00030528
53 | 0.00016779 | 4.2051e-05
54 | 0.001568 | 0.00039298
55 | 0.00014963 | 3.75e-05
56 | 0.0012756 | 0.0003197
57 | 0.00053611 | 0.00013436
58 | 0.00015934 | 3.9934e-05
59 | 0.00017587 | 4.4078e-05
60 | 0.00013123 | 3.289e-05
61 | 0.044305 | 0.011104
62 | 0.0023266 | 0.0005831
63 | 0.0018323 | 0.00045921
64 | 0.001399 | 0.00035062
65 | 0.0033459 | 0.00083856
66 | 0.0011819 | 0.00029622
67 | 0.0012618 | 0.00031624
68 | 0.0016458 | 0.00041248
69 | 0.0022049 | 0.00055259
70 | 0.0012441 | 0.0003118
71 | 0.00071284 | 0.00017865
72 | 0.029773 | 0.0074619
73 | 0.00072197 | 0.00018094
74 | 0.0035387 | 0.00088688
75 | 0.00174 | 0.00043608
76 | 0.0037848 | 0.00094855
77 | 0.00082338 | 0.00020636
78 | 0.00045132 | 0.00011311
79 | 0.0069955 | 0.0017532
80 | 0.0042254 | 0.001059
81 | 0.0011254 | 0.00028206
82 | 0.00089505 | 0.00022432
83 | 0.00079461 | 0.00019915
84 | 0.0022996 | 0.00057633
85 | 0.0042172 | 0.0010569
86 | 0.0017203 | 0.00043114
87 | 0.000441 | 0.00011053
88 | 0.0019988 | 0.00050095
89 | 0.0020819 | 0.00052179
90 | 0.0063269 | 0.0015857
91 | 0.0026518 | 0.00066462
92 | 0.0015132 | 0.00037925
93 | 0.0011731 | 0.000294
94 | 0.0014612 | 0.00036621
95 | 0.001169 | 0.00029299
96 | 0.0008193 | 0.00020534
97 | 0.0021792 | 0.00054615
98 | 0.0015924 | 0.00039908
99 | 0.0017925 | 0.00044924
100 | 0.0019606 | 0.00049136
101 | 0.00086656 | 0.00021718
102 | 0.0015119 | 0.00037892

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1