## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2535-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2535-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2535-2_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2535-2_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2535-2_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2535-2_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2535-2_0_3_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_2535-2_0_3_node_77 | 0.4 | n |  | TRUE
8 | bus_LV_2535-2_0_3_node_83 | 0.4 | n |  | TRUE
9 | bus_LV_2535-2_0_3_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_2535-2_0_3_node_48 | 0.4 | n |  | TRUE
11 | bus_LV_2535-2_0_3_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_2535-2_0_3_node_66 | 0.4 | n |  | TRUE
13 | bus_LV_2535-2_0_3_node_75 | 0.4 | n |  | TRUE
14 | bus_LV_2535-2_0_3_node_84 | 0.4 | n |  | TRUE
15 | bus_LV_2535-2_0_3_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_2535-2_0_3_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_2535-2_0_3_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_2535-2_0_3_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_2535-2_0_3_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2535-2_0_3_node_127 | 0.4 | n |  | TRUE
21 | bus_LV_2535-2_0_3_node_101 | 0.4 | n |  | TRUE
22 | bus_LV_2535-2_0_3_node_128 | 0.4 | n |  | TRUE
23 | bus_LV_2535-2_0_3_node_102 | 0.4 | n |  | TRUE
24 | bus_LV_2535-2_0_3_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2535-2_0_3_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2535-2_0_3_node_54 | 0.4 | n |  | TRUE
27 | bus_LV_2535-2_0_3_node_51 | 0.4 | n |  | TRUE
28 | bus_LV_2535-2_0_3_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_2535-2_0_3_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2535-2_0_3_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2535-2_0_3_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_2535-2_0_3_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_2535-2_0_3_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_2535-2_0_3_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_2535-2_0_3_node_125 | 0.4 | n |  | TRUE
36 | bus_LV_2535-2_0_3_node_124 | 0.4 | n |  | TRUE
37 | bus_LV_2535-2_0_3_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_2535-2_0_3_node_103 | 0.4 | n |  | TRUE
39 | bus_LV_2535-2_0_3_node_104 | 0.4 | n |  | TRUE
40 | bus_LV_2535-2_0_3_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_2535-2_0_3_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_2535-2_0_3_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_2535-2_0_3_node_115 | 0.4 | n |  | TRUE
44 | bus_LV_2535-2_0_3_node_114 | 0.4 | n |  | TRUE
45 | bus_LV_2535-2_0_3_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_2535-2_0_3_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_2535-2_0_3_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_2535-2_0_3_node_134 | 0.4 | n |  | TRUE
49 | bus_LV_2535-2_0_3_node_138 | 0.4 | n |  | TRUE
50 | bus_LV_2535-2_0_3_node_141 | 0.4 | n |  | TRUE
51 | bus_LV_2535-2_0_3_node_137 | 0.4 | n |  | TRUE
52 | bus_LV_2535-2_0_3_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_2535-2_0_3_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_2535-2_0_3_node_33 | 0.4 | n |  | TRUE
55 | bus_LV_2535-2_0_3_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_2535-2_0_3_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_2535-2_0_3_node_55 | 0.4 | n |  | TRUE
58 | bus_LV_2535-2_0_3_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_2535-2_0_3_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_2535-2_0_3_node_36 | 0.4 | n |  | TRUE
61 | bus_LV_2535-2_0_3_node_37 | 0.4 | n |  | TRUE
62 | bus_LV_2535-2_0_3_node_38 | 0.4 | n |  | TRUE
63 | bus_LV_2535-2_0_3_node_39 | 0.4 | n |  | TRUE
64 | bus_LV_2535-2_0_3_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_2535-2_0_3_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_2535-2_0_3_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_2535-2_0_3_node_57 | 0.4 | n |  | TRUE
68 | bus_LV_2535-2_0_3_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_2535-2_0_3_node_42 | 0.4 | n |  | TRUE
70 | bus_LV_2535-2_0_3_node_43 | 0.4 | n |  | TRUE
71 | bus_LV_2535-2_0_3_node_46 | 0.4 | n |  | TRUE
72 | bus_LV_2535-2_0_3_node_44 | 0.4 | n |  | TRUE
73 | bus_LV_2535-2_0_3_node_45 | 0.4 | n |  | TRUE
74 | bus_LV_2535-2_0_3_node_47 | 0.4 | n |  | TRUE
75 | bus_LV_2535-2_0_3_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_2535-2_0_3_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_2535-2_0_3_node_49 | 0.4 | n |  | TRUE
78 | bus_LV_2535-2_0_3_node_58 | 0.4 | n |  | TRUE
79 | bus_LV_2535-2_0_3_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_2535-2_0_3_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_2535-2_0_3_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_2535-2_0_3_node_67 | 0.4 | n |  | TRUE
83 | bus_LV_2535-2_0_3_node_79 | 0.4 | n |  | TRUE
84 | bus_LV_2535-2_0_3_node_85 | 0.4 | n |  | TRUE
85 | bus_LV_2535-2_0_3_node_72 | 0.4 | n |  | TRUE
86 | bus_LV_2535-2_0_3_node_80 | 0.4 | n |  | TRUE
87 | bus_LV_2535-2_0_3_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_2535-2_0_3_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_2535-2_0_3_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_2535-2_0_3_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_2535-2_0_3_node_71 | 0.4 | n |  | TRUE
92 | bus_LV_2535-2_0_3_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_2535-2_0_3_node_105 | 0.4 | n |  | TRUE
94 | bus_LV_2535-2_0_3_node_98 | 0.4 | n |  | TRUE
95 | bus_LV_2535-2_0_3_node_107 | 0.4 | n |  | TRUE
96 | bus_LV_2535-2_0_3_node_95 | 0.4 | n |  | TRUE
97 | bus_LV_2535-2_0_3_node_76 | 0.4 | n |  | TRUE
98 | bus_LV_2535-2_0_3_node_78 | 0.4 | n |  | TRUE
99 | bus_LV_2535-2_0_3_node_81 | 0.4 | n |  | TRUE
100 | bus_LV_2535-2_0_3_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_2535-2_0_3_node_86 | 0.4 | n |  | TRUE
102 | bus_LV_2535-2_0_3_node_87 | 0.4 | n |  | TRUE
103 | bus_LV_2535-2_0_3_node_88 | 0.4 | n |  | TRUE
104 | bus_LV_2535-2_0_3_node_89 | 0.4 | n |  | TRUE
105 | bus_LV_2535-2_0_3_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_2535-2_0_3_node_91 | 0.4 | n |  | TRUE
107 | bus_LV_2535-2_0_3_node_92 | 0.4 | n |  | TRUE
108 | bus_LV_2535-2_0_3_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_2535-2_0_3_node_100 | 0.4 | n |  | TRUE
110 | bus_LV_2535-2_0_3_node_110 | 0.4 | n |  | TRUE
111 | bus_LV_2535-2_0_3_node_99 | 0.4 | n |  | TRUE
112 | bus_LV_2535-2_0_3_node_93 | 0.4 | n |  | TRUE
113 | bus_LV_2535-2_0_3_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_2535-2_0_3_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_2535-2_0_3_node_97 | 0.4 | n |  | TRUE
116 | bus_LV_2535-2_0_3_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_2535-2_0_3_node_108 | 0.4 | n |  | TRUE
118 | bus_LV_2535-2_0_3_node_109 | 0.4 | n |  | TRUE
119 | bus_LV_2535-2_0_3_node_111 | 0.4 | n |  | TRUE
120 | bus_LV_2535-2_0_3_node_113 | 0.4 | n |  | TRUE
121 | bus_LV_2535-2_0_3_node_248 | 0.4 | n |  | TRUE
122 | bus_LV_2535-2_0_3_node_129 | 0.4 | n |  | TRUE
123 | bus_LV_2535-2_0_3_node_249 | 0.4 | n |  | TRUE
124 | bus_LV_2535-2_0_3_node_130 | 0.4 | n |  | TRUE
125 | bus_LV_2535-2_0_3_node_116 | 0.4 | n |  | TRUE
126 | bus_LV_2535-2_0_3_node_117 | 0.4 | n |  | TRUE
127 | bus_LV_2535-2_0_3_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_2535-2_0_3_node_119 | 0.4 | n |  | TRUE
129 | bus_LV_2535-2_0_3_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_2535-2_0_3_node_122 | 0.4 | n |  | TRUE
131 | bus_LV_2535-2_0_3_node_121 | 0.4 | n |  | TRUE
132 | bus_LV_2535-2_0_3_node_132 | 0.4 | n |  | TRUE
133 | bus_LV_2535-2_0_3_node_123 | 0.4 | n |  | TRUE
134 | bus_LV_2535-2_0_3_node_133 | 0.4 | n |  | TRUE
135 | bus_LV_2535-2_0_3_node_126 | 0.4 | n |  | TRUE
136 | bus_LV_2535-2_0_3_node_131 | 0.4 | n |  | TRUE
137 | bus_LV_2535-2_0_3_node_136 | 0.4 | n |  | TRUE
138 | bus_LV_2535-2_0_3_node_140 | 0.4 | n |  | TRUE
139 | bus_LV_2535-2_0_3_node_139 | 0.4 | n |  | TRUE
140 | bus_LV_2535-2_0_3_node_250 | 0.4 | n |  | TRUE
141 | bus_LV_2535-2_0_3_node_251 | 0.4 | n |  | TRUE
142 | bus_LV_2535-2_0_3_node_252 | 0.4 | n |  | TRUE
143 | bus_LV_2535-2_0_3_node_253 | 0.4 | n |  | TRUE
144 | bus_MV_392_1_node_167 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2535-2_0_3_load_0 | 0 | 0.0073015 | 0.0018299 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2535-2_0_3_load_1 | 1 | 0.0042904 | 0.0010753 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2535-2_0_3_load_3 | 2 | 0.0028565 | 0.00071591 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2535-2_0_3_load_5 | 5 | 0.0029753 | 0.00074567 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2535-2_0_3_load_83 | 8 | 0.0021915 | 0.00054925 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2535-2_0_3_load_11 | 9 | 0.0048992 | 0.0012279 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2535-2_0_3_load_48 | 10 | 0.063234 | 0.015848 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2535-2_0_3_load_75 | 13 | 0.0034265 | 0.00085876 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2535-2_0_3_load_84 | 14 | 0.001088 | 0.00027267 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2535-2_0_3_load_6 | 15 | 0.0038398 | 0.00096235 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2535-2_0_3_load_7 | 16 | 0.0035952 | 0.00090103 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2535-2_0_3_load_8 | 17 | 0.0027164 | 0.00068079 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2535-2_0_3_load_9 | 18 | 0.0036346 | 0.00091092 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2535-2_0_3_load_10 | 19 | 0.0020537 | 0.00051471 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2535-2_0_3_load_127 | 20 | 0.0019138 | 0.00047965 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2535-2_0_3_load_101 | 21 | 0.0015104 | 0.00037854 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2535-2_0_3_load_128 | 22 | 0.002215 | 0.00055513 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2535-2_0_3_load_102 | 23 | 0.0026728 | 0.00066988 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2535-2_0_3_load_14 | 24 | 0.01017 | 0.0025487 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2535-2_0_3_load_15 | 25 | 0.018767 | 0.0047035 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2535-2_0_3_load_54 | 26 | 0.013447 | 0.0033701 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2535-2_0_3_load_16 | 28 | 0.0025143 | 0.00063014 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2535-2_0_3_load_17 | 29 | 0.0027893 | 0.00069907 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2535-2_0_3_load_19 | 31 | 0.0025531 | 0.00063986 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2535-2_0_3_load_21 | 32 | 0.0018932 | 0.00047447 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2535-2_0_3_load_22 | 33 | 0.0031687 | 0.00079414 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2535-2_0_3_load_23 | 34 | 0.0021744 | 0.00054495 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2535-2_0_3_load_124 | 36 | 0.0043028 | 0.0010784 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2535-2_0_3_load_24 | 37 | 0.0020661 | 0.00051782 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2535-2_0_3_load_103 | 38 | 0.0019209 | 0.00048144 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2535-2_0_3_load_104 | 39 | 0.0022382 | 0.00056096 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2535-2_0_3_load_25 | 40 | 0.0012671 | 0.00031756 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2535-2_0_3_load_27 | 42 | 0.0012792 | 0.00032061 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2535-2_0_3_load_115 | 43 | 0.0012932 | 0.00032412 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2535-2_0_3_load_114 | 44 | 0.0025092 | 0.00062888 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2535-2_0_3_load_29 | 46 | 0.0015979 | 0.00040047 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2535-2_0_3_load_134 | 48 | 0.0013706 | 0.00034351 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2535-2_0_3_load_138 | 49 | 0.0006866 | 0.00017208 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2535-2_0_3_load_141 | 50 | 0.0042872 | 0.0010745 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2535-2_0_3_load_137 | 51 | 0.00099278 | 0.00024881 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2535-2_0_3_load_31 | 52 | 0.0031491 | 0.00078923 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2535-2_0_3_load_32 | 53 | 0.00091889 | 0.0002303 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2535-2_0_3_load_33 | 54 | 0.0035606 | 0.00089236 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2535-2_0_3_load_55 | 57 | 0.00074229 | 0.00018603 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2535-2_0_3_load_60 | 58 | 0.014228 | 0.0035659 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2535-2_0_3_load_36 | 60 | 0.0033785 | 0.00084674 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2535-2_0_3_load_39 | 63 | 0.001087 | 0.00027242 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2535-2_0_3_load_52 | 64 | 0.0017705 | 0.00044374 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2535-2_0_3_load_41 | 65 | 0.0051834 | 0.0012991 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2535-2_0_3_load_50 | 66 | 0.00082423 | 0.00020657 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2535-2_0_3_load_57 | 67 | 0.00042456 | 0.00010641 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2535-2_0_3_load_40 | 68 | 0.0016419 | 0.0004115 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2535-2_0_3_load_42 | 69 | 0.0010039 | 0.00025161 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2535-2_0_3_load_43 | 70 | 0.0027759 | 0.0006957 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2535-2_0_3_load_44 | 72 | 0.0026215 | 0.00065701 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2535-2_0_3_load_45 | 73 | 0.004128 | 0.0010346 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2535-2_0_3_load_47 | 74 | 0.00132 | 0.00033082 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2535-2_0_3_load_61 | 75 | 0.0012395 | 0.00031066 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2535-2_0_3_load_62 | 76 | 0.0018164 | 0.00045523 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2535-2_0_3_load_49 | 77 | 0.012899 | 0.0032328 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2535-2_0_3_load_58 | 78 | 0.0020638 | 0.00051723 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2535-2_0_3_load_63 | 79 | 0.0043165 | 0.0010818 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2535-2_0_3_load_79 | 83 | 0.00037164 | 9.3142e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2535-2_0_3_load_85 | 84 | 0.0046685 | 0.00117 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2535-2_0_3_load_80 | 86 | 0.00066871 | 0.00016759 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2535-2_0_3_load_74 | 87 | 0.0058619 | 0.0014691 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2535-2_0_3_load_68 | 89 | 0.00043605 | 0.00010929 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2535-2_0_3_load_69 | 90 | 0.00060548 | 0.00015175 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2535-2_0_3_load_71 | 91 | 0.0015112 | 0.00037874 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2535-2_0_3_load_73 | 92 | 0.00070804 | 0.00017745 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2535-2_0_3_load_98 | 94 | 0.0005123 | 0.00012839 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2535-2_0_3_load_107 | 95 | 0.0014899 | 0.00037339 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2535-2_0_3_load_76 | 97 | 0.0012763 | 0.00031987 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2535-2_0_3_load_78 | 98 | 0.0023085 | 0.00057857 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2535-2_0_3_load_81 | 99 | 0.00056301 | 0.0001411 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2535-2_0_3_load_82 | 100 | 0.001909 | 0.00047844 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2535-2_0_3_load_86 | 101 | 0.0028542 | 0.00071533 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2535-2_0_3_load_87 | 102 | 0.0013656 | 0.00034225 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2535-2_0_3_load_88 | 103 | 0.0018025 | 0.00045176 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2535-2_0_3_load_90 | 105 | 0.0013181 | 0.00033036 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2535-2_0_3_load_91 | 106 | 0.0017094 | 0.00042842 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2535-2_0_3_load_92 | 107 | 0.0021494 | 0.00053869 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2535-2_0_3_load_100 | 109 | 0.0013118 | 0.00032876 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2535-2_0_3_load_99 | 111 | 0.0026488 | 0.00066385 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2535-2_0_3_load_93 | 112 | 0.0018993 | 0.00047601 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2535-2_0_3_load_94 | 113 | 0.0023838 | 0.00059744 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2535-2_0_3_load_96 | 114 | 0.0013444 | 0.00033693 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2535-2_0_3_load_97 | 115 | 0.004058 | 0.001017 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2535-2_0_3_load_112 | 116 | 0.0024177 | 0.00060592 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2535-2_0_3_load_108 | 117 | 0.0011624 | 0.00029133 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2535-2_0_3_load_109 | 118 | 0.0017782 | 0.00044567 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2535-2_0_3_load_111 | 119 | 0.0018809 | 0.0004714 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2535-2_0_3_load_113 | 120 | 0.0038404 | 0.00096249 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2535-2_0_3_load_248 | 121 | 0.001361 | 0.00034109 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2535-2_0_3_load_129 | 122 | 0.0011291 | 0.00028298 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2535-2_0_3_load_249 | 123 | 0.0024504 | 0.00061413 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2535-2_0_3_load_130 | 124 | 0.0036367 | 0.00091145 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2535-2_0_3_load_116 | 125 | 0.0043793 | 0.0010976 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2535-2_0_3_load_117 | 126 | 0.0032246 | 0.00080816 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2535-2_0_3_load_132 | 132 | 0.00079611 | 0.00019952 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2535-2_0_3_load_123 | 133 | 0.0043247 | 0.0010839 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2535-2_0_3_load_133 | 134 | 0.0012406 | 0.00031092 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2535-2_0_3_load_126 | 135 | 0.002723 | 0.00068244 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2535-2_0_3_load_131 | 136 | 0.003156 | 0.00079096 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2535-2_0_3_load_140 | 138 | 0.00049856 | 0.00012495 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2535-2_0_3_load_139 | 139 | 0.0018131 | 0.00045441 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2535-2_0_3_load_250 | 140 | 0.0012474 | 0.00031264 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2535-2_0_3_load_251 | 141 | 0.0012605 | 0.0003159 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2535-2_0_3_load_252 | 142 | 0.0013567 | 0.00034002 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2535-2_0_3_load_253 | 143 | 0.0017766 | 0.00044527 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2535-2_0_3_line_0 |  | 0 | 1 | 0.014761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2535-2_0_3_line_1 |  | 1 | 2 | 0.016024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2535-2_0_3_line_2 |  | 2 | 6 | 0.0074436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2535-2_0_3_line_3 |  | 3 | 4 | 0.028685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2535-2_0_3_line_4 |  | 3 | 5 | 0.0024295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_2535-2_0_3_line_5 |  | 4 | 7 | 0.002344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2535-2_0_3_line_6 |  | 4 | 8 | 0.021038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2535-2_0_3_line_7 |  | 5 | 9 | 0.027616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2535-2_0_3_line_8 |  | 6 | 10 | 0.0058046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2535-2_0_3_line_9 |  | 6 | 11 | 0.03928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2535-2_0_3_line_10 |  | 7 | 12 | 0.020823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2535-2_0_3_line_11 |  | 7 | 13 | 0.01598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2535-2_0_3_line_12 |  | 8 | 14 | 0.016191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2535-2_0_3_line_13 |  | 9 | 11 | 0.0178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2535-2_0_3_line_14 |  | 11 | 24 | 0.012898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2535-2_0_3_line_15 |  | 11 | 25 | 0.034807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2535-2_0_3_line_16 |  | 12 | 84 | 0.012044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2535-2_0_3_line_17 |  | 13 | 97 | 0.0013005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2535-2_0_3_line_18 |  | 15 | 16 | 0.019901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2535-2_0_3_line_19 |  | 15 | 17 | 0.0031296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2535-2_0_3_line_20 |  | 16 | 18 | 0.0047915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2535-2_0_3_line_21 |  | 17 | 19 | 0.023219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2535-2_0_3_line_22 |  | 18 | 20 | 0.021109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2535-2_0_3_line_23 |  | 19 | 21 | 0.0035291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2535-2_0_3_line_24 |  | 20 | 22 | 0.02079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2535-2_0_3_line_25 |  | 21 | 23 | 0.022115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2535-2_0_3_line_26 |  | 22 | 35 | 0.011973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2535-2_0_3_line_27 |  | 23 | 106 | 0.0082443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2535-2_0_3_line_28 |  | 24 | 26 | 0.025509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2535-2_0_3_line_29 |  | 26 | 27 | 0.028048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2535-2_0_3_line_30 |  | 27 | 56 | 0.01378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2535-2_0_3_line_31 |  | 27 | 77 | 0.01149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2535-2_0_3_line_32 |  | 28 | 29 | 0.02186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2535-2_0_3_line_33 |  | 28 | 30 | 0.01354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2535-2_0_3_line_34 |  | 29 | 31 | 0.01603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2535-2_0_3_line_35 |  | 30 | 32 | 0.019206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2535-2_0_3_line_36 |  | 31 | 33 | 0.005582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2535-2_0_3_line_37 |  | 33 | 34 | 0.018765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2535-2_0_3_line_38 |  | 34 | 37 | 0.0040996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2535-2_0_3_line_39 |  | 35 | 36 | 0.023941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2535-2_0_3_line_40 |  | 36 | 133 | 0.028406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2535-2_0_3_line_41 |  | 37 | 38 | 0.022355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2535-2_0_3_line_42 |  | 38 | 39 | 0.0046167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2535-2_0_3_line_43 |  | 39 | 114 | 0.01499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2535-2_0_3_line_44 |  | 40 | 41 | 0.0040272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2535-2_0_3_line_45 |  | 41 | 42 | 0.031714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2535-2_0_3_line_46 |  | 42 | 43 | 0.023343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2535-2_0_3_line_47 |  | 43 | 44 | 0.022334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2535-2_0_3_line_48 |  | 44 | 95 | 0.036543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2535-2_0_3_line_49 |  | 45 | 46 | 0.02817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2535-2_0_3_line_50 |  | 45 | 47 | 0.022743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2535-2_0_3_line_51 |  | 46 | 48 | 0.043558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2535-2_0_3_line_52 |  | 47 | 49 | 0.041897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2535-2_0_3_line_53 |  | 48 | 50 | 0.055985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2535-2_0_3_line_54 |  | 49 | 51 | 0.037445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2535-2_0_3_line_55 |  | 50 | 138 | 0.011794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2535-2_0_3_line_56 |  | 51 | 129 | 0.030327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2535-2_0_3_line_57 |  | 52 | 53 | 0.019978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2535-2_0_3_line_58 |  | 52 | 54 | 0.018794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2535-2_0_3_line_59 |  | 54 | 55 | 0.020181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2535-2_0_3_line_60 |  | 55 | 56 | 0.026374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2535-2_0_3_line_61 |  | 55 | 57 | 0.024534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2535-2_0_3_line_62 |  | 56 | 58 | 0.021524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2535-2_0_3_line_63 |  | 57 | 59 | 0.010813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2535-2_0_3_line_64 |  | 59 | 67 | 0.029569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2535-2_0_3_line_65 |  | 60 | 61 | 0.071608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2535-2_0_3_line_66 |  | 61 | 62 | 0.028363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2535-2_0_3_line_67 |  | 61 | 63 | 0.015445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2535-2_0_3_line_68 |  | 62 | 64 | 0.02345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2535-2_0_3_line_69 |  | 63 | 65 | 0.022751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2535-2_0_3_line_70 |  | 64 | 66 | 0.020439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2535-2_0_3_line_71 |  | 65 | 68 | 0.018468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2535-2_0_3_line_72 |  | 66 | 77 | 0.014638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2535-2_0_3_line_73 |  | 67 | 78 | 0.011791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2535-2_0_3_line_74 |  | 68 | 69 | 0.032881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2535-2_0_3_line_75 |  | 69 | 70 | 0.034422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2535-2_0_3_line_76 |  | 70 | 71 | 0.021783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2535-2_0_3_line_77 |  | 71 | 72 | 0.020131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2535-2_0_3_line_78 |  | 72 | 73 | 0.033019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2535-2_0_3_line_79 |  | 73 | 74 | 0.045984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2535-2_0_3_line_80 |  | 74 | 75 | 0.012881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2535-2_0_3_line_81 |  | 75 | 76 | 0.017608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2535-2_0_3_line_82 |  | 79 | 80 | 0.023393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2535-2_0_3_line_83 |  | 80 | 81 | 0.018906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2535-2_0_3_line_84 |  | 80 | 82 | 0.04397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2535-2_0_3_line_85 |  | 81 | 83 | 0.012058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2535-2_0_3_line_86 |  | 82 | 85 | 0.008423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2535-2_0_3_line_87 |  | 82 | 84 | 0.028996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_2535-2_0_3_line_88 |  | 83 | 86 | 0.0025237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2535-2_0_3_line_89 |  | 85 | 87 | 0.022997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2535-2_0_3_line_90 |  | 85 | 88 | 0.013992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_2535-2_0_3_line_91 |  | 86 | 99 | 0.0082698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2535-2_0_3_line_92 |  | 88 | 92 | 0.023076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_2535-2_0_3_line_93 |  | 88 | 89 | 0.050794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2535-2_0_3_line_94 |  | 89 | 90 | 0.014364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2535-2_0_3_line_95 |  | 90 | 91 | 0.03728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2535-2_0_3_line_96 |  | 91 | 93 | 0.035107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2535-2_0_3_line_97 |  | 92 | 94 | 0.028022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_2535-2_0_3_line_98 |  | 93 | 95 | 0.014656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2535-2_0_3_line_99 |  | 94 | 96 | 0.019936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_2535-2_0_3_line_100 |  | 96 | 115 | 0.023489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_2535-2_0_3_line_101 |  | 96 | 112 | 0.01322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2535-2_0_3_line_102 |  | 97 | 98 | 0.024505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2535-2_0_3_line_103 |  | 99 | 100 | 0.019188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2535-2_0_3_line_104 |  | 101 | 102 | 0.021001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2535-2_0_3_line_105 |  | 101 | 103 | 0.018381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2535-2_0_3_line_106 |  | 102 | 104 | 0.01075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2535-2_0_3_line_107 |  | 103 | 105 | 0.0038111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2535-2_0_3_line_108 |  | 104 | 106 | 0.017818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2535-2_0_3_line_109 |  | 104 | 107 | 0.0094501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2535-2_0_3_line_110 |  | 105 | 108 | 0.013064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2535-2_0_3_line_111 |  | 107 | 109 | 0.0094457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2535-2_0_3_line_112 |  | 108 | 110 | 0.025726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2535-2_0_3_line_113 |  | 109 | 111 | 0.020279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2535-2_0_3_line_114 |  | 110 | 116 | 0.019598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2535-2_0_3_line_115 |  | 110 | 117 | 0.008203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2535-2_0_3_line_116 |  | 111 | 115 | 0.002295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2535-2_0_3_line_117 |  | 112 | 113 | 0.01829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2535-2_0_3_line_118 |  | 113 | 114 | 0.0063551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2535-2_0_3_line_119 |  | 116 | 121 | 0.0019172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2535-2_0_3_line_120 |  | 117 | 118 | 0.019492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2535-2_0_3_line_121 |  | 118 | 119 | 0.01391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2535-2_0_3_line_122 |  | 119 | 120 | 0.0068927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2535-2_0_3_line_123 |  | 120 | 122 | 0.014654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2535-2_0_3_line_124 |  | 121 | 123 | 0.030643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2535-2_0_3_line_125 |  | 122 | 124 | 0.0006716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2535-2_0_3_line_126 |  | 123 | 140 | 8.1246e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2535-2_0_3_line_127 |  | 124 | 136 | 0.021181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2535-2_0_3_line_128 |  | 125 | 126 | 0.033339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2535-2_0_3_line_129 |  | 125 | 127 | 0.0073568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2535-2_0_3_line_130 |  | 126 | 128 | 0.058331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2535-2_0_3_line_131 |  | 127 | 129 | 0.012972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2535-2_0_3_line_132 |  | 128 | 130 | 0.037267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2535-2_0_3_line_133 |  | 129 | 131 | 0.033649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2535-2_0_3_line_134 |  | 130 | 133 | 0.013996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2535-2_0_3_line_135 |  | 131 | 132 | 0.015761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2535-2_0_3_line_136 |  | 132 | 134 | 0.14217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2535-2_0_3_line_137 |  | 135 | 136 | 0.005814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2535-2_0_3_line_138 |  | 137 | 138 | 0.018987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2535-2_0_3_line_139 |  | 137 | 139 | 0.022474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2535-2_0_3_line_140 |  | 140 | 141 | 0.040643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2535-2_0_3_line_141 |  | 141 | 142 | 0.021963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2535-2_0_3_line_142 |  | 142 | 143 | 0.0077375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2535-2_0_3_trafo_84 | 0.63 MVA 20/0.4 kV | 144 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2614925.8851 | 1222923.6826 | 2614919.1339 | 1222920.878 | 2614912.4577 | 1222917.5716
1 | 2614898.0983 | 1222910.46 | 2614912.4577 | 1222917.5716
2 | 2614891.428 | 1222907.1565 | 2614898.0983 | 1222910.46
3 | 2614969.3619 | 1222907.518 | 2614944.5169 | 1222893.0585
4 | 2614944.5169 | 1222893.0585 | 2614942.3427 | 1222891.9743
5 | 2614969.3619 | 1222907.518 | 2614971.3913 | 1222908.7015
6 | 2614969.3619 | 1222907.518 | 2614960.4884 | 1222926.5928
7 | 2614917.6291 | 1222879.6502 | 2614942.3427 | 1222891.9743
8 | 2614891.428 | 1222907.1565 | 2614886.3107 | 1222909.8964
9 | 2614891.428 | 1222907.1565 | 2614896.4017 | 1222904.5006 | 2614898.5981 | 1222902.605 | 2614900.4003 | 1222900.5972 | 2614903.4037 | 1222894.4011 | 2614903.803 | 1222892.4009 | 2614903.7033 | 1222889.7992 | 2614903.1024 | 1222887.4963 | 2614900.5008 | 1222881.5975 | 2614900.7854 | 1222873.8938
10 | 2614971.3913 | 1222908.7015 | 2614980.2889 | 1222913.8824 | 2614989.9774 | 1222918.1203
11 | 2614971.3913 | 1222908.7015 | 2614979.7926 | 1222895.1076
12 | 2614958.8494 | 1222941.6115 | 2614956.6901 | 1222934.7577 | 2614960.4884 | 1222926.5928
13 | 2614900.7854 | 1222873.8938 | 2614917.6291 | 1222879.6502 | 2614917.6291 | 1222879.6502
14 | 2614900.7854 | 1222873.8938 | 2614888.3526 | 1222870.461
15 | 2614900.7854 | 1222873.8938 | 2614907.7975 | 1222847.5959 | 2614910.998 | 1222840.7129
16 | 2614989.9774 | 1222918.1203 | 2614995.6057 | 1222926.6505 | 2614997.0421 | 1222927.7758
17 | 2614979.7926 | 1222895.1076 | 2614980.4763 | 1222894.0013
18 | 2615027.3236 | 1223113.1021 | 2615018.0028 | 1223130.6851
19 | 2615027.3236 | 1223113.1021 | 2615028.7894 | 1223110.337
20 | 2615018.0028 | 1223130.6851 | 2615015.7586 | 1223134.9185
21 | 2615039.658 | 1223089.8192 | 2615039.1992 | 1223090.6999 | 2615028.7894 | 1223110.337
22 | 2615005.8716 | 1223153.5694 | 2615015.7586 | 1223134.9185
23 | 2615039.658 | 1223089.8192 | 2615041.2886 | 1223086.6894
24 | 2614996.1344 | 1223171.9377 | 2615005.8716 | 1223153.5694
25 | 2615051.5064 | 1223067.0768 | 2615041.2886 | 1223086.6894
26 | 2614992.6031 | 1223183.3035 | 2614992.8968 | 1223181.103 | 2614993.8001 | 1223177.7032 | 2614995.1979 | 1223173.7044 | 2614996.1344 | 1223171.9377
27 | 2615051.5064 | 1223067.0768 | 2615055.3155 | 1223059.7653
28 | 2614888.3526 | 1222870.461 | 2614879.7785 | 1222868.0936 | 2614863.6389 | 1222864.1529
29 | 2614835.9736 | 1222866.1614 | 2614842.8107 | 1222864.3662 | 2614853.0139 | 1222863.0241 | 2614863.3096 | 1222864.0725 | 2614863.6389 | 1222864.1529
30 | 2614829.0184 | 1222854.404 | 2614833.9995 | 1222861.0202 | 2614835.9736 | 1222866.1614
31 | 2614835.9736 | 1222866.1614 | 2614828.8379 | 1222869.0565 | 2614825.6018 | 1222871.0273
32 | 2614943.6497 | 1223153.8385 | 2614953.1462 | 1223134.1494
33 | 2614937.7676 | 1223166.0339 | 2614943.6497 | 1223153.8385
34 | 2614960.1098 | 1223119.7115 | 2614953.1462 | 1223134.1494
35 | 2614937.7676 | 1223166.0339 | 2614955.955 | 1223172.2063
36 | 2614962.5348 | 1223114.6838 | 2614960.1098 | 1223119.7115
37 | 2614962.5348 | 1223114.6838 | 2614970.6869 | 1223097.7819
38 | 2614970.6869 | 1223097.7819 | 2614972.4679 | 1223094.0893
39 | 2614992.6031 | 1223183.3035 | 2615014.0972 | 1223187.9046 | 2615016.019 | 1223188.2922
40 | 2615043.8642 | 1223193.9077 | 2615016.019 | 1223188.2922
41 | 2614982.6627 | 1223074.1974 | 2614975.3704 | 1223088.0715 | 2614972.4679 | 1223094.0893
42 | 2614982.6627 | 1223074.1974 | 2614984.8106 | 1223070.1108
43 | 2614991.7848 | 1223056.8419 | 2614984.8106 | 1223070.1108
44 | 2615247.3988 | 1223110.3055 | 2615247.8848 | 1223114.3033
45 | 2615247.3988 | 1223110.3055 | 2615244.2002 | 1223100.8029 | 2615236.8008 | 1223091.2007 | 2615230.1375 | 1223084.3378
46 | 2615212.6485 | 1223068.9039 | 2615226.8021 | 1223080.9025 | 2615230.1375 | 1223084.3378
47 | 2615212.6485 | 1223068.9039 | 2615195.612 | 1223054.4614
48 | 2615195.612 | 1223054.4614 | 2615171.0036 | 1223033.5997 | 2615167.7478 | 1223030.8189
49 | 2615240.8018 | 1223193.4037 | 2615248.4034 | 1223201.0053 | 2615254.3971 | 1223208.7029 | 2615259.2789 | 1223214.6108
50 | 2615224.5717 | 1223209.2049 | 2615231.5998 | 1223203.7975 | 2615237.8039 | 1223197.3984 | 2615240.8018 | 1223193.4037
51 | 2615294.3501 | 1223239.6285 | 2615294.0003 | 1223239.4998 | 2615290.5994 | 1223238.0014 | 2615281.899 | 1223233.0985 | 2615270.1034 | 1223225.7974 | 2615265.904 | 1223222.1957 | 2615263.4006 | 1223219.5989 | 2615259.2789 | 1223214.6108
52 | 2615224.5717 | 1223209.2049 | 2615200.794 | 1223229.0004 | 2615192.3728 | 1223236.0119
53 | 2615294.3501 | 1223239.6285 | 2615344.2344 | 1223214.2138
54 | 2615163.5963 | 1223259.9715 | 2615192.3728 | 1223236.0119
55 | 2615344.2344 | 1223214.2138 | 2615355.9606 | 1223215.4751
56 | 2615140.2903 | 1223279.3762 | 2615163.5963 | 1223259.9715
57 | 2614774.975 | 1222818.5178 | 2614773.7052 | 1222817.2454 | 2614764.4544 | 1222807.5836 | 2614762.3969 | 1222805.4995 | 2614761.071 | 1222804.1735
58 | 2614788.6969 | 1222831.3478 | 2614780.6346 | 1222824.1888 | 2614774.975 | 1222818.5178
59 | 2614805.6763 | 1222842.1835 | 2614797.1643 | 1222837.4152 | 2614789.6619 | 1222832.2047 | 2614788.6969 | 1222831.3478
60 | 2614829.0184 | 1222854.404 | 2614824.6007 | 1222853.0033 | 2614805.6763 | 1222842.1835
61 | 2614805.6763 | 1222842.1835 | 2614788.7102 | 1222859.9048
62 | 2614829.0184 | 1222854.404 | 2614830.1553 | 1222848.5367 | 2614832.2369 | 1222840.9263 | 2614832.5652 | 1222833.2758
63 | 2614781.2322 | 1222867.7156 | 2614788.7102 | 1222859.9048
64 | 2614781.2322 | 1222867.7156 | 2614773.0249 | 1222865.4384 | 2614756.3227 | 1222852.6241
65 | 2614744.4991 | 1222900.9998 | 2614705.8033 | 1222912.3 | 2614685.3016 | 1222919.9985 | 2614676.7715 | 1222923.9403
66 | 2614771.834 | 1222893.1516 | 2614744.4991 | 1222900.9998
67 | 2614744.4991 | 1222900.9998 | 2614745.3034 | 1222903.8813 | 2614746.4009 | 1222907.7974 | 2614747.598 | 1222911.3023 | 2614749.1986 | 1222914.1969 | 2614750.0546 | 1222915.2724
68 | 2614771.834 | 1222893.1516 | 2614793.4926 | 1222886.9349 | 2614794.3515 | 1222886.614
69 | 2614766.7973 | 1222930.5054 | 2614758.5995 | 1222924.4038 | 2614753.0995 | 1222919.0982 | 2614750.0546 | 1222915.2724
70 | 2614813.0995 | 1222878.6416 | 2614808.9847 | 1222881.1477 | 2614794.3515 | 1222886.614
71 | 2614781.8052 | 1222941.2687 | 2614766.7973 | 1222930.5054 | 2614766.7973 | 1222930.5054
72 | 2614825.6018 | 1222871.0273 | 2614813.0995 | 1222878.6416
73 | 2614746.9679 | 1222845.4469 | 2614756.3227 | 1222852.6241
74 | 2614781.8052 | 1222941.2687 | 2614783.7994 | 1222942.6989 | 2614795.798 | 1222951.2002 | 2614801.7397 | 1222946.5567 | 2614806.7319 | 1222940.0749
75 | 2614833.1219 | 1222937.5265 | 2614819.3469 | 1222928.7788 | 2614815.3198 | 1222928.9245 | 2614806.7319 | 1222940.0749
76 | 2614851.5104 | 1222949.2039 | 2614833.1219 | 1222937.5265
77 | 2614851.5104 | 1222949.2039 | 2614845.1981 | 1222956.5036 | 2614838.367 | 1222964.4524
78 | 2614838.367 | 1222964.4524 | 2614816.8459 | 1222989.4946
79 | 2614816.8459 | 1222989.4946 | 2614805.4985 | 1223002.6987 | 2614786.8578 | 1223024.3546
80 | 2614786.8578 | 1223024.3546 | 2614782.5993 | 1223029.3019 | 2614778.4679 | 1223034.129
81 | 2614767.0183 | 1223047.5063 | 2614778.4679 | 1223034.129
82 | 2615039.7736 | 1222925.7831 | 2615063.1207 | 1222924.3159
83 | 2615039.7736 | 1222925.7831 | 2615040.0553 | 1222919.3023 | 2615045.445 | 1222908.1093
84 | 2615020.8827 | 1222944.1463 | 2615016.5703 | 1222934.0741 | 2615015.8042 | 1222925.0891 | 2615029.4598 | 1222925.9239 | 2615039.7736 | 1222925.7831
85 | 2615045.445 | 1222908.1093 | 2615034.9057 | 1222902.2504
86 | 2615026.0225 | 1222950.8298 | 2615020.8827 | 1222944.1463
87 | 2615020.8827 | 1222944.1463 | 2615010.0842 | 1222937.9934 | 2614997.0421 | 1222927.7758
88 | 2615034.9057 | 1222902.2504 | 2615032.7 | 1222901.0241
89 | 2615026.0225 | 1222950.8298 | 2615017.202 | 1222960.302 | 2615010.2467 | 1222967.5617
90 | 2615026.0225 | 1222950.8298 | 2615037.065 | 1222959.4626
91 | 2615032.7 | 1222901.0241 | 2615025.472 | 1222897.0059
92 | 2615037.065 | 1222959.4626 | 2615028.0031 | 1222971.4023 | 2615023.3092 | 1222977.9871
93 | 2615037.065 | 1222959.4626 | 2615050.9543 | 1222966.8018 | 2615061.7604 | 1222969.9086 | 2615085.1521 | 1222974.5132
94 | 2615085.1521 | 1222974.5132 | 2615093.7993 | 1222976.2153 | 2615099.0223 | 1222978.0935
95 | 2615129.6571 | 1222998.7986 | 2615113.9773 | 1222985.7052 | 2615104.6033 | 1222980.1004 | 2615099.0223 | 1222978.0935
96 | 2615156.6039 | 1223021.3005 | 2615129.6571 | 1222998.7986
97 | 2615011.294 | 1223003.2587 | 2615017.2998 | 1222990.7978 | 2615021.0003 | 1222981.8019 | 2615022.7978 | 1222978.7046 | 2615023.3092 | 1222977.9871
98 | 2615156.6039 | 1223021.3005 | 2615167.7478 | 1223030.8189
99 | 2615003.0952 | 1223021.4133 | 2615005.1029 | 1223016.1041 | 2615011.294 | 1223003.2587
100 | 2615003.0952 | 1223021.4133 | 2615024.4342 | 1223031.2296
101 | 2615003.0952 | 1223021.4133 | 2615001.7143 | 1223034.561
102 | 2614984.492 | 1222870.779 | 2614984.9677 | 1222886.7339 | 2614980.4763 | 1222894.0013
103 | 2615008.7015 | 1222887.6829 | 2615025.472 | 1222897.0059
104 | 2615093.5561 | 1223053.8426 | 2615076.7975 | 1223048.3033 | 2615073.6141 | 1223047.257
105 | 2615093.5561 | 1223053.8426 | 2615111.0085 | 1223059.6112
106 | 2615063.4014 | 1223043.9003 | 2615073.6141 | 1223047.257
107 | 2615111.0085 | 1223059.6112 | 2615113.0985 | 1223060.3019 | 2615114.6062 | 1223060.8665
108 | 2615063.4014 | 1223043.9003 | 2615061.6014 | 1223047.9981 | 2615059.2018 | 1223052.3057 | 2615055.3155 | 1223059.7653
109 | 2615063.4014 | 1223043.9003 | 2615054.4436 | 1223040.8901
110 | 2615126.3006 | 1223066.4056 | 2615123.5004 | 1223064.1972 | 2615114.6062 | 1223060.8665
111 | 2615045.3906 | 1223039.4939 | 2615049.0924 | 1223040.6401 | 2615051.8013 | 1223040.0021 | 2615054.4436 | 1223040.8901
112 | 2615126.3006 | 1223066.4056 | 2615113.4285 | 1223088.6971
113 | 2615026.5192 | 1223032.1887 | 2615036.2412 | 1223036.661 | 2615045.3906 | 1223039.4939
114 | 2615113.4285 | 1223088.6971 | 2615129.6522 | 1223099.6916
115 | 2615113.4285 | 1223088.6971 | 2615109.5722 | 1223095.9371
116 | 2615026.5192 | 1223032.1887 | 2615024.4342 | 1223031.2296
117 | 2615001.7143 | 1223034.561 | 2615001.2695 | 1223038.7966 | 2614994.7415 | 1223051.2165
118 | 2614991.7848 | 1223056.8419 | 2614994.7415 | 1223051.2165
119 | 2615131.2393 | 1223100.7671 | 2615129.6522 | 1223099.6916
120 | 2615109.5722 | 1223095.9371 | 2615100.4089 | 1223113.1407
121 | 2615093.8695 | 1223125.418 | 2615100.4089 | 1223113.1407
122 | 2615093.8695 | 1223125.418 | 2615090.6292 | 1223131.5015
123 | 2615083.74 | 1223144.4354 | 2615090.6292 | 1223131.5015
124 | 2615131.2393 | 1223100.7671 | 2615156.6059 | 1223117.9576
125 | 2615083.4243 | 1223145.0282 | 2615083.74 | 1223144.4354
126 | 2615156.6059 | 1223117.9576 | 2615156.6731 | 1223118.0032
127 | 2615073.4671 | 1223163.7223 | 2615083.4243 | 1223145.0282
128 | 2615127.1491 | 1223267.3581 | 2615130.0392 | 1223258.0044 | 2615127.618 | 1223252.8842 | 2615117.0297 | 1223244.8861 | 2615112.8041 | 1223243.0283
129 | 2615128.1771 | 1223274.6428 | 2615127.1491 | 1223267.3581
130 | 2615094.5406 | 1223202.0154 | 2615086.9271 | 1223220.1067 | 2615087.681 | 1223230.8482 | 2615101.7442 | 1223238.1658 | 2615112.8041 | 1223243.0283
131 | 2615128.1771 | 1223274.6428 | 2615140.2903 | 1223279.3762
132 | 2615094.5406 | 1223202.0154 | 2615086.7011 | 1223201.5064 | 2615072.3001 | 1223198.8018 | 2615063.1971 | 1223197.1001 | 2615057.7022 | 1223195.9968
133 | 2615114.6425 | 1223301.2351 | 2615122.5999 | 1223294.1067 | 2615140.2903 | 1223279.3762
134 | 2615057.7022 | 1223195.9968 | 2615044.8006 | 1223194.0965 | 2615043.8642 | 1223193.9077
135 | 2615114.6425 | 1223301.2351 | 2615102.9056 | 1223311.7549
136 | 2615102.9056 | 1223311.7549 | 2615011.7721 | 1223420.8772
137 | 2615070.7338 | 1223168.8538 | 2615073.4671 | 1223163.7223
138 | 2615374.8387 | 1223217.5055 | 2615355.9606 | 1223215.4751
139 | 2615374.8387 | 1223217.5055 | 2615374.5936 | 1223195.033
140 | 2615156.6731 | 1223118.0032 | 2615161.8247 | 1223121.4943 | 2615164.1649 | 1223125.6694 | 2615163.9824 | 1223131.8503 | 2615161.9593 | 1223137.1927 | 2615153.3968 | 1223152.7262
141 | 2615153.3968 | 1223152.7262 | 2615142.7943 | 1223171.9605
142 | 2615139.0591 | 1223178.7366 | 2615142.7943 | 1223171.9605

## bus_geodata
| x | y | coords
0 | 2614925.8851 | 1222923.6826
1 | 2614912.4577 | 1222917.5716
2 | 2614898.0983 | 1222910.46
3 | 2614944.5169 | 1222893.0585
4 | 2614969.3619 | 1222907.518
5 | 2614942.3427 | 1222891.9743
6 | 2614891.428 | 1222907.1565
7 | 2614971.3913 | 1222908.7015
8 | 2614960.4884 | 1222926.5928
9 | 2614917.6291 | 1222879.6502
10 | 2614886.3107 | 1222909.8964
11 | 2614900.7854 | 1222873.8938
12 | 2614989.9774 | 1222918.1203
13 | 2614979.7926 | 1222895.1076
14 | 2614958.8494 | 1222941.6115
15 | 2615027.3236 | 1223113.1021
16 | 2615018.0028 | 1223130.6851
17 | 2615028.7894 | 1223110.337
18 | 2615015.7586 | 1223134.9185
19 | 2615039.658 | 1223089.8192
20 | 2615005.8716 | 1223153.5694
21 | 2615041.2886 | 1223086.6894
22 | 2614996.1344 | 1223171.9377
23 | 2615051.5064 | 1223067.0768
24 | 2614888.3526 | 1222870.461
25 | 2614910.998 | 1222840.7129
26 | 2614863.6389 | 1222864.1529
27 | 2614835.9736 | 1222866.1614
28 | 2614943.6497 | 1223153.8385
29 | 2614953.1462 | 1223134.1494
30 | 2614937.7676 | 1223166.0339
31 | 2614960.1098 | 1223119.7115
32 | 2614955.955 | 1223172.2063
33 | 2614962.5348 | 1223114.6838
34 | 2614970.6869 | 1223097.7819
35 | 2614992.6031 | 1223183.3035
36 | 2615016.019 | 1223188.2922
37 | 2614972.4679 | 1223094.0893
38 | 2614982.6627 | 1223074.1974
39 | 2614984.8106 | 1223070.1108
40 | 2615247.8848 | 1223114.3033
41 | 2615247.3988 | 1223110.3055
42 | 2615230.1375 | 1223084.3378
43 | 2615212.6485 | 1223068.9039
44 | 2615195.612 | 1223054.4614
45 | 2615240.8018 | 1223193.4037
46 | 2615259.2789 | 1223214.6108
47 | 2615224.5717 | 1223209.2049
48 | 2615294.3501 | 1223239.6285
49 | 2615192.3728 | 1223236.0119
50 | 2615344.2344 | 1223214.2138
51 | 2615163.5963 | 1223259.9715
52 | 2614774.975 | 1222818.5178
53 | 2614761.071 | 1222804.1735
54 | 2614788.6969 | 1222831.3478
55 | 2614805.6763 | 1222842.1835
56 | 2614829.0184 | 1222854.404
57 | 2614788.7102 | 1222859.9048
58 | 2614832.5652 | 1222833.2758
59 | 2614781.2322 | 1222867.7156
60 | 2614676.7715 | 1222923.9403
61 | 2614744.4991 | 1222900.9998
62 | 2614771.834 | 1222893.1516
63 | 2614750.0546 | 1222915.2724
64 | 2614794.3515 | 1222886.614
65 | 2614766.7973 | 1222930.5054
66 | 2614813.0995 | 1222878.6416
67 | 2614756.3227 | 1222852.6241
68 | 2614781.8052 | 1222941.2687
69 | 2614806.7319 | 1222940.0749
70 | 2614833.1219 | 1222937.5265
71 | 2614851.5104 | 1222949.2039
72 | 2614838.367 | 1222964.4524
73 | 2614816.8459 | 1222989.4946
74 | 2614786.8578 | 1223024.3546
75 | 2614778.4679 | 1223034.129
76 | 2614767.0183 | 1223047.5063
77 | 2614825.6018 | 1222871.0273
78 | 2614746.9679 | 1222845.4469
79 | 2615063.1207 | 1222924.3159
80 | 2615039.7736 | 1222925.7831
81 | 2615045.445 | 1222908.1093
82 | 2615020.8826 | 1222944.1463
83 | 2615034.9058 | 1222902.2504
84 | 2614997.0421 | 1222927.7758
85 | 2615026.0225 | 1222950.8298
86 | 2615032.7 | 1222901.0241
87 | 2615010.2467 | 1222967.5617
88 | 2615037.065 | 1222959.4626
89 | 2615085.1521 | 1222974.5132
90 | 2615099.0223 | 1222978.0935
91 | 2615129.6571 | 1222998.7986
92 | 2615023.3092 | 1222977.9871
93 | 2615156.6039 | 1223021.3005
94 | 2615011.294 | 1223003.2587
95 | 2615167.7478 | 1223030.8189
96 | 2615003.0952 | 1223021.4133
97 | 2614980.4763 | 1222894.0013
98 | 2614984.492 | 1222870.779
99 | 2615025.472 | 1222897.0059
100 | 2615008.7015 | 1222887.6829
101 | 2615093.5561 | 1223053.8426
102 | 2615073.6141 | 1223047.257
103 | 2615111.0085 | 1223059.6112
104 | 2615063.4014 | 1223043.9003
105 | 2615114.6062 | 1223060.8665
106 | 2615055.3155 | 1223059.7653
107 | 2615054.4436 | 1223040.8901
108 | 2615126.3006 | 1223066.4056
109 | 2615045.3906 | 1223039.4939
110 | 2615113.4285 | 1223088.6971
111 | 2615026.5192 | 1223032.1887
112 | 2615001.7143 | 1223034.561
113 | 2614994.7415 | 1223051.2165
114 | 2614991.7848 | 1223056.8419
115 | 2615024.4342 | 1223031.2296
116 | 2615129.6522 | 1223099.6916
117 | 2615109.5722 | 1223095.9371
118 | 2615100.4089 | 1223113.1407
119 | 2615093.8695 | 1223125.418
120 | 2615090.6292 | 1223131.5015
121 | 2615131.2393 | 1223100.7671
122 | 2615083.74 | 1223144.4354
123 | 2615156.6059 | 1223117.9576
124 | 2615083.4243 | 1223145.0282
125 | 2615127.1491 | 1223267.3581
126 | 2615112.8041 | 1223243.0283
127 | 2615128.1771 | 1223274.6428
128 | 2615094.5406 | 1223202.0154
129 | 2615140.2903 | 1223279.3762
130 | 2615057.7022 | 1223195.9968
131 | 2615114.6425 | 1223301.2351
132 | 2615102.9056 | 1223311.7549
133 | 2615043.8642 | 1223193.9077
134 | 2615011.7721 | 1223420.8772
135 | 2615070.7338 | 1223168.8538
136 | 2615073.4671 | 1223163.7223
137 | 2615374.8387 | 1223217.5055
138 | 2615355.9606 | 1223215.4751
139 | 2615374.5936 | 1223195.033
140 | 2615156.6731 | 1223118.0032
141 | 2615153.3968 | 1223152.7262
142 | 2615142.7943 | 1223171.9605
143 | 2615139.0591 | 1223178.7366
144 | 2614969.3619 | 1222907.518

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98767 | -0.23674 | 0.0073015 | 0.0018299
1 | 0.98776 | -0.23482 | 0.0042904 | 0.0010753
2 | 0.98793 | -0.2315 | 0.0028565 | 0.00071591
3 | 0.99413 | -0.11179 | 0 | 0
4 | 0.99584 | -0.07901 | 0 | 0
5 | 0.99399 | -0.11458 | 0.0029753 | 0.00074567
6 | 0.98803 | -0.22958 | 0 | 0
7 | 0.99572 | -0.081318 | 0 | 0
8 | 0.99819 | -0.034398 | 0.0021915 | 0.00054925
9 | 0.99236 | -0.14577 | 0.0048992 | 0.0012279
10 | 0.9877 | -0.23613 | 0.063234 | 0.015848
11 | 0.99083 | -0.17525 | 0 | 0
12 | 0.99469 | -0.10099 | 0 | 0
13 | 0.99562 | -0.083288 | 0.0034265 | 0.00085876
14 | 1 | 0 | -0.37153 | -0.094596
15 | 0.97988 | -0.38693 | 0.0038398 | 0.00096235
16 | 0.97912 | -0.40172 | 0.0035952 | 0.00090103
17 | 0.98001 | -0.38439 | 0.0027164 | 0.00068079
18 | 0.97895 | -0.40497 | 0.0036346 | 0.00091092
19 | 0.98103 | -0.36442 | 0.0020537 | 0.00051471
20 | 0.97829 | -0.4179 | 0.0019138 | 0.00047965
21 | 0.98119 | -0.36125 | 0.0015104 | 0.00037854
22 | 0.97768 | -0.42993 | 0.002215 | 0.00055513
23 | 0.98224 | -0.34085 | 0.0026728 | 0.00066988
24 | 0.98976 | -0.19598 | 0.01017 | 0.0025487
25 | 0.99024 | -0.18685 | 0.018767 | 0.0047035
26 | 0.98788 | -0.23246 | 0.013447 | 0.0033701
27 | 0.98615 | -0.26598 | 0 | 0
28 | 0.98628 | -0.26291 | 0.0025143 | 0.00063014
29 | 0.98636 | -0.26118 | 0.0027893 | 0.00069907
30 | 0.98625 | -0.26337 | 0 | 0
31 | 0.98647 | -0.25912 | 0.0025531 | 0.00063986
32 | 0.98622 | -0.26402 | 0.0018932 | 0.00047447
33 | 0.98652 | -0.25814 | 0.0031687 | 0.00079414
34 | 0.98674 | -0.2538 | 0.0021744 | 0.00054495
35 | 0.97735 | -0.43639 | 0 | 0
36 | 0.97669 | -0.4493 | 0.0043028 | 0.0010784
37 | 0.9868 | -0.25269 | 0.0020661 | 0.00051782
38 | 0.98715 | -0.24583 | 0.0019209 | 0.00048144
39 | 0.98723 | -0.24425 | 0.0022382 | 0.00056096
40 | 0.99002 | -0.19079 | 0.0012671 | 0.00031756
41 | 0.99002 | -0.1907 | 0 | 0
42 | 0.99006 | -0.18999 | 0.0012792 | 0.00032061
43 | 0.99011 | -0.18893 | 0.0012932 | 0.00032412
44 | 0.99019 | -0.1874 | 0.0025092 | 0.00062888
45 | 0.97183 | -0.54501 | 0 | 0
46 | 0.97158 | -0.54999 | 0.0015979 | 0.00040047
47 | 0.97204 | -0.54099 | 0 | 0
48 | 0.97126 | -0.5564 | 0.0013706 | 0.00034351
49 | 0.97241 | -0.5336 | 0.0006866 | 0.00017208
50 | 0.97091 | -0.56323 | 0.0042872 | 0.0010745
51 | 0.97277 | -0.52652 | 0.00099278 | 0.00024881
52 | 0.98536 | -0.28146 | 0.0031491 | 0.00078923
53 | 0.98534 | -0.28179 | 0.00091889 | 0.0002303
54 | 0.98543 | -0.28009 | 0.0035606 | 0.00089236
55 | 0.98557 | -0.27732 | 0 | 0
56 | 0.98583 | -0.27218 | 0 | 0
57 | 0.9855 | -0.27875 | 0.00074229 | 0.00018603
58 | 0.98555 | -0.27768 | 0.014228 | 0.0035659
59 | 0.98547 | -0.27923 | 0 | 0
60 | 0.98332 | -0.32121 | 0.0033785 | 0.00084674
61 | 0.98354 | -0.31685 | 0 | 0
62 | 0.98422 | -0.30347 | 0 | 0
63 | 0.98321 | -0.32321 | 0.001087 | 0.00027242
64 | 0.98479 | -0.29242 | 0.0017705 | 0.00044374
65 | 0.98276 | -0.33213 | 0.0051834 | 0.0012991
66 | 0.98532 | -0.28214 | 0.00082423 | 0.00020657
67 | 0.9854 | -0.28055 | 0.00042456 | 0.00010641
68 | 0.98247 | -0.33765 | 0.0016419 | 0.0004115
69 | 0.98202 | -0.3465 | 0.0010039 | 0.00025161
70 | 0.98158 | -0.35516 | 0.0027759 | 0.0006957
71 | 0.98136 | -0.35955 | 0 | 0
72 | 0.98115 | -0.3636 | 0.0026215 | 0.00065701
73 | 0.98089 | -0.36869 | 0.004128 | 0.0010346
74 | 0.9807 | -0.37234 | 0.00132 | 0.00033082
75 | 0.98067 | -0.37305 | 0.0012395 | 0.00031066
76 | 0.98064 | -0.37363 | 0.0018164 | 0.00045523
77 | 0.98571 | -0.27458 | 0.012899 | 0.0032328
78 | 0.98538 | -0.28099 | 0.0020638 | 0.00051723
79 | 0.99229 | -0.14696 | 0.0043165 | 0.0010818
80 | 0.99238 | -0.14518 | 0 | 0
81 | 0.99232 | -0.14635 | 0 | 0
82 | 0.9927 | -0.13908 | 0 | 0
83 | 0.99228 | -0.1471 | 0.00037164 | 9.3142e-05
84 | 0.99409 | -0.11239 | 0.0046685 | 0.00117
85 | 0.99231 | -0.14646 | 0 | 0
86 | 0.99227 | -0.14724 | 0.00066871 | 0.00016759
87 | 0.99219 | -0.14885 | 0.0058619 | 0.0014691
88 | 0.99169 | -0.15825 | 0 | 0
89 | 0.99121 | -0.16761 | 0.00043605 | 0.00010929
90 | 0.99108 | -0.17015 | 0.00060548 | 0.00015175
91 | 0.99076 | -0.17634 | 0.0015112 | 0.00037874
92 | 0.99075 | -0.1763 | 0.00070804 | 0.00017745
93 | 0.99051 | -0.18124 | 0 | 0
94 | 0.98962 | -0.19814 | 0.0005123 | 0.00012839
95 | 0.9904 | -0.18328 | 0.0014899 | 0.00037339
96 | 0.98841 | -0.22142 | 0 | 0
97 | 0.99561 | -0.08337 | 0.0012763 | 0.00031987
98 | 0.99556 | -0.084365 | 0.0023085 | 0.00057857
99 | 0.99226 | -0.1476 | 0.00056301 | 0.0001411
100 | 0.99222 | -0.14825 | 0.001909 | 0.00047844
101 | 0.98246 | -0.3366 | 0.0028542 | 0.00071533
102 | 0.98318 | -0.32252 | 0.0013656 | 0.00034225
103 | 0.98188 | -0.34799 | 0.0018025 | 0.00045176
104 | 0.98357 | -0.31505 | 0 | 0
105 | 0.98176 | -0.35023 | 0.0013181 | 0.00033036
106 | 0.98265 | -0.33286 | 0.0017094 | 0.00042842
107 | 0.98439 | -0.29907 | 0.0021494 | 0.00053869
108 | 0.98139 | -0.3576 | 0 | 0
109 | 0.98523 | -0.28276 | 0.0013118 | 0.00032876
110 | 0.98065 | -0.37213 | 0 | 0
111 | 0.98706 | -0.24737 | 0.0026488 | 0.00066385
112 | 0.98808 | -0.22778 | 0.0018993 | 0.00047601
113 | 0.98766 | -0.23596 | 0.0023838 | 0.00059744
114 | 0.98753 | -0.23854 | 0.0013444 | 0.00033693
115 | 0.98728 | -0.24326 | 0.004058 | 0.001017
116 | 0.98043 | -0.37635 | 0.0024177 | 0.00060592
117 | 0.9805 | -0.375 | 0.0011624 | 0.00029133
118 | 0.98017 | -0.38142 | 0.0017782 | 0.00044567
119 | 0.97996 | -0.38555 | 0.0018809 | 0.0004714
120 | 0.97987 | -0.38736 | 0.0038404 | 0.00096249
121 | 0.98041 | -0.37668 | 0.001361 | 0.00034109
122 | 0.97972 | -0.39019 | 0.0011291 | 0.00028298
123 | 0.98018 | -0.38118 | 0.0024504 | 0.00061413
124 | 0.97972 | -0.39031 | 0.0036367 | 0.00091145
125 | 0.97334 | -0.51526 | 0.0043793 | 0.0010976
126 | 0.97389 | -0.50442 | 0.0032246 | 0.00080816
127 | 0.97325 | -0.51706 | 0 | 0
128 | 0.97502 | -0.48203 | 0 | 0
129 | 0.97309 | -0.52023 | 0 | 0
130 | 0.97575 | -0.46776 | 0 | 0
131 | 0.97302 | -0.5215 | 0 | 0
132 | 0.97299 | -0.52209 | 0.00079611 | 0.00019952
133 | 0.97602 | -0.4624 | 0.0043247 | 0.0010839
134 | 0.97283 | -0.52534 | 0.0012406 | 0.00031092
135 | 0.97959 | -0.39286 | 0.002723 | 0.00068244
136 | 0.9796 | -0.39257 | 0.003156 | 0.00079096
137 | 0.97085 | -0.56438 | 0 | 0
138 | 0.97089 | -0.56374 | 0.00049856 | 0.00012495
139 | 0.97082 | -0.56513 | 0.0018131 | 0.00045441
140 | 0.98018 | -0.38119 | 0.0012474 | 0.00031264
141 | 0.98002 | -0.38443 | 0.0012605 | 0.0003159
142 | 0.97996 | -0.38568 | 0.0013567 | 0.00034002
143 | 0.97994 | -0.38593 | 0.0017766 | 0.00044527
144 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0073015 | -0.0018299 | 0.0073021 | 0.0018302 | 6.6981e-07 | 2.3976e-07 | 0.011 | 0.011 | 0.011 | 0.98767 | -0.23674 | 0.98776 | -0.23482 | 3.0221
1 | -0.011593 | -0.0029054 | 0.011594 | 0.0029064 | 1.8326e-06 | 9.6771e-07 | 0.017464 | 0.017463 | 0.017464 | 0.98776 | -0.23482 | 0.98793 | -0.2315 | 4.7977
2 | -0.014451 | -0.0036223 | 0.014452 | 0.0036231 | 1.3224e-06 | 7.5103e-07 | 0.021766 | 0.021766 | 0.021766 | 0.98793 | -0.2315 | 0.98803 | -0.22958 | 5.9797
3 | -0.196 | -0.049609 | 0.19631 | 0.049806 | 0.00030897 | 0.00019662 | 0.29354 | 0.29354 | 0.29354 | 0.99413 | -0.11179 | 0.99584 | -0.07901 | 26.8814
4 | 0.196 | 0.049609 | -0.19597 | -0.049592 | 2.6168e-05 | 1.6653e-05 | 0.29354 | 0.29354 | 0.29354 | 0.99413 | -0.11179 | 0.99399 | -0.11458 | 26.8814
5 | 0.16998 | 0.043344 | -0.16996 | -0.043332 | 1.894e-05 | 1.203e-05 | 0.25425 | 0.25425 | 0.25425 | 0.99584 | -0.07901 | 0.99572 | -0.081318 | 23.2828
6 | -0.36628 | -0.093149 | 0.36707 | 0.093654 | 0.00078912 | 0.00050421 | 0.54779 | 0.54779 | 0.54779 | 0.99584 | -0.07901 | 0.99819 | -0.034398 | 50.1641
7 | 0.193 | 0.048847 | -0.19271 | -0.048663 | 0.0002885 | 0.00018357 | 0.28909 | 0.28909 | 0.28909 | 0.99399 | -0.11458 | 0.99236 | -0.14577 | 26.4735
8 | 0.063254 | 0.015861 | -0.063234 | -0.015848 | 1.9755e-05 | 1.2569e-05 | 0.095266 | 0.095266 | 0.095266 | 0.98803 | -0.22958 | 0.9877 | -0.23613 | 26.1719
9 | -0.077706 | -0.019484 | 0.077908 | 0.019612 | 0.00020175 | 0.00012861 | 0.11703 | 0.11703 | 0.11703 | 0.98803 | -0.22958 | 0.99083 | -0.17525 | 32.1515
10 | 0.16295 | 0.041575 | -0.16279 | -0.041477 | 0.00015467 | 9.8179e-05 | 0.24377 | 0.24377 | 0.24377 | 0.99572 | -0.081318 | 0.99469 | -0.10099 | 22.3232
11 | 0.007012 | 0.0017571 | -0.0070114 | -0.0017569 | 6.5803e-07 | 2.133e-07 | 0.010479 | 0.010479 | 0.010479 | 0.99572 | -0.081318 | 0.99562 | -0.083288 | 2.8788
12 | -0.36927 | -0.094203 | 0.36988 | 0.094596 | 0.00061458 | 0.0003927 | 0.55106 | 0.55106 | 0.55106 | 0.99819 | -0.034398 | 1 | 0 | 50.4633
13 | 0.18781 | 0.047435 | -0.18755 | -0.047266 | 0.00026493 | 0.0001691 | 0.28174 | 0.28174 | 0.28174 | 0.99236 | -0.14577 | 0.99083 | -0.17525 | 38.7012
14 | 0.09086 | 0.022944 | -0.09077 | -0.022887 | 9.0137e-05 | 5.7521e-05 | 0.13651 | 0.13651 | 0.13651 | 0.99083 | -0.17525 | 0.98976 | -0.19598 | 37.5035
15 | 0.018778 | 0.0047097 | -0.018767 | -0.0047035 | 1.0381e-05 | 6.1958e-06 | 0.028201 | 0.028201 | 0.028201 | 0.99083 | -0.17525 | 0.99024 | -0.18685 | 7.7476
16 | 0.16279 | 0.041477 | -0.1627 | -0.04142 | 8.9465e-05 | 5.6789e-05 | 0.24377 | 0.24377 | 0.24377 | 0.99469 | -0.10099 | 0.99409 | -0.11239 | 22.3233
17 | 0.0035849 | 0.00089817 | -0.0035849 | -0.00089818 | 1.3999e-08 | -7.9525e-09 | 0.0053578 | 0.0053578 | 0.0053578 | 0.99562 | -0.083288 | 0.99561 | -0.08337 | 1.4719
18 | 0.041065 | 0.010356 | -0.041036 | -0.010338 | 2.9042e-05 | 1.8337e-05 | 0.062383 | 0.062383 | 0.062383 | 0.97988 | -0.38693 | 0.97912 | -0.40172 | 17.1382
19 | -0.044904 | -0.011319 | 0.04491 | 0.011322 | 5.4609e-06 | 3.4556e-06 | 0.068214 | 0.068214 | 0.068214 | 0.97988 | -0.38693 | 0.98001 | -0.38439 | 18.7401
20 | 0.03744 | 0.0094368 | -0.037435 | -0.0094332 | 5.8213e-06 | 3.6654e-06 | 0.056919 | 0.056919 | 0.056919 | 0.97912 | -0.40172 | 0.97895 | -0.40497 | 15.6371
21 | -0.047626 | -0.012003 | 0.047672 | 0.012032 | 4.5562e-05 | 2.8867e-05 | 0.072338 | 0.072338 | 0.072338 | 0.98001 | -0.38439 | 0.98103 | -0.36442 | 19.8732
22 | 0.0338 | 0.0085223 | -0.033779 | -0.0085091 | 2.091e-05 | 1.3117e-05 | 0.051395 | 0.051395 | 0.051395 | 0.97895 | -0.40497 | 0.97829 | -0.4179 | 14.1194
23 | -0.049726 | -0.012546 | 0.049733 | 0.012551 | 7.5346e-06 | 4.7776e-06 | 0.075453 | 0.075453 | 0.075453 | 0.98103 | -0.36442 | 0.98119 | -0.36125 | 20.7289
24 | 0.031865 | 0.0080295 | -0.031847 | -0.008018 | 1.8326e-05 | 1.1468e-05 | 0.048484 | 0.048484 | 0.048484 | 0.97829 | -0.4179 | 0.97768 | -0.42993 | 13.3197
25 | -0.051243 | -0.01293 | 0.051294 | 0.012962 | 5.0124e-05 | 3.1799e-05 | 0.077744 | 0.077744 | 0.077744 | 0.98119 | -0.36125 | 0.98224 | -0.34085 | 21.3582
26 | 0.029632 | 0.0074629 | -0.029623 | -0.0074572 | 9.1379e-06 | 5.6981e-06 | 0.045113 | 0.045113 | 0.045113 | 0.97768 | -0.42993 | 0.97735 | -0.43639 | 12.3936
27 | -0.053966 | -0.013631 | 0.053987 | 0.013645 | 2.0683e-05 | 1.3133e-05 | 0.081793 | 0.081793 | 0.081793 | 0.98224 | -0.34085 | 0.98265 | -0.33286 | 22.4706
28 | 0.0806 | 0.020338 | -0.080459 | -0.020248 | 0.00014057 | 8.9638e-05 | 0.12122 | 0.12122 | 0.12122 | 0.98976 | -0.19598 | 0.98788 | -0.23246 | 33.3032
29 | 0.067013 | 0.016878 | -0.066905 | -0.01681 | 0.00010723 | 6.8268e-05 | 0.10097 | 0.10097 | 0.10097 | 0.98788 | -0.23246 | 0.98615 | -0.26598 | 27.7388
30 | 0.025103 | 0.0062949 | -0.025095 | -0.0062903 | 7.4145e-06 | 4.5695e-06 | 0.037879 | 0.037879 | 0.037879 | 0.98615 | -0.26598 | 0.98583 | -0.27218 | 10.4064
31 | 0.041803 | 0.010515 | -0.041786 | -0.010504 | 1.715e-05 | 1.0829e-05 | 0.06309 | 0.06309 | 0.06309 | 0.98615 | -0.26598 | 0.98571 | -0.27458 | 17.3325
32 | -0.0044075 | -0.0011043 | 0.0044079 | 0.0011042 | 3.6246e-07 | -4.7016e-08 | 0.0066496 | 0.0066495 | 0.0066496 | 0.98628 | -0.26291 | 0.98636 | -0.26118 | 1.8268
33 | 0.0018933 | 0.00047412 | -0.0018932 | -0.00047426 | 4.1424e-08 | -1.4628e-07 | 0.0028563 | 0.0028563 | 0.0028563 | 0.98628 | -0.26291 | 0.98625 | -0.26337 | 0.78471
34 | -0.0071972 | -0.0018033 | 0.0071979 | 0.0018035 | 7.0861e-07 | 2.4889e-07 | 0.010857 | 0.010857 | 0.010857 | 0.98636 | -0.26118 | 0.98647 | -0.25912 | 2.9828
35 | 0.0018932 | 0.00047426 | -0.0018932 | -0.00047447 | 5.8763e-08 | -2.0747e-07 | 0.0028563 | 0.0028564 | 0.0028564 | 0.98625 | -0.26337 | 0.98622 | -0.26402 | 0.78473
36 | -0.009751 | -0.0024434 | 0.0097515 | 0.0024436 | 4.5285e-07 | 2.1856e-07 | 0.014708 | 0.014708 | 0.014708 | 0.98647 | -0.25912 | 0.98652 | -0.25814 | 4.0408
37 | -0.01292 | -0.0032377 | 0.012923 | 0.0032392 | 2.6725e-06 | 1.4707e-06 | 0.019488 | 0.019488 | 0.019488 | 0.98652 | -0.25814 | 0.98674 | -0.2538 | 5.3538
38 | -0.015097 | -0.0037842 | 0.015098 | 0.0037846 | 7.9685e-07 | 4.5761e-07 | 0.022767 | 0.022767 | 0.022767 | 0.98674 | -0.2538 | 0.9868 | -0.25269 | 6.2546
39 | 0.029623 | 0.0074572 | -0.029604 | -0.0074458 | 1.8272e-05 | 1.1394e-05 | 0.045113 | 0.045113 | 0.045113 | 0.97735 | -0.43639 | 0.97669 | -0.4493 | 12.3936
40 | 0.025302 | 0.0063674 | -0.025286 | -0.0063576 | 1.5836e-05 | 9.7799e-06 | 0.038557 | 0.038557 | 0.038557 | 0.97669 | -0.4493 | 0.97602 | -0.4624 | 10.5927
41 | -0.017164 | -0.0043024 | 0.01717 | 0.0043057 | 5.6158e-06 | 3.3084e-06 | 0.025882 | 0.025882 | 0.025882 | 0.9868 | -0.25269 | 0.98715 | -0.24583 | 7.1105
42 | -0.019091 | -0.0047872 | 0.019092 | 0.004788 | 1.4338e-06 | 8.5857e-07 | 0.028778 | 0.028778 | 0.028778 | 0.98715 | -0.24583 | 0.98723 | -0.24425 | 7.906
43 | -0.02133 | -0.005349 | 0.021336 | 0.0053525 | 5.8108e-06 | 3.5272e-06 | 0.032151 | 0.032151 | 0.032151 | 0.98723 | -0.24425 | 0.98753 | -0.23854 | 8.8328
44 | -0.0012671 | -0.00031756 | 0.0012671 | 0.00031751 | 5.4774e-09 | -4.828e-08 | 0.0019044 | 0.0019044 | 0.0019044 | 0.99002 | -0.19079 | 0.99002 | -0.1907 | 0.5232
45 | -0.0012671 | -0.00031751 | 0.0012671 | 0.00031713 | 4.313e-08 | -3.8022e-07 | 0.0019044 | 0.0019043 | 0.0019044 | 0.99002 | -0.1907 | 0.99006 | -0.18999 | 0.52319
46 | -0.0025464 | -0.00063774 | 0.0025465 | 0.00063752 | 1.282e-07 | -2.1816e-07 | 0.0038269 | 0.0038268 | 0.0038269 | 0.99006 | -0.18999 | 0.99011 | -0.18893 | 1.0514
47 | -0.0038397 | -0.00096164 | 0.00384 | 0.00096153 | 2.7888e-07 | -1.0879e-07 | 0.0057704 | 0.0057703 | 0.0057704 | 0.99011 | -0.18893 | 0.99019 | -0.1874 | 1.5853
48 | -0.0063493 | -0.0015904 | 0.0063505 | 0.0015907 | 1.2474e-06 | 3.282e-07 | 0.0095411 | 0.0095409 | 0.0095411 | 0.99019 | -0.1874 | 0.9904 | -0.18328 | 2.6212
49 | 0.0095744 | 0.0024001 | -0.0095721 | -0.002399 | 2.2703e-06 | 1.1041e-06 | 0.01466 | 0.01466 | 0.01466 | 0.97183 | -0.54501 | 0.97158 | -0.54999 | 4.0275
50 | -0.0095744 | -0.0024001 | 0.0095762 | 0.002401 | 1.8329e-06 | 8.9121e-07 | 0.01466 | 0.01466 | 0.01466 | 0.97183 | -0.54501 | 0.97204 | -0.54099 | 4.0275
51 | 0.0079742 | 0.0019985 | -0.0079718 | -0.0019975 | 2.4364e-06 | 1.02e-06 | 0.012213 | 0.012213 | 0.012213 | 0.97158 | -0.54999 | 0.97126 | -0.5564 | 3.3552
52 | -0.0095762 | -0.002401 | 0.0095796 | 0.0024026 | 3.3766e-06 | 1.6414e-06 | 0.01466 | 0.01466 | 0.01466 | 0.97204 | -0.54099 | 0.97241 | -0.5336 | 4.0274
53 | 0.0066012 | 0.001654 | -0.006599 | -0.0016533 | 2.1473e-06 | 6.8164e-07 | 0.010113 | 0.010113 | 0.010113 | 0.97126 | -0.5564 | 0.97091 | -0.56323 | 2.7784
54 | -0.010266 | -0.0025747 | 0.01027 | 0.0025764 | 3.4657e-06 | 1.7534e-06 | 0.01571 | 0.01571 | 0.01571 | 0.97241 | -0.5336 | 0.97277 | -0.52652 | 4.316
55 | 0.0023118 | 0.00057881 | -0.0023118 | -0.00057892 | 5.5516e-08 | -1.1032e-07 | 0.0035429 | 0.003543 | 0.003543 | 0.97091 | -0.56323 | 0.97089 | -0.56374 | 0.97334
56 | -0.011262 | -0.0028252 | 0.011266 | 0.002827 | 3.3757e-06 | 1.7838e-06 | 0.017229 | 0.017229 | 0.017229 | 0.97277 | -0.52652 | 0.97309 | -0.52023 | 4.7332
57 | 0.0009189 | 0.00023005 | -0.00091889 | -0.0002303 | 1.4425e-08 | -2.4524e-07 | 0.0013876 | 0.0013877 | 0.0013877 | 0.98536 | -0.28146 | 0.98534 | -0.28179 | 0.38123
58 | -0.004068 | -0.0010193 | 0.0040682 | 0.0010192 | 2.6596e-07 | -6.92e-08 | 0.0061431 | 0.006143 | 0.0061431 | 0.98536 | -0.28146 | 0.98543 | -0.28009 | 1.6877
59 | -0.0076288 | -0.0019116 | 0.0076298 | 0.001912 | 1.0043e-06 | 3.8558e-07 | 0.01152 | 0.011519 | 0.01152 | 0.98543 | -0.28009 | 0.98557 | -0.27732 | 3.1647
60 | -0.010861 | -0.002721 | 0.010864 | 0.0027223 | 2.6592e-06 | 1.3657e-06 | 0.016397 | 0.016397 | 0.016397 | 0.98557 | -0.27732 | 0.98583 | -0.27218 | 4.5048
61 | 0.0032311 | 0.000809 | -0.0032309 | -0.00080917 | 2.1892e-07 | -1.7251e-07 | 0.004878 | 0.0048781 | 0.0048781 | 0.98557 | -0.27732 | 0.9855 | -0.27875 | 1.3401
62 | 0.014232 | 0.003568 | -0.014228 | -0.0035659 | 3.7248e-06 | 2.1095e-06 | 0.021482 | 0.021482 | 0.021482 | 0.98583 | -0.27218 | 0.98555 | -0.27768 | 5.9016
63 | 0.0024886 | 0.00062313 | -0.0024885 | -0.00062323 | 5.7248e-08 | -1.0114e-07 | 0.0037573 | 0.0037574 | 0.0037574 | 0.9855 | -0.27875 | 0.98547 | -0.27923 | 1.0323
64 | 0.0024885 | 0.00062323 | -0.0024884 | -0.00062351 | 1.5655e-07 | -2.7652e-07 | 0.0037574 | 0.0037575 | 0.0037575 | 0.98547 | -0.27923 | 0.9854 | -0.28055 | 1.0323
65 | -0.0033785 | -0.00084674 | 0.0033792 | 0.00084628 | 7.0186e-07 | -4.5938e-07 | 0.0051126 | 0.0051123 | 0.0051126 | 0.98332 | -0.32121 | 0.98354 | -0.31685 | 1.4046
66 | -0.026237 | -0.006587 | 0.026254 | 0.0065974 | 1.6762e-05 | 1.0367e-05 | 0.039698 | 0.039698 | 0.039698 | 0.98354 | -0.31685 | 0.98422 | -0.30347 | 10.9061
67 | 0.022858 | 0.0057407 | -0.022851 | -0.0057365 | 6.928e-06 | 4.238e-06 | 0.034586 | 0.034586 | 0.034586 | 0.98354 | -0.31685 | 0.98321 | -0.32321 | 9.5017
68 | -0.026254 | -0.0065974 | 0.026267 | 0.006606 | 1.3858e-05 | 8.5712e-06 | 0.039698 | 0.039698 | 0.039698 | 0.98422 | -0.30347 | 0.98479 | -0.29242 | 10.9061
69 | 0.021764 | 0.0054641 | -0.021754 | -0.0054585 | 9.2577e-06 | 5.6365e-06 | 0.032941 | 0.032941 | 0.032941 | 0.98321 | -0.32321 | 0.98276 | -0.33213 | 9.0498
70 | -0.028038 | -0.0070497 | 0.028052 | 0.0070582 | 1.3762e-05 | 8.5472e-06 | 0.042373 | 0.042373 | 0.042373 | 0.98479 | -0.29242 | 0.98532 | -0.28214 | 11.641
71 | 0.016571 | 0.0041594 | -0.016567 | -0.0041568 | 4.3607e-06 | 2.5569e-06 | 0.025093 | 0.025093 | 0.025093 | 0.98276 | -0.33213 | 0.98247 | -0.33765 | 6.8936
72 | -0.028876 | -0.0072648 | 0.028886 | 0.0072713 | 1.0444e-05 | 6.4975e-06 | 0.043618 | 0.043618 | 0.043618 | 0.98532 | -0.28214 | 0.98571 | -0.27458 | 11.9829
73 | 0.0020638 | 0.00051711 | -0.0020638 | -0.00051723 | 4.2943e-08 | -1.2272e-07 | 0.0031164 | 0.0031165 | 0.0031165 | 0.9854 | -0.28055 | 0.98538 | -0.28099 | 0.85617
74 | 0.014925 | 0.0037453 | -0.014918 | -0.0037417 | 6.3014e-06 | 3.6167e-06 | 0.022606 | 0.022606 | 0.022606 | 0.98247 | -0.33765 | 0.98202 | -0.3465 | 6.2105
75 | 0.013914 | 0.0034901 | -0.013909 | -0.0034868 | 5.7387e-06 | 3.2375e-06 | 0.021085 | 0.021085 | 0.021085 | 0.98202 | -0.3465 | 0.98158 | -0.35516 | 5.7926
76 | 0.011133 | 0.0027911 | -0.01113 | -0.0027899 | 2.3267e-06 | 1.2138e-06 | 0.016877 | 0.016877 | 0.016877 | 0.98158 | -0.35516 | 0.98136 | -0.35955 | 4.6366
77 | 0.01113 | 0.0027899 | -0.011128 | -0.0027888 | 2.1503e-06 | 1.1219e-06 | 0.016877 | 0.016877 | 0.016877 | 0.98136 | -0.35955 | 0.98115 | -0.3636 | 4.6366
78 | 0.0085069 | 0.0021318 | -0.0085048 | -0.0021309 | 2.061e-06 | 9.0215e-07 | 0.012901 | 0.012902 | 0.012902 | 0.98115 | -0.3636 | 0.98089 | -0.36869 | 3.5444
79 | 0.0043768 | 0.0010963 | -0.0043761 | -0.0010964 | 7.6018e-07 | -9.3813e-08 | 0.0066395 | 0.0066397 | 0.0066397 | 0.98089 | -0.36869 | 0.9807 | -0.37234 | 1.8241
80 | 0.0030561 | 0.0007656 | -0.003056 | -0.0007657 | 1.0386e-07 | -9.6059e-08 | 0.0046369 | 0.0046369 | 0.0046369 | 0.9807 | -0.37234 | 0.98067 | -0.37305 | 1.2739
81 | 0.0018165 | 0.00045504 | -0.0018164 | -0.00045523 | 5.016e-08 | -1.9005e-07 | 0.0027561 | 0.0027562 | 0.0027562 | 0.98067 | -0.37305 | 0.98064 | -0.37363 | 0.7572
82 | -0.0043165 | -0.0010818 | 0.0043168 | 0.0010817 | 3.6754e-07 | -6.6988e-08 | 0.0064729 | 0.0064728 | 0.0064729 | 0.99229 | -0.14696 | 0.99238 | -0.14518 | 1.7783
83 | 0.0035128 | 0.00087978 | -0.0035126 | -0.0008799 | 1.9669e-07 | -1.1837e-07 | 0.005267 | 0.0052671 | 0.0052671 | 0.99238 | -0.14518 | 0.99232 | -0.14635 | 1.447
84 | -0.0078296 | -0.0019615 | 0.0078319 | 0.0019624 | 2.2725e-06 | 8.8612e-07 | 0.01174 | 0.01174 | 0.01174 | 0.99238 | -0.14518 | 0.9927 | -0.13908 | 3.2252
85 | 0.0035126 | 0.0008799 | -0.0035125 | -0.00087998 | 1.2545e-07 | -7.5482e-08 | 0.0052671 | 0.0052672 | 0.0052672 | 0.99232 | -0.14635 | 0.99228 | -0.1471 | 1.447
86 | 0.15 | 0.038158 | -0.14994 | -0.038125 | 5.3322e-05 | 3.38e-05 | 0.22504 | 0.22504 | 0.22504 | 0.9927 | -0.13908 | 0.99231 | -0.14646 | 20.6083
87 | -0.15783 | -0.040121 | 0.15803 | 0.04025 | 0.00020321 | 0.00012893 | 0.23678 | 0.23678 | 0.23678 | 0.9927 | -0.13908 | 0.99409 | -0.11239 | 21.6834
88 | 0.0031409 | 0.00078683 | -0.0031408 | -0.00078685 | 2.0994e-08 | -1.9164e-08 | 0.0047099 | 0.0047099 | 0.0047099 | 0.99228 | -0.1471 | 0.99227 | -0.14724 | 1.2939
89 | 0.0058626 | 0.0014693 | -0.0058619 | -0.0014691 | 6.665e-07 | 1.2952e-07 | 0.0087912 | 0.0087913 | 0.0087913 | 0.99231 | -0.14646 | 0.99219 | -0.14885 | 2.4152
90 | 0.14408 | 0.036655 | -0.144 | -0.036604 | 8.1792e-05 | 5.1805e-05 | 0.21625 | 0.21625 | 0.21625 | 0.99231 | -0.14646 | 0.99169 | -0.15825 | 19.8033
91 | 0.0024721 | 0.00061926 | -0.0024721 | -0.00061934 | 4.2618e-08 | -7.9546e-08 | 0.0037071 | 0.0037071 | 0.0037071 | 0.99227 | -0.14724 | 0.99226 | -0.1476 | 1.0184
92 | 0.1336 | 0.033994 | -0.13348 | -0.033921 | 0.00011612 | 7.3423e-05 | 0.20064 | 0.20064 | 0.20064 | 0.99169 | -0.15825 | 0.99075 | -0.1763 | 18.3737
93 | 0.010404 | 0.0026091 | -0.0104 | -0.0026068 | 4.6426e-06 | 2.3162e-06 | 0.015612 | 0.015612 | 0.015612 | 0.99169 | -0.15825 | 0.99121 | -0.16761 | 4.2891
94 | 0.0099636 | 0.0024975 | -0.0099624 | -0.0024969 | 1.2051e-06 | 5.8613e-07 | 0.014958 | 0.014958 | 0.014958 | 0.99121 | -0.16761 | 0.99108 | -0.17015 | 4.1092
95 | 0.0093569 | 0.0023452 | -0.0093541 | -0.0023439 | 2.7592e-06 | 1.2856e-06 | 0.014049 | 0.014049 | 0.014049 | 0.99108 | -0.17015 | 0.99076 | -0.17634 | 3.8595
96 | 0.007843 | 0.0019651 | -0.0078411 | -0.0019644 | 1.8266e-06 | 7.1705e-07 | 0.011779 | 0.011779 | 0.011779 | 0.99076 | -0.17634 | 0.99051 | -0.18124 | 3.2361
97 | 0.13277 | 0.033744 | -0.13263 | -0.033655 | 0.00013952 | 8.8211e-05 | 0.19958 | 0.19958 | 0.19958 | 0.99075 | -0.1763 | 0.98962 | -0.19814 | 18.2763
98 | 0.0078411 | 0.0019644 | -0.0078404 | -0.0019641 | 7.6256e-07 | 2.9942e-07 | 0.011779 | 0.011779 | 0.011779 | 0.99051 | -0.18124 | 0.9904 | -0.18328 | 3.2361
99 | 0.13212 | 0.033527 | -0.13197 | -0.033433 | 0.00014774 | 9.4041e-05 | 0.19881 | 0.19881 | 0.19881 | 0.98962 | -0.19814 | 0.98841 | -0.22142 | 27.3087
100 | 0.10499 | 0.026657 | -0.10488 | -0.026587 | 0.00011019 | 6.9922e-05 | 0.15818 | 0.15818 | 0.15818 | 0.98841 | -0.22142 | 0.98728 | -0.24326 | 21.7279
101 | 0.026984 | 0.0067757 | -0.026976 | -0.0067706 | 8.1833e-06 | 5.0679e-06 | 0.040629 | 0.040629 | 0.040629 | 0.98841 | -0.22142 | 0.98808 | -0.22778 | 11.1617
102 | 0.0023086 | 0.00057832 | -0.0023085 | -0.00057857 | 1.094e-07 | -2.4865e-07 | 0.0034503 | 0.0034504 | 0.0034504 | 0.99561 | -0.08337 | 0.99556 | -0.084365 | 0.94791
103 | 0.0019091 | 0.00047823 | -0.001909 | -0.00047844 | 5.8974e-08 | -2.1009e-07 | 0.0028628 | 0.0028629 | 0.0028629 | 0.99226 | -0.1476 | 0.99222 | -0.14825 | 0.78651
104 | -0.037227 | -0.0093555 | 0.037252 | 0.0093713 | 2.5044e-05 | 1.5762e-05 | 0.056392 | 0.056392 | 0.056392 | 0.98246 | -0.3366 | 0.98318 | -0.32252 | 15.4922
105 | 0.034372 | 0.0086402 | -0.034354 | -0.0086285 | 1.8688e-05 | 1.1728e-05 | 0.052069 | 0.052069 | 0.052069 | 0.98246 | -0.3366 | 0.98188 | -0.34799 | 14.3047
106 | -0.038617 | -0.0097135 | 0.038631 | 0.0097222 | 1.3777e-05 | 8.6806e-06 | 0.058458 | 0.058458 | 0.058458 | 0.98318 | -0.32252 | 0.98357 | -0.31505 | 16.06
107 | 0.032551 | 0.0081767 | -0.032548 | -0.0081745 | 3.4788e-06 | 2.1783e-06 | 0.049337 | 0.049337 | 0.049337 | 0.98188 | -0.34799 | 0.98176 | -0.35023 | 13.5542
108 | 0.055744 | 0.014103 | -0.055696 | -0.014073 | 4.7575e-05 | 3.0222e-05 | 0.084381 | 0.084381 | 0.084381 | 0.98357 | -0.31505 | 0.98265 | -0.33286 | 23.1817
109 | -0.094375 | -0.023825 | 0.094447 | 0.023872 | 7.2304e-05 | 4.6155e-05 | 0.14284 | 0.14284 | 0.14284 | 0.98357 | -0.31505 | 0.98439 | -0.29907 | 39.2417
110 | 0.03123 | 0.0078442 | -0.031219 | -0.0078373 | 1.0978e-05 | 6.8611e-06 | 0.047339 | 0.047339 | 0.047339 | 0.98176 | -0.35023 | 0.98139 | -0.3576 | 13.0053
111 | -0.096597 | -0.02441 | 0.096672 | 0.024458 | 7.5596e-05 | 4.8261e-05 | 0.14609 | 0.14609 | 0.14609 | 0.98439 | -0.29907 | 0.98523 | -0.28276 | 40.1343
112 | 0.031219 | 0.0078373 | -0.031197 | -0.0078238 | 2.162e-05 | 1.3512e-05 | 0.047339 | 0.04734 | 0.04734 | 0.98139 | -0.3576 | 0.98065 | -0.37213 | 13.0054
113 | -0.097984 | -0.024787 | 0.098151 | 0.024894 | 0.00016673 | 0.00010645 | 0.14807 | 0.14807 | 0.14807 | 0.98523 | -0.28276 | 0.98706 | -0.24737 | 40.6785
114 | 0.011875 | 0.0029767 | -0.011873 | -0.0029754 | 2.3864e-06 | 1.2801e-06 | 0.01802 | 0.01802 | 0.01802 | 0.98065 | -0.37213 | 0.98043 | -0.37635 | 4.9505
115 | 0.019322 | 0.0048471 | -0.019319 | -0.0048455 | 2.6444e-06 | 1.5889e-06 | 0.02932 | 0.02932 | 0.02932 | 0.98065 | -0.37213 | 0.9805 | -0.375 | 8.0549
116 | -0.1008 | -0.025558 | 0.10082 | 0.02557 | 1.9901e-05 | 1.2707e-05 | 0.15206 | 0.15206 | 0.15206 | 0.98706 | -0.24737 | 0.98728 | -0.24326 | 41.7755
117 | 0.025077 | 0.0062946 | -0.025067 | -0.0062886 | 9.7836e-06 | 6.0274e-06 | 0.037768 | 0.037769 | 0.037769 | 0.98808 | -0.22778 | 0.98766 | -0.23596 | 10.376
118 | 0.022683 | 0.0056912 | -0.02268 | -0.0056895 | 2.7837e-06 | 1.7003e-06 | 0.034177 | 0.034177 | 0.034177 | 0.98766 | -0.23596 | 0.98753 | -0.23854 | 9.3893
119 | 0.0094554 | 0.0023695 | -0.0094552 | -0.0023695 | 1.4806e-07 | 7.058e-08 | 0.014351 | 0.014351 | 0.014351 | 0.98043 | -0.37635 | 0.98041 | -0.37668 | 3.9425
120 | 0.018156 | 0.0045541 | -0.018151 | -0.0045508 | 5.5502e-06 | 3.3064e-06 | 0.027556 | 0.027556 | 0.027556 | 0.9805 | -0.375 | 0.98017 | -0.38142 | 7.5703
121 | 0.016373 | 0.0041052 | -0.016369 | -0.0041033 | 3.2228e-06 | 1.8873e-06 | 0.024856 | 0.024856 | 0.024856 | 0.98017 | -0.38142 | 0.97996 | -0.38555 | 6.8287
122 | 0.014489 | 0.0036319 | -0.014487 | -0.0036312 | 1.2511e-06 | 7.1385e-07 | 0.022 | 0.022 | 0.022 | 0.97996 | -0.38555 | 0.97987 | -0.38736 | 6.0441
123 | 0.010647 | 0.0026687 | -0.010646 | -0.002668 | 1.4366e-06 | 7.3485e-07 | 0.016168 | 0.016168 | 0.016168 | 0.97987 | -0.38736 | 0.97972 | -0.39019 | 4.4419
124 | 0.0080943 | 0.0020284 | -0.0080925 | -0.0020276 | 1.7342e-06 | 7.2359e-07 | 0.012285 | 0.012285 | 0.012285 | 0.98041 | -0.37668 | 0.98018 | -0.38118 | 3.375
125 | 0.0095164 | 0.002385 | -0.0095164 | -0.0023849 | 5.2613e-08 | 2.5215e-08 | 0.014454 | 0.014454 | 0.014454 | 0.97972 | -0.39019 | 0.97972 | -0.39031 | 3.9708
126 | 0.0056421 | 0.0014135 | -0.0056421 | -0.0014135 | 2.2354e-09 | 4.0615e-10 | 0.0085651 | 0.0085651 | 0.0085651 | 0.98018 | -0.38118 | 0.98018 | -0.38119 | 2.3531
127 | 0.0058796 | 0.0014735 | -0.005879 | -0.0014734 | 6.3341e-07 | 1.3869e-07 | 0.0089301 | 0.0089302 | 0.0089302 | 0.97972 | -0.39031 | 0.9796 | -0.39257 | 2.4533
128 | -0.017685 | -0.0044347 | 0.017695 | 0.0044401 | 9.1397e-06 | 5.4348e-06 | 0.027038 | 0.027038 | 0.027038 | 0.97334 | -0.51526 | 0.97389 | -0.50442 | 7.428
129 | 0.013306 | 0.0033371 | -0.013305 | -0.0033365 | 1.1417e-06 | 6.3925e-07 | 0.020343 | 0.020343 | 0.020343 | 0.97334 | -0.51526 | 0.97325 | -0.51706 | 5.5887
130 | -0.020919 | -0.0052483 | 0.020941 | 0.0052618 | 2.2349e-05 | 1.3577e-05 | 0.031965 | 0.031964 | 0.031965 | 0.97389 | -0.50442 | 0.97502 | -0.48203 | 8.7815
131 | 0.013305 | 0.0033365 | -0.013303 | -0.0033353 | 2.0131e-06 | 1.1272e-06 | 0.020343 | 0.020343 | 0.020343 | 0.97325 | -0.51706 | 0.97309 | -0.52023 | 5.5887
132 | -0.020941 | -0.0052618 | 0.020956 | 0.0052705 | 1.4279e-05 | 8.6731e-06 | 0.031964 | 0.031964 | 0.031964 | 0.97502 | -0.48203 | 0.97575 | -0.46776 | 8.7814
133 | 0.0020371 | 0.00050831 | -0.002037 | -0.00050865 | 1.2239e-07 | -3.3965e-07 | 0.0031142 | 0.0031144 | 0.0031144 | 0.97309 | -0.52023 | 0.97302 | -0.5215 | 0.8556
134 | -0.020956 | -0.0052705 | 0.020961 | 0.0052738 | 5.3624e-06 | 3.2571e-06 | 0.031964 | 0.031964 | 0.031964 | 0.97575 | -0.46776 | 0.97602 | -0.4624 | 8.7814
135 | 0.002037 | 0.00050865 | -0.0020369 | -0.00050881 | 5.733e-08 | -1.5907e-07 | 0.0031144 | 0.0031145 | 0.0031145 | 0.97302 | -0.5215 | 0.97299 | -0.52209 | 0.85562
136 | 0.0012408 | 0.00030928 | -0.0012406 | -0.00031092 | 1.9191e-07 | -1.6427e-06 | 0.001897 | 0.0018976 | 0.0018976 | 0.97299 | -0.52209 | 0.97283 | -0.52534 | 0.52132
137 | -0.002723 | -0.00068244 | 0.002723 | 0.00068239 | 3.7301e-08 | -4.9322e-08 | 0.0041363 | 0.0041362 | 0.0041363 | 0.97959 | -0.39286 | 0.9796 | -0.39257 | 1.1363
138 | -0.0018132 | -0.00045417 | 0.0018132 | 0.00045397 | 5.4983e-08 | -1.996e-07 | 0.0027789 | 0.0027789 | 0.0027789 | 0.97085 | -0.56438 | 0.97089 | -0.56374 | 0.76344
139 | 0.0018132 | 0.00045417 | -0.0018131 | -0.00045441 | 6.5085e-08 | -2.3624e-07 | 0.0027789 | 0.002779 | 0.002779 | 0.97085 | -0.56438 | 0.97082 | -0.56513 | 0.76347
140 | 0.0043947 | 0.0011009 | -0.004394 | -0.001101 | 6.7835e-07 | -7.8046e-08 | 0.0066714 | 0.0066716 | 0.0066716 | 0.98018 | -0.38119 | 0.98002 | -0.38443 | 1.8328
141 | 0.0031335 | 0.00078505 | -0.0031334 | -0.00078521 | 1.8644e-07 | -1.574e-07 | 0.0047577 | 0.0047578 | 0.0047578 | 0.98002 | -0.38443 | 0.97996 | -0.38568 | 1.3071
142 | 0.0017767 | 0.00044519 | -0.0017766 | -0.00044527 | 2.1117e-08 | -8.3965e-08 | 0.0026978 | 0.0026978 | 0.0026978 | 0.97996 | -0.38568 | 0.97994 | -0.38593 | 0.74115

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37262 | 0.094868

## res_load
| p_mw | q_mvar
0 | 0.0073015 | 0.0018299
1 | 0.0042904 | 0.0010753
2 | 0.0028565 | 0.00071591
3 | 0.0029753 | 0.00074567
4 | 0.0021915 | 0.00054925
5 | 0.0048992 | 0.0012279
6 | 0.063234 | 0.015848
7 | 0.0034265 | 0.00085876
8 | 0.001088 | 0.00027267
9 | 0.0038398 | 0.00096235
10 | 0.0035952 | 0.00090103
11 | 0.0027164 | 0.00068079
12 | 0.0036346 | 0.00091092
13 | 0.0020537 | 0.00051471
14 | 0.0019138 | 0.00047965
15 | 0.0015104 | 0.00037854
16 | 0.002215 | 0.00055513
17 | 0.0026728 | 0.00066988
18 | 0.01017 | 0.0025487
19 | 0.018767 | 0.0047035
20 | 0.013447 | 0.0033701
21 | 0.0025143 | 0.00063014
22 | 0.0027893 | 0.00069907
23 | 0.0025531 | 0.00063986
24 | 0.0018932 | 0.00047447
25 | 0.0031687 | 0.00079414
26 | 0.0021744 | 0.00054495
27 | 0.0043028 | 0.0010784
28 | 0.0020661 | 0.00051782
29 | 0.0019209 | 0.00048144
30 | 0.0022382 | 0.00056096
31 | 0.0012671 | 0.00031756
32 | 0.0012792 | 0.00032061
33 | 0.0012932 | 0.00032412
34 | 0.0025092 | 0.00062888
35 | 0.0015979 | 0.00040047
36 | 0.0013706 | 0.00034351
37 | 0.0006866 | 0.00017208
38 | 0.0042872 | 0.0010745
39 | 0.00099278 | 0.00024881
40 | 0.0031491 | 0.00078923
41 | 0.00091889 | 0.0002303
42 | 0.0035606 | 0.00089236
43 | 0.00074229 | 0.00018603
44 | 0.014228 | 0.0035659
45 | 0.0033785 | 0.00084674
46 | 0.001087 | 0.00027242
47 | 0.0017705 | 0.00044374
48 | 0.0051834 | 0.0012991
49 | 0.00082423 | 0.00020657
50 | 0.00042456 | 0.00010641
51 | 0.0016419 | 0.0004115
52 | 0.0010039 | 0.00025161
53 | 0.0027759 | 0.0006957
54 | 0.0026215 | 0.00065701
55 | 0.004128 | 0.0010346
56 | 0.00132 | 0.00033082
57 | 0.0012395 | 0.00031066
58 | 0.0018164 | 0.00045523
59 | 0.012899 | 0.0032328
60 | 0.0020638 | 0.00051723
61 | 0.0043165 | 0.0010818
62 | 0.00037164 | 9.3142e-05
63 | 0.0046685 | 0.00117
64 | 0.00066871 | 0.00016759
65 | 0.0058619 | 0.0014691
66 | 0.00043605 | 0.00010929
67 | 0.00060548 | 0.00015175
68 | 0.0015112 | 0.00037874
69 | 0.00070804 | 0.00017745
70 | 0.0005123 | 0.00012839
71 | 0.0014899 | 0.00037339
72 | 0.0012763 | 0.00031987
73 | 0.0023085 | 0.00057857
74 | 0.00056301 | 0.0001411
75 | 0.001909 | 0.00047844
76 | 0.0028542 | 0.00071533
77 | 0.0013656 | 0.00034225
78 | 0.0018025 | 0.00045176
79 | 0.0013181 | 0.00033036
80 | 0.0017094 | 0.00042842
81 | 0.0021494 | 0.00053869
82 | 0.0013118 | 0.00032876
83 | 0.0026488 | 0.00066385
84 | 0.0018993 | 0.00047601
85 | 0.0023838 | 0.00059744
86 | 0.0013444 | 0.00033693
87 | 0.004058 | 0.001017
88 | 0.0024177 | 0.00060592
89 | 0.0011624 | 0.00029133
90 | 0.0017782 | 0.00044567
91 | 0.0018809 | 0.0004714
92 | 0.0038404 | 0.00096249
93 | 0.001361 | 0.00034109
94 | 0.0011291 | 0.00028298
95 | 0.0024504 | 0.00061413
96 | 0.0036367 | 0.00091145
97 | 0.0043793 | 0.0010976
98 | 0.0032246 | 0.00080816
99 | 0.00079611 | 0.00019952
100 | 0.0043247 | 0.0010839
101 | 0.0012406 | 0.00031092
102 | 0.002723 | 0.00068244
103 | 0.003156 | 0.00079096
104 | 0.00049856 | 0.00012495
105 | 0.0018131 | 0.00045441
106 | 0.0012474 | 0.00031264
107 | 0.0012605 | 0.0003159
108 | 0.0013567 | 0.00034002
109 | 0.0017766 | 0.00044527

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1