## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2554-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2554-4_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2554-4_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2554-4_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2554-4_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2554-4_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2554-4_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2554-4_0_3_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_2554-4_0_3_node_114 | 0.4 | n |  | TRUE
9 | bus_LV_2554-4_0_3_node_137 | 0.4 | n |  | TRUE
10 | bus_LV_2554-4_0_3_node_149 | 0.4 | n |  | TRUE
11 | bus_LV_2554-4_0_3_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_2554-4_0_3_node_130 | 0.4 | n |  | TRUE
13 | bus_LV_2554-4_0_3_node_113 | 0.4 | n |  | TRUE
14 | bus_LV_2554-4_0_3_node_72 | 0.4 | n |  | TRUE
15 | bus_LV_2554-4_0_3_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2554-4_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2554-4_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2554-4_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2554-4_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2554-4_0_3_node_37 | 0.4 | n |  | TRUE
21 | bus_LV_2554-4_0_3_node_38 | 0.4 | n |  | TRUE
22 | bus_LV_2554-4_0_3_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_2554-4_0_3_node_138 | 0.4 | n |  | TRUE
24 | bus_LV_2554-4_0_3_node_105 | 0.4 | n |  | TRUE
25 | bus_LV_2554-4_0_3_node_128 | 0.4 | n |  | TRUE
26 | bus_LV_2554-4_0_3_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_2554-4_0_3_node_139 | 0.4 | n |  | TRUE
28 | bus_LV_2554-4_0_3_node_140 | 0.4 | n |  | TRUE
29 | bus_LV_2554-4_0_3_node_12 | 0.4 | n |  | TRUE
30 | bus_LV_2554-4_0_3_node_13 | 0.4 | n |  | TRUE
31 | bus_LV_2554-4_0_3_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_2554-4_0_3_node_82 | 0.4 | n |  | TRUE
33 | bus_LV_2554-4_0_3_node_83 | 0.4 | n |  | TRUE
34 | bus_LV_2554-4_0_3_node_84 | 0.4 | n |  | TRUE
35 | bus_LV_2554-4_0_3_node_85 | 0.4 | n |  | TRUE
36 | bus_LV_2554-4_0_3_node_16 | 0.4 | n |  | TRUE
37 | bus_LV_2554-4_0_3_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_2554-4_0_3_node_116 | 0.4 | n |  | TRUE
39 | bus_LV_2554-4_0_3_node_17 | 0.4 | n |  | TRUE
40 | bus_LV_2554-4_0_3_node_150 | 0.4 | n |  | TRUE
41 | bus_LV_2554-4_0_3_node_110 | 0.4 | n |  | TRUE
42 | bus_LV_2554-4_0_3_node_18 | 0.4 | n |  | TRUE
43 | bus_LV_2554-4_0_3_node_109 | 0.4 | n |  | TRUE
44 | bus_LV_2554-4_0_3_node_108 | 0.4 | n |  | TRUE
45 | bus_LV_2554-4_0_3_node_146 | 0.4 | n |  | TRUE
46 | bus_LV_2554-4_0_3_node_21 | 0.4 | n |  | TRUE
47 | bus_LV_2554-4_0_3_node_99 | 0.4 | n |  | TRUE
48 | bus_LV_2554-4_0_3_node_97 | 0.4 | n |  | TRUE
49 | bus_LV_2554-4_0_3_node_106 | 0.4 | n |  | TRUE
50 | bus_LV_2554-4_0_3_node_143 | 0.4 | n |  | TRUE
51 | bus_LV_2554-4_0_3_node_29 | 0.4 | n |  | TRUE
52 | bus_LV_2554-4_0_3_node_98 | 0.4 | n |  | TRUE
53 | bus_LV_2554-4_0_3_node_71 | 0.4 | n |  | TRUE
54 | bus_LV_2554-4_0_3_node_117 | 0.4 | n |  | TRUE
55 | bus_LV_2554-4_0_3_node_48 | 0.4 | n |  | TRUE
56 | bus_LV_2554-4_0_3_node_134 | 0.4 | n |  | TRUE
57 | bus_LV_2554-4_0_3_node_135 | 0.4 | n |  | TRUE
58 | bus_LV_2554-4_0_3_node_133 | 0.4 | n |  | TRUE
59 | bus_LV_2554-4_0_3_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_2554-4_0_3_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_2554-4_0_3_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_2554-4_0_3_node_41 | 0.4 | n |  | TRUE
63 | bus_LV_2554-4_0_3_node_47 | 0.4 | n |  | TRUE
64 | bus_LV_2554-4_0_3_node_26 | 0.4 | n |  | TRUE
65 | bus_LV_2554-4_0_3_node_25 | 0.4 | n |  | TRUE
66 | bus_LV_2554-4_0_3_node_60 | 0.4 | n |  | TRUE
67 | bus_LV_2554-4_0_3_node_56 | 0.4 | n |  | TRUE
68 | bus_LV_2554-4_0_3_node_142 | 0.4 | n |  | TRUE
69 | bus_LV_2554-4_0_3_node_156 | 0.4 | n |  | TRUE
70 | bus_LV_2554-4_0_3_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_2554-4_0_3_node_122 | 0.4 | n |  | TRUE
72 | bus_LV_2554-4_0_3_node_27 | 0.4 | n |  | TRUE
73 | bus_LV_2554-4_0_3_node_28 | 0.4 | n |  | TRUE
74 | bus_LV_2554-4_0_3_node_30 | 0.4 | n |  | TRUE
75 | bus_LV_2554-4_0_3_node_32 | 0.4 | n |  | TRUE
76 | bus_LV_2554-4_0_3_node_31 | 0.4 | n |  | TRUE
77 | bus_LV_2554-4_0_3_node_157 | 0.4 | n |  | TRUE
78 | bus_LV_2554-4_0_3_node_158 | 0.4 | n |  | TRUE
79 | bus_LV_2554-4_0_3_node_34 | 0.4 | n |  | TRUE
80 | bus_LV_2554-4_0_3_node_66 | 0.4 | n |  | TRUE
81 | bus_LV_2554-4_0_3_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_2554-4_0_3_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_2554-4_0_3_node_153 | 0.4 | n |  | TRUE
84 | bus_LV_2554-4_0_3_node_159 | 0.4 | n |  | TRUE
85 | bus_LV_2554-4_0_3_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_2554-4_0_3_node_74 | 0.4 | n |  | TRUE
87 | bus_LV_2554-4_0_3_node_121 | 0.4 | n |  | TRUE
88 | bus_LV_2554-4_0_3_node_39 | 0.4 | n |  | TRUE
89 | bus_LV_2554-4_0_3_node_40 | 0.4 | n |  | TRUE
90 | bus_LV_2554-4_0_3_node_76 | 0.4 | n |  | TRUE
91 | bus_LV_2554-4_0_3_node_86 | 0.4 | n |  | TRUE
92 | bus_LV_2554-4_0_3_node_107 | 0.4 | n |  | TRUE
93 | bus_LV_2554-4_0_3_node_151 | 0.4 | n |  | TRUE
94 | bus_LV_2554-4_0_3_node_126 | 0.4 | n |  | TRUE
95 | bus_LV_2554-4_0_3_node_55 | 0.4 | n |  | TRUE
96 | bus_LV_2554-4_0_3_node_42 | 0.4 | n |  | TRUE
97 | bus_LV_2554-4_0_3_node_44 | 0.4 | n |  | TRUE
98 | bus_LV_2554-4_0_3_node_49 | 0.4 | n |  | TRUE
99 | bus_LV_2554-4_0_3_node_141 | 0.4 | n |  | TRUE
100 | bus_LV_2554-4_0_3_node_68 | 0.4 | n |  | TRUE
101 | bus_LV_2554-4_0_3_node_70 | 0.4 | n |  | TRUE
102 | bus_LV_2554-4_0_3_node_67 | 0.4 | n |  | TRUE
103 | bus_LV_2554-4_0_3_node_145 | 0.4 | n |  | TRUE
104 | bus_LV_2554-4_0_3_node_51 | 0.4 | n |  | TRUE
105 | bus_LV_2554-4_0_3_node_52 | 0.4 | n |  | TRUE
106 | bus_LV_2554-4_0_3_node_54 | 0.4 | n |  | TRUE
107 | bus_LV_2554-4_0_3_node_111 | 0.4 | n |  | TRUE
108 | bus_LV_2554-4_0_3_node_124 | 0.4 | n |  | TRUE
109 | bus_LV_2554-4_0_3_node_154 | 0.4 | n |  | TRUE
110 | bus_LV_2554-4_0_3_node_58 | 0.4 | n |  | TRUE
111 | bus_LV_2554-4_0_3_node_123 | 0.4 | n |  | TRUE
112 | bus_LV_2554-4_0_3_node_64 | 0.4 | n |  | TRUE
113 | bus_LV_2554-4_0_3_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_2554-4_0_3_node_119 | 0.4 | n |  | TRUE
115 | bus_LV_2554-4_0_3_node_101 | 0.4 | n |  | TRUE
116 | bus_LV_2554-4_0_3_node_61 | 0.4 | n |  | TRUE
117 | bus_LV_2554-4_0_3_node_62 | 0.4 | n |  | TRUE
118 | bus_LV_2554-4_0_3_node_63 | 0.4 | n |  | TRUE
119 | bus_LV_2554-4_0_3_node_69 | 0.4 | n |  | TRUE
120 | bus_LV_2554-4_0_3_node_77 | 0.4 | n |  | TRUE
121 | bus_LV_2554-4_0_3_node_78 | 0.4 | n |  | TRUE
122 | bus_LV_2554-4_0_3_node_79 | 0.4 | n |  | TRUE
123 | bus_LV_2554-4_0_3_node_80 | 0.4 | n |  | TRUE
124 | bus_LV_2554-4_0_3_node_81 | 0.4 | n |  | TRUE
125 | bus_LV_2554-4_0_3_node_96 | 0.4 | n |  | TRUE
126 | bus_LV_2554-4_0_3_node_147 | 0.4 | n |  | TRUE
127 | bus_LV_2554-4_0_3_node_89 | 0.4 | n |  | TRUE
128 | bus_LV_2554-4_0_3_node_90 | 0.4 | n |  | TRUE
129 | bus_LV_2554-4_0_3_node_87 | 0.4 | n |  | TRUE
130 | bus_LV_2554-4_0_3_node_144 | 0.4 | n |  | TRUE
131 | bus_LV_2554-4_0_3_node_88 | 0.4 | n |  | TRUE
132 | bus_LV_2554-4_0_3_node_91 | 0.4 | n |  | TRUE
133 | bus_LV_2554-4_0_3_node_92 | 0.4 | n |  | TRUE
134 | bus_LV_2554-4_0_3_node_93 | 0.4 | n |  | TRUE
135 | bus_LV_2554-4_0_3_node_94 | 0.4 | n |  | TRUE
136 | bus_LV_2554-4_0_3_node_95 | 0.4 | n |  | TRUE
137 | bus_LV_2554-4_0_3_node_136 | 0.4 | n |  | TRUE
138 | bus_LV_2554-4_0_3_node_148 | 0.4 | n |  | TRUE
139 | bus_LV_2554-4_0_3_node_104 | 0.4 | n |  | TRUE
140 | bus_LV_2554-4_0_3_node_100 | 0.4 | n |  | TRUE
141 | bus_LV_2554-4_0_3_node_102 | 0.4 | n |  | TRUE
142 | bus_LV_2554-4_0_3_node_120 | 0.4 | n |  | TRUE
143 | bus_LV_2554-4_0_3_node_155 | 0.4 | n |  | TRUE
144 | bus_LV_2554-4_0_3_node_112 | 0.4 | n |  | TRUE
145 | bus_LV_2554-4_0_3_node_115 | 0.4 | n |  | TRUE
146 | bus_LV_2554-4_0_3_node_131 | 0.4 | n |  | TRUE
147 | bus_LV_2554-4_0_3_node_132 | 0.4 | n |  | TRUE
148 | bus_LV_2554-4_0_3_node_118 | 0.4 | n |  | TRUE
149 | bus_LV_2554-4_0_3_node_125 | 0.4 | n |  | TRUE
150 | bus_LV_2554-4_0_3_node_127 | 0.4 | n |  | TRUE
151 | bus_LV_2554-4_0_3_node_152 | 0.4 | n |  | TRUE
152 | bus_MV_292_0_node_172 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2554-4_0_3_load_0 | 0 | 0.0019709 | 0.00049396 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2554-4_0_3_load_3 | 3 | 0.0015463 | 0.00038755 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2554-4_0_3_load_4 | 4 | 0.0034969 | 0.00087642 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2554-4_0_3_load_6 | 6 | 0.0010442 | 0.00026171 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2554-4_0_3_load_23 | 7 | 0.0016412 | 0.00041131 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2554-4_0_3_load_137 | 9 | 0.0018255 | 0.00045751 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2554-4_0_3_load_149 | 10 | 0.0020628 | 0.00051698 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2554-4_0_3_load_130 | 12 | 0.0042015 | 0.001053 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2554-4_0_3_load_7 | 15 | 0.0019108 | 0.0004789 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2554-4_0_3_load_8 | 16 | 0.0025651 | 0.00064288 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2554-4_0_3_load_9 | 17 | 0.0013015 | 0.00032619 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2554-4_0_3_load_11 | 19 | 0.0030292 | 0.00075918 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2554-4_0_3_load_37 | 20 | 0.0024674 | 0.00061838 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2554-4_0_3_load_38 | 21 | 0.0026446 | 0.0006628 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2554-4_0_3_load_35 | 22 | 0.002996 | 0.00075087 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2554-4_0_3_load_139 | 27 | 0.0012702 | 0.00031835 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2554-4_0_3_load_140 | 28 | 0.0020144 | 0.00050485 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2554-4_0_3_load_12 | 29 | 0.00186 | 0.00046616 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2554-4_0_3_load_13 | 30 | 0.0021 | 0.00052631 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2554-4_0_3_load_82 | 32 | 0.0021365 | 0.00053546 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2554-4_0_3_load_83 | 33 | 0.0028327 | 0.00070994 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2554-4_0_3_load_84 | 34 | 0.0034943 | 0.00087575 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2554-4_0_3_load_85 | 35 | 0.0012222 | 0.00030631 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2554-4_0_3_load_116 | 38 | 0.003411 | 0.00085487 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2554-4_0_3_load_150 | 40 | 0.0065221 | 0.0016346 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2554-4_0_3_load_110 | 41 | 0.013632 | 0.0034164 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2554-4_0_3_load_109 | 43 | 0.0089942 | 0.0022542 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2554-4_0_3_load_108 | 44 | 0.0063336 | 0.0015873 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2554-4_0_3_load_146 | 45 | 0.0051006 | 0.0012783 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2554-4_0_3_load_97 | 48 | 0.0042138 | 0.0010561 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2554-4_0_3_load_106 | 49 | 0.002646 | 0.00066315 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2554-4_0_3_load_117 | 54 | 0.0015554 | 0.00038981 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2554-4_0_3_load_134 | 56 | 0.0018544 | 0.00046476 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2554-4_0_3_load_135 | 57 | 0.015232 | 0.0038175 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2554-4_0_3_load_133 | 58 | 0.00080239 | 0.0002011 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2554-4_0_3_load_45 | 60 | 0.0026382 | 0.00066119 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2554-4_0_3_load_46 | 61 | 0.0029485 | 0.00073896 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2554-4_0_3_load_41 | 62 | 0.0013569 | 0.00034006 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2554-4_0_3_load_26 | 64 | 0.0012364 | 0.00030987 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2554-4_0_3_load_56 | 67 | 0.0019949 | 0.00049996 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2554-4_0_3_load_142 | 68 | 0.00098212 | 0.00024614 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2554-4_0_3_load_156 | 69 | 0.0090236 | 0.0022615 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2554-4_0_3_load_122 | 71 | 0.0022375 | 0.00056077 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2554-4_0_3_load_27 | 72 | 0.0069865 | 0.001751 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2554-4_0_3_load_30 | 74 | 0.0069088 | 0.0017315 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2554-4_0_3_load_157 | 77 | 0.0060116 | 0.0015067 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2554-4_0_3_load_66 | 80 | 0.010051 | 0.0025191 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2554-4_0_3_load_65 | 81 | 0.0094954 | 0.0023798 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2554-4_0_3_load_153 | 83 | 0.002525 | 0.00063282 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2554-4_0_3_load_159 | 84 | 0.0060196 | 0.0015087 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2554-4_0_3_load_73 | 85 | 0.006465 | 0.0016203 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2554-4_0_3_load_74 | 86 | 0.0048241 | 0.001209 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2554-4_0_3_load_121 | 87 | 0.0026605 | 0.00066679 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2554-4_0_3_load_39 | 88 | 0.0036176 | 0.00090666 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2554-4_0_3_load_40 | 89 | 0.0032389 | 0.00081175 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2554-4_0_3_load_76 | 90 | 0.0048324 | 0.0012111 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2554-4_0_3_load_86 | 91 | 0.0011491 | 0.00028798 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2554-4_0_3_load_107 | 92 | 0.0018458 | 0.00046261 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2554-4_0_3_load_151 | 93 | 0.0027493 | 0.00068905 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2554-4_0_3_load_55 | 95 | 0.0010913 | 0.0002735 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2554-4_0_3_load_42 | 96 | 0.0083776 | 0.0020996 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2554-4_0_3_load_44 | 97 | 0.0035536 | 0.00089063 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2554-4_0_3_load_141 | 99 | 0.0056027 | 0.0014042 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2554-4_0_3_load_70 | 101 | 0.0069296 | 0.0017367 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2554-4_0_3_load_67 | 102 | 0.0026313 | 0.00065948 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2554-4_0_3_load_145 | 103 | 0.0026749 | 0.00067039 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2554-4_0_3_load_51 | 104 | 0.0011656 | 0.00029213 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2554-4_0_3_load_52 | 105 | 0.0014897 | 0.00037335 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2554-4_0_3_load_54 | 106 | 0.0024193 | 0.00060633 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2554-4_0_3_load_154 | 109 | 0.0005577 | 0.00013977 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2554-4_0_3_load_123 | 111 | 0.0021961 | 0.0005504 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2554-4_0_3_load_119 | 114 | 0.00075797 | 0.00018996 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2554-4_0_3_load_61 | 116 | 0.0013704 | 0.00034346 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2554-4_0_3_load_62 | 117 | 0.001377 | 0.00034511 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2554-4_0_3_load_63 | 118 | 0.0031402 | 0.00078702 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2554-4_0_3_load_69 | 119 | 0.0075024 | 0.0018803 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2554-4_0_3_load_77 | 120 | 0.002299 | 0.00057619 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2554-4_0_3_load_78 | 121 | 0.0013846 | 0.000347 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2554-4_0_3_load_79 | 122 | 0.001773 | 0.00044435 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2554-4_0_3_load_80 | 123 | 0.0015463 | 0.00038754 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2554-4_0_3_load_96 | 125 | 0.002352 | 0.00058945 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2554-4_0_3_load_147 | 126 | 0.00091644 | 0.00022968 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2554-4_0_3_load_90 | 128 | 0.00070103 | 0.00017569 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2554-4_0_3_load_87 | 129 | 0.0033842 | 0.00084817 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2554-4_0_3_load_88 | 131 | 0.0029437 | 0.00073775 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2554-4_0_3_load_91 | 132 | 0.0025589 | 0.00064132 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2554-4_0_3_load_92 | 133 | 0.00076429 | 0.00019155 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2554-4_0_3_load_93 | 134 | 0.0014634 | 0.00036676 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2554-4_0_3_load_94 | 135 | 0.0018165 | 0.00045525 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2554-4_0_3_load_95 | 136 | 0.0010718 | 0.00026862 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2554-4_0_3_load_136 | 137 | 0.0022939 | 0.00057491 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2554-4_0_3_load_148 | 138 | 0.0017326 | 0.00043423 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2554-4_0_3_load_100 | 140 | 0.0016437 | 0.00041195 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2554-4_0_3_load_102 | 141 | 0.001496 | 0.00037494 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2554-4_0_3_load_120 | 142 | 0.00096772 | 0.00024253 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2554-4_0_3_load_155 | 143 | 0.0025465 | 0.00063822 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2554-4_0_3_load_112 | 144 | 0.0052943 | 0.0013269 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2554-4_0_3_load_115 | 145 | 0.0053816 | 0.0013487 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2554-4_0_3_load_132 | 147 | 0.0051781 | 0.0012977 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2554-4_0_3_load_118 | 148 | 0.0021188 | 0.00053102 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2554-4_0_3_load_125 | 149 | 0.0025017 | 0.00062699 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2554-4_0_3_load_127 | 150 | 0.0012284 | 0.00030787 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2554-4_0_3_load_152 | 151 | 0.0037485 | 0.00093945 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 74 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2554-4_0_3_line_0 |  | 0 | 1 | 0.014651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2554-4_0_3_line_1 |  | 0 | 2 | 0.013035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2554-4_0_3_line_2 |  | 1 | 3 | 0.028234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2554-4_0_3_line_3 |  | 1 | 4 | 0.018567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2554-4_0_3_line_4 |  | 2 | 5 | 0.016535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2554-4_0_3_line_5 |  | 2 | 6 | 0.010705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2554-4_0_3_line_6 |  | 3 | 7 | 0.00090128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2554-4_0_3_line_7 |  | 4 | 8 | 0.0072153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2554-4_0_3_line_8 |  | 5 | 9 | 0.014111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2554-4_0_3_line_9 |  | 6 | 10 | 0.0093804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2554-4_0_3_line_10 |  | 7 | 11 | 0.010914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2554-4_0_3_line_11 |  | 8 | 12 | 0.024392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2554-4_0_3_line_12 |  | 8 | 13 | 0.021501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2554-4_0_3_line_13 |  | 9 | 14 | 0.040493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2554-4_0_3_line_14 |  | 11 | 64 | 0.02081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2554-4_0_3_line_15 |  | 12 | 146 | 0.028415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2554-4_0_3_line_16 |  | 13 | 145 | 0.038138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2554-4_0_3_line_17 |  | 13 | 144 | 0.025458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2554-4_0_3_line_18 |  | 14 | 100 | 0.024809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2554-4_0_3_line_19 |  | 15 | 16 | 0.022957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2554-4_0_3_line_20 |  | 15 | 17 | 0.0020018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2554-4_0_3_line_21 |  | 16 | 18 | 0.029799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2554-4_0_3_line_22 |  | 17 | 19 | 0.016844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2554-4_0_3_line_23 |  | 18 | 20 | 0.022594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2554-4_0_3_line_24 |  | 18 | 21 | 0.021362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2554-4_0_3_line_25 |  | 18 | 22 | 0.034316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2554-4_0_3_line_26 |  | 19 | 23 | 0.0090018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2554-4_0_3_line_27 |  | 20 | 24 | 0.016511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2554-4_0_3_line_28 |  | 21 | 25 | 0.015202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2554-4_0_3_line_29 |  | 22 | 26 | 0.037177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2554-4_0_3_line_30 |  | 23 | 27 | 0.049964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2554-4_0_3_line_31 |  | 23 | 28 | 0.0097568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2554-4_0_3_line_32 |  | 24 | 49 | 0.0044397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_2554-4_0_3_line_33 |  | 24 | 92 | 0.030262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2554-4_0_3_line_34 |  | 25 | 93 | 0.027568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2554-4_0_3_line_35 |  | 25 | 94 | 0.014155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2554-4_0_3_line_36 |  | 26 | 88 | 0.024642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2554-4_0_3_line_37 |  | 26 | 89 | 0.018972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2554-4_0_3_line_38 |  | 28 | 137 | 0.018369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2554-4_0_3_line_39 |  | 29 | 30 | 0.034103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2554-4_0_3_line_40 |  | 30 | 31 | 0.021905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2554-4_0_3_line_41 |  | 31 | 32 | 0.02757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2554-4_0_3_line_42 |  | 31 | 33 | 0.023833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2554-4_0_3_line_43 |  | 31 | 34 | 0.048805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2554-4_0_3_line_44 |  | 31 | 35 | 0.020939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2554-4_0_3_line_45 |  | 32 | 49 | 0.03254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2554-4_0_3_line_46 |  | 33 | 50 | 0.05088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_2554-4_0_3_line_47 |  | 35 | 51 | 0.038553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_2554-4_0_3_line_48 |  | 36 | 37 | 0.020196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2554-4_0_3_line_49 |  | 36 | 38 | 0.012925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2554-4_0_3_line_50 |  | 37 | 45 | 0.011535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2554-4_0_3_line_51 |  | 37 | 39 | 0.014189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2554-4_0_3_line_52 |  | 38 | 54 | 0.016342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2554-4_0_3_line_53 |  | 39 | 40 | 0.007379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2554-4_0_3_line_54 |  | 39 | 41 | 0.0233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2554-4_0_3_line_55 |  | 41 | 47 | 0.001913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2554-4_0_3_line_56 |  | 42 | 43 | 0.023849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2554-4_0_3_line_57 |  | 42 | 44 | 0.0093415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2554-4_0_3_line_58 |  | 44 | 47 | 0.035362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2554-4_0_3_line_59 |  | 45 | 50 | 0.028739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_2554-4_0_3_line_60 |  | 46 | 47 | 0.035656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2554-4_0_3_line_61 |  | 46 | 48 | 0.030068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2554-4_0_3_line_62 |  | 48 | 52 | 0.035936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2554-4_0_3_line_63 |  | 50 | 130 | 0.026187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2554-4_0_3_line_64 |  | 51 | 75 | 0.058671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2554-4_0_3_line_65 |  | 51 | 73 | 0.012206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_2554-4_0_3_line_66 |  | 52 | 53 | 0.013037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2554-4_0_3_line_67 |  | 53 | 103 | 0.0034786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2554-4_0_3_line_68 |  | 53 | 63 | 0.072657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2554-4_0_3_line_69 |  | 54 | 148 | 0.00037952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2554-4_0_3_line_70 |  | 55 | 56 | 0.029777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2554-4_0_3_line_71 |  | 55 | 57 | 0.039091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2554-4_0_3_line_72 |  | 55 | 58 | 0.019657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2554-4_0_3_line_73 |  | 56 | 63 | 0.023557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2554-4_0_3_line_74 |  | 59 | 60 | 0.038973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2554-4_0_3_line_75 |  | 59 | 61 | 0.023207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2554-4_0_3_line_76 |  | 59 | 62 | 0.017235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2554-4_0_3_line_77 |  | 60 | 63 | 0.032037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2554-4_0_3_line_78 |  | 62 | 96 | 0.013271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2554-4_0_3_line_79 |  | 64 | 68 | 0.0056096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2554-4_0_3_line_80 |  | 65 | 66 | 0.014621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2554-4_0_3_line_81 |  | 65 | 67 | 0.019473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2554-4_0_3_line_82 |  | 66 | 69 | 0.021974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2554-4_0_3_line_83 |  | 67 | 70 | 0.016577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2554-4_0_3_line_84 |  | 68 | 71 | 0.014617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2554-4_0_3_line_85 |  | 70 | 110 | 0.032277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2554-4_0_3_line_86 |  | 71 | 112 | 0.014994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2554-4_0_3_line_87 |  | 72 | 73 | 0.015307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2554-4_0_3_line_88 |  | 73 | 74 | 0.015971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2554-4_0_3_line_89 |  | 75 | 80 | 0.021601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2554-4_0_3_line_90 |  | 75 | 81 | 0.044358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2554-4_0_3_line_91 |  | 76 | 77 | 0.021481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2554-4_0_3_line_92 |  | 76 | 78 | 0.018519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2554-4_0_3_line_93 |  | 76 | 79 | 0.063543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2554-4_0_3_line_94 |  | 78 | 84 | 0.001539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2554-4_0_3_line_95 |  | 79 | 82 | 0.034305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2554-4_0_3_line_96 |  | 79 | 83 | 0.018055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2554-4_0_3_line_97 |  | 82 | 86 | 0.016549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2554-4_0_3_line_98 |  | 83 | 87 | 0.028101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2554-4_0_3_line_99 |  | 85 | 86 | 0.034168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2554-4_0_3_line_100 |  | 87 | 142 | 0.017171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2554-4_0_3_line_101 |  | 88 | 90 | 0.031207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2554-4_0_3_line_102 |  | 89 | 91 | 0.031739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2554-4_0_3_line_103 |  | 91 | 95 | 0.023914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2554-4_0_3_line_104 |  | 92 | 143 | 0.038336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2554-4_0_3_line_105 |  | 94 | 149 | 0.020665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2554-4_0_3_line_106 |  | 96 | 97 | 0.031979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2554-4_0_3_line_107 |  | 97 | 98 | 0.016747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2554-4_0_3_line_108 |  | 98 | 99 | 0.022173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2554-4_0_3_line_109 |  | 100 | 101 | 0.016324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2554-4_0_3_line_110 |  | 100 | 102 | 0.013552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2554-4_0_3_line_111 |  | 102 | 119 | 0.030671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2554-4_0_3_line_112 |  | 104 | 105 | 0.022085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2554-4_0_3_line_113 |  | 105 | 106 | 0.03732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2554-4_0_3_line_114 |  | 106 | 107 | 0.014679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2554-4_0_3_line_115 |  | 107 | 108 | 0.046977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2554-4_0_3_line_116 |  | 107 | 109 | 0.015386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2554-4_0_3_line_117 |  | 108 | 139 | 0.028559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2554-4_0_3_line_118 |  | 108 | 125 | 0.01632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2554-4_0_3_line_119 |  | 110 | 111 | 0.039916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2554-4_0_3_line_120 |  | 111 | 112 | 0.017314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2554-4_0_3_line_121 |  | 112 | 117 | 0.017976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2554-4_0_3_line_122 |  | 113 | 114 | 0.013354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2554-4_0_3_line_123 |  | 113 | 115 | 0.03873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2554-4_0_3_line_124 |  | 114 | 142 | 0.024949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2554-4_0_3_line_125 |  | 115 | 139 | 0.034684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2554-4_0_3_line_126 |  | 115 | 140 | 0.039316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2554-4_0_3_line_127 |  | 116 | 117 | 0.0086928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2554-4_0_3_line_128 |  | 116 | 118 | 0.022708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2554-4_0_3_line_129 |  | 120 | 121 | 0.019553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2554-4_0_3_line_130 |  | 120 | 122 | 0.021384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2554-4_0_3_line_131 |  | 121 | 123 | 0.015648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2554-4_0_3_line_132 |  | 122 | 124 | 0.010445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2554-4_0_3_line_133 |  | 123 | 125 | 0.004872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2554-4_0_3_line_134 |  | 124 | 126 | 0.004223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2554-4_0_3_line_135 |  | 124 | 127 | 0.004405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2554-4_0_3_line_136 |  | 127 | 128 | 0.013453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2554-4_0_3_line_137 |  | 127 | 129 | 0.053639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2554-4_0_3_line_138 |  | 128 | 131 | 0.012434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2554-4_0_3_line_139 |  | 130 | 151 | 0.024029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2554-4_0_3_line_140 |  | 130 | 147 | 0.0021414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2554-4_0_3_line_141 |  | 132 | 133 | 0.018782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2554-4_0_3_line_142 |  | 132 | 134 | 0.017119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2554-4_0_3_line_143 |  | 133 | 135 | 0.014977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2554-4_0_3_line_144 |  | 134 | 136 | 0.017937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2554-4_0_3_line_145 |  | 135 | 137 | 0.026756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2554-4_0_3_line_146 |  | 136 | 138 | 0.015211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2554-4_0_3_line_147 |  | 138 | 139 | 0.014922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2554-4_0_3_line_148 |  | 140 | 141 | 0.04467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2554-4_0_3_line_149 |  | 146 | 147 | 0.0042969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2554-4_0_3_line_150 |  | 149 | 150 | 0.0015875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2554-4_0_3_trafo_30 | 0.63 MVA 20/0.4 kV | 152 | 74 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2609710.002 | 1231124.1597 | 2609713.76 | 1231109.9984
1 | 2609717.1034 | 1231097.3996 | 2609713.76 | 1231109.9984
2 | 2609710.002 | 1231124.1597 | 2609705.2614 | 1231124.1075 | 2609695.8709 | 1231124.1923 | 2609685.602 | 1231124.1757 | 2609681.7761 | 1231123.9444
3 | 2609710.002 | 1231124.1597 | 2609715.0977 | 1231124.6794 | 2609722.4265 | 1231125.8031 | 2609728.3516 | 1231126.924
4 | 2609717.1034 | 1231097.3996 | 2609721.8698 | 1231081.5646
5 | 2609717.1034 | 1231097.3996 | 2609706.9215 | 1231094.0945
6 | 2609680.8764 | 1231123.89 | 2609681.7761 | 1231123.9444
7 | 2609735.3564 | 1231128.6369 | 2609730.4286 | 1231127.317 | 2609728.3516 | 1231126.924
8 | 2609721.8698 | 1231081.5646 | 2609726.2688 | 1231068.1563
9 | 2609697.9993 | 1231091.1983 | 2609706.9215 | 1231094.0945
10 | 2609670.0038 | 1231122.9609 | 2609677.0985 | 1231123.6616 | 2609680.8764 | 1231123.89
11 | 2609735.3564 | 1231128.6369 | 2609740.1781 | 1231130.0456 | 2609758.404 | 1231136.6007
12 | 2609735.3564 | 1231128.6369 | 2609729.9231 | 1231149.4405
13 | 2609755.8569 | 1231044.6867 | 2609755.1071 | 1231044.741 | 2609751.0469 | 1231045.3681 | 2609745.6221 | 1231046.938 | 2609740.8629 | 1231048.9982 | 2609736.6023 | 1231051.7818 | 2609733.5006 | 1231054.4116 | 2609731.5731 | 1231056.8544 | 2609729.0216 | 1231061.1417 | 2609727.1669 | 1231065.4191 | 2609726.2688 | 1231068.1563
14 | 2609670.0038 | 1231122.9609 | 2609667.8529 | 1231118.388 | 2609666.7724 | 1231116.8409 | 2609656.9716 | 1231107.0268
15 | 2609785.1423 | 1231146.2175 | 2609758.404 | 1231136.6007
16 | 2609729.9231 | 1231149.4405 | 2609732.0302 | 1231152.9683 | 2609736.3699 | 1231157.3446 | 2609737.1556 | 1231158.4688 | 2609738.1823 | 1231160.4383 | 2609739.2109 | 1231161.2627 | 2609741.9354 | 1231162.3344 | 2609760.9918 | 1231168.4953
17 | 2609729.9231 | 1231149.4405 | 2609728.35 | 1231152.8289 | 2609726.6645 | 1231155.5055 | 2609725.7087 | 1231156.4934 | 2609724.3817 | 1231157.5475 | 2609723.2381 | 1231157.6012 | 2609709.5082 | 1231153.4438
18 | 2609755.8569 | 1231044.6867 | 2609759.0379 | 1231044.4584 | 2609752.8555 | 1231060.1355 | 2609757.3361 | 1231061.766
19 | 2609710.3411 | 1231306.988 | 2609713.6397 | 1231309.0207 | 2609721.4859 | 1231313.1693 | 2609726.5939 | 1231315.3344 | 2609731.006 | 1231316.8325
20 | 2609710.3411 | 1231306.988 | 2609708.6369 | 1231305.9377
21 | 2609759.9988 | 1231323.4937 | 2609745.6754 | 1231320.9911 | 2609736.168 | 1231318.5853 | 2609731.006 | 1231316.8325
22 | 2609694.3215 | 1231297.0634 | 2609695.4607 | 1231297.8179 | 2609708.6369 | 1231305.9377
23 | 2609759.9988 | 1231323.4937 | 2609770.3268 | 1231303.3982
24 | 2609759.9988 | 1231323.4937 | 2609781.0027 | 1231327.3862
25 | 2609759.9988 | 1231323.4937 | 2609758.1537 | 1231326.5481 | 2609745.042 | 1231351.853 | 2609744.2086 | 1231353.9408
26 | 2609686.6322 | 1231292.4003 | 2609690.1428 | 1231294.296 | 2609694.3215 | 1231297.0634
27 | 2609777.8741 | 1231288.7132 | 2609770.3268 | 1231303.3982
28 | 2609795.9505 | 1231330.1564 | 2609781.0027 | 1231327.3862
29 | 2609737.5806 | 1231390.4973 | 2609743.0551 | 1231358.2758 | 2609743.8711 | 1231354.7862 | 2609744.2086 | 1231353.9408
30 | 2609686.6322 | 1231292.4003 | 2609675.8023 | 1231330.4056 | 2609672.4049 | 1231340.2831
31 | 2609686.6322 | 1231292.4003 | 2609680.0485 | 1231289.5547 | 2609677.6083 | 1231288.7035
32 | 2609777.8741 | 1231288.7132 | 2609779.9701 | 1231284.7994
33 | 2609777.8741 | 1231288.7132 | 2609807.5264 | 1231294.757
34 | 2609820.6853 | 1231324.0155 | 2609810.4727 | 1231322.2199 | 2609807.8146 | 1231322.2489 | 2609805.08 | 1231322.8114 | 2609802.67 | 1231323.9415 | 2609795.9505 | 1231330.1564
35 | 2609795.9505 | 1231330.1564 | 2609809.9179 | 1231332.6919
36 | 2609737.5806 | 1231390.4973 | 2609761.9018 | 1231394.462
37 | 2609737.5806 | 1231390.4973 | 2609718.9096 | 1231387.1289
38 | 2609677.6083 | 1231288.7035 | 2609674.9247 | 1231287.7675 | 2609666.4023 | 1231284.9965 | 2609660.0589 | 1231283.305
39 | 2609828.5122 | 1231237.0902 | 2609861.423 | 1231246.0281
40 | 2609807.373 | 1231231.3493 | 2609828.5122 | 1231237.0902
41 | 2609807.373 | 1231231.3493 | 2609803.3889 | 1231241.0708 | 2609795.3328 | 1231256.1136
42 | 2609807.373 | 1231231.3493 | 2609810.0552 | 1231221.2587 | 2609811.3219 | 1231215.3795 | 2609812.2602 | 1231208.061
43 | 2609807.373 | 1231231.3493 | 2609812.4238 | 1231236.116 | 2609843.8355 | 1231263.7857
44 | 2609807.373 | 1231231.3493 | 2609804.4818 | 1231230.3551 | 2609787.599 | 1231224.4618
45 | 2609795.3328 | 1231256.1136 | 2609779.9701 | 1231284.7994
46 | 2609815.8927 | 1231157.3189 | 2609812.8254 | 1231203.6527 | 2609812.2602 | 1231208.061
47 | 2609751.1998 | 1231211.7569 | 2609760.6301 | 1231215.052 | 2609772.3537 | 1231219.1402 | 2609787.599 | 1231224.4618
48 | 2609853.2172 | 1231172.4449 | 2609872.2288 | 1231179.4137
49 | 2609872.2288 | 1231179.4137 | 2609869.4386 | 1231192.0344
50 | 2609853.2172 | 1231172.4449 | 2609842.508 | 1231168.1579
51 | 2609853.2172 | 1231172.4449 | 2609854.1989 | 1231169.5336 | 2609857.7528 | 1231158.9998
52 | 2609869.4386 | 1231192.0344 | 2609865.911 | 1231207.9907
53 | 2609857.7528 | 1231158.9998 | 2609850.8355 | 1231156.3758
54 | 2609857.7528 | 1231158.9998 | 2609860.4472 | 1231159.927 | 2609878.0541 | 1231149.525
55 | 2609879.7011 | 1231148.552 | 2609878.0541 | 1231149.525
56 | 2609905.6747 | 1231176.8786 | 2609907.9832 | 1231177.5717 | 2609927.0767 | 1231167.8215
57 | 2609905.6747 | 1231176.8786 | 2609898.5983 | 1231174.332 | 2609899.1608 | 1231172.6002
58 | 2609879.7011 | 1231148.552 | 2609894.8534 | 1231158.3718 | 2609901.5364 | 1231165.287 | 2609899.1608 | 1231172.6002
59 | 2609815.8927 | 1231157.3189 | 2609825.8593 | 1231161.4933 | 2609842.508 | 1231168.1579
60 | 2609879.7011 | 1231148.552 | 2609886.1065 | 1231144.7714 | 2609891.1669 | 1231129.9709 | 2609893.4192 | 1231123.5041 | 2609895.2987 | 1231118.0929
61 | 2609895.2987 | 1231118.0929 | 2609867.1068 | 1231107.6385
62 | 2609833.4126 | 1231095.1438 | 2609867.1068 | 1231107.6385
63 | 2609815.8927 | 1231157.3189 | 2609791.197 | 1231148.4065
64 | 2609715.7621 | 1231228.4982 | 2609709.6062 | 1231223.3851 | 2609711.168 | 1231222.2536 | 2609712.6092 | 1231220.8218 | 2609722.7323 | 1231207.9083 | 2609724.681 | 1231206.3216 | 2609726.1059 | 1231205.6235 | 2609727.8332 | 1231205.1482 | 2609729.4767 | 1231205.0286 | 2609731.5587 | 1231205.3878 | 2609751.1998 | 1231211.7569
65 | 2609753.3397 | 1231199.7532 | 2609752.7684 | 1231201.7979 | 2609751.1998 | 1231211.7569
66 | 2609833.4126 | 1231095.1438 | 2609820.855 | 1231091.5099
67 | 2609820.855 | 1231091.5099 | 2609820.4411 | 1231094.9638
68 | 2609820.855 | 1231091.5099 | 2609821.6656 | 1231086.7306 | 2609824.0765 | 1231075.8614 | 2609825.2639 | 1231072.1611 | 2609826.7319 | 1231068.2723 | 2609828.199 | 1231064.9505 | 2609832.0736 | 1231057.3857 | 2609844.9336 | 1231038.3398 | 2609850.7917 | 1231031.2563 | 2609853.6748 | 1231028.0258
69 | 2609865.911 | 1231207.9907 | 2609865.8291 | 1231208.3613
70 | 2609898.6795 | 1231056.6172 | 2609894.9798 | 1231054.5098 | 2609875.3554 | 1231042.3924 | 2609873.2943 | 1231041.0591
71 | 2609898.6795 | 1231056.6172 | 2609911.776 | 1231064.0878 | 2609925.3266 | 1231071.6926 | 2609932.985 | 1231075.322
72 | 2609898.6795 | 1231056.6172 | 2609893.356 | 1231075.5394
73 | 2609853.6748 | 1231028.0258 | 2609860.7096 | 1231032.9181 | 2609873.2943 | 1231041.0591
74 | 2609799.2993 | 1230982.3981 | 2609814.5291 | 1230996.098 | 2609828.6396 | 1231008.0443
75 | 2609799.2993 | 1230982.3981 | 2609786.8247 | 1230997.32 | 2609784.6542 | 1231000.3871
76 | 2609799.2993 | 1230982.3981 | 2609786.765 | 1230970.5685
77 | 2609853.6748 | 1231028.0258 | 2609835.5152 | 1231013.8653 | 2609828.6396 | 1231008.0443
78 | 2609777.1978 | 1230961.3719 | 2609782.46 | 1230966.5055 | 2609786.765 | 1230970.5685
79 | 2609656.9716 | 1231107.0268 | 2609653.0077 | 1231103.0576
80 | 2609574.5109 | 1231117.1595 | 2609578.2065 | 1231103.0125
81 | 2609578.2065 | 1231103.0125 | 2609583.7465 | 1231084.3444
82 | 2609574.5109 | 1231117.1595 | 2609595.9112 | 1231122.408
83 | 2609588.4626 | 1231068.4526 | 2609583.7465 | 1231084.3444
84 | 2609653.0077 | 1231103.0576 | 2609642.6788 | 1231092.7147
85 | 2609597.2895 | 1231037.4038 | 2609588.4626 | 1231068.4526
86 | 2609634.2522 | 1231080.4889 | 2609636.4714 | 1231084.9952 | 2609638.9263 | 1231088.9571 | 2609642.6788 | 1231092.7147
87 | 2609753.3397 | 1231199.7532 | 2609759.5678 | 1231202.4094 | 2609768.099 | 1231202.6864
88 | 2609738.8855 | 1231193.6816 | 2609747.1749 | 1231195.4072 | 2609753.3397 | 1231199.7532
89 | 2609726.4059 | 1231244.6807 | 2609727.6766 | 1231240.9472 | 2609727.5198 | 1231239.5461 | 2609726.765 | 1231238.0217 | 2609725.3968 | 1231236.4964 | 2609715.7621 | 1231228.4982
90 | 2609715.7621 | 1231228.4982 | 2609740.5315 | 1231238.5556 | 2609757.1746 | 1231244.3551
91 | 2609676.9952 | 1231248.3584 | 2609668.537 | 1231247.9778 | 2609657.7813 | 1231244.7474 | 2609658.3294 | 1231242.9917
92 | 2609694.501 | 1231254.546 | 2609676.9952 | 1231248.3584
93 | 2609654.7119 | 1231208.7653 | 2609680.6804 | 1231217.2791 | 2609685.5469 | 1231219.0213 | 2609681.1524 | 1231229.7873 | 2609681.8736 | 1231233.3684 | 2609676.9952 | 1231248.3584
94 | 2609694.501 | 1231254.546 | 2609694.8896 | 1231253.0568
95 | 2609654.7119 | 1231208.7653 | 2609663.0564 | 1231185.7539 | 2609658.2005 | 1231182.1328 | 2609659.4406 | 1231178.5549
96 | 2609654.7119 | 1231208.7653 | 2609645.2432 | 1231205.7149 | 2609637.4633 | 1231203.4333
97 | 2609659.4406 | 1231178.5549 | 2609660.6047 | 1231175.1881 | 2609668.7846 | 1231179.1592 | 2609672.6783 | 1231179.1443
98 | 2609637.4633 | 1231203.4333 | 2609610.4976 | 1231195.5252
99 | 2609704.36 | 1231188.6201 | 2609695.4107 | 1231188.4856 | 2609679.008 | 1231179.1202 | 2609672.6783 | 1231179.1443
100 | 2609594.0209 | 1231190.6931 | 2609610.4976 | 1231195.5252
101 | 2609792.7018 | 1231399.4828 | 2609761.9018 | 1231394.462
102 | 2609718.9096 | 1231387.1289 | 2609687.6749 | 1231381.494
103 | 2609664.1405 | 1231377.2482 | 2609687.6749 | 1231381.494
104 | 2609807.5264 | 1231294.757 | 2609818.7304 | 1231297.0406 | 2609845.2111 | 1231301.7807
105 | 2609809.9179 | 1231332.6919 | 2609806.4964 | 1231350.3302 | 2609806.2875 | 1231353.0204
106 | 2609777.1978 | 1230961.3719 | 2609766.0676 | 1230950.5136 | 2609754.6225 | 1230938.7264
107 | 2609742.6594 | 1230927.017 | 2609747.9679 | 1230931.873 | 2609754.6225 | 1230938.7264
108 | 2609742.6594 | 1230927.017 | 2609727.1036 | 1230941.2891 | 2609726.0433 | 1230941.343
109 | 2609757.3361 | 1231061.766 | 2609751.427 | 1231076.9877
110 | 2609757.3361 | 1231061.766 | 2609770.0662 | 1231066.4144
111 | 2609778.6823 | 1231086.171 | 2609784.2193 | 1231071.5824 | 2609770.0662 | 1231066.4144
112 | 2609574.1694 | 1231336.4921 | 2609595.1978 | 1231343.2428
113 | 2609574.1694 | 1231336.4921 | 2609566.7501 | 1231334.1103 | 2609559.7181 | 1231332.2646 | 2609537.9829 | 1231327.4729
114 | 2609524.1109 | 1231323.0802 | 2609525.4272 | 1231323.9606 | 2609526.9935 | 1231324.7413 | 2609528.6811 | 1231325.4222 | 2609537.9829 | 1231327.4729
115 | 2609531.2321 | 1231278.5092 | 2609521.1873 | 1231313.9145 | 2609520.8808 | 1231316.2153 | 2609520.9767 | 1231317.8053 | 2609521.353 | 1231319.229 | 2609522.138 | 1231320.8646 | 2609523.0447 | 1231322.1001 | 2609524.1109 | 1231323.0802
116 | 2609524.1109 | 1231323.0802 | 2609524.3543 | 1231331.9192 | 2609524.4941 | 1231338.4613
117 | 2609538.5989 | 1231250.9155 | 2609531.2321 | 1231278.5092
118 | 2609531.2321 | 1231278.5092 | 2609546.9558 | 1231282.8823
119 | 2609597.2895 | 1231037.4038 | 2609601.5258 | 1231040.2789 | 2609603.2346 | 1231041.9605 | 2609620.3077 | 1231063.3006 | 2609623.177 | 1231067.4794
120 | 2609634.2522 | 1231080.4889 | 2609633.0643 | 1231079.8755 | 2609631.4757 | 1231078.7612 | 2609629.6083 | 1231076.8459 | 2609623.177 | 1231067.4794
121 | 2609634.2522 | 1231080.4889 | 2609636.3717 | 1231081.0816 | 2609640.256 | 1231081.477 | 2609645.6705 | 1231081.5857 | 2609647.9506 | 1231081.1781 | 2609650.2471 | 1231080.0144 | 2609651.4539 | 1231079.0189
122 | 2609557.2656 | 1231179.9139 | 2609570.0803 | 1231183.6721
123 | 2609557.2656 | 1231179.9139 | 2609547.1795 | 1231217.3091
124 | 2609570.0803 | 1231183.6721 | 2609594.0209 | 1231190.6931
125 | 2609538.5989 | 1231250.9155 | 2609547.1795 | 1231217.3091
126 | 2609547.1795 | 1231217.3091 | 2609585.2336 | 1231227.191
127 | 2609657.2459 | 1231072.582 | 2609654.6611 | 1231076.008 | 2609652.0898 | 1231078.4942 | 2609651.4539 | 1231079.0189
128 | 2609666.4378 | 1231052.1238 | 2609663.7866 | 1231061.8921 | 2609660.8691 | 1231067.7798 | 2609657.2459 | 1231072.582
129 | 2609585.5635 | 1231293.6198 | 2609566.7252 | 1231288.3805
130 | 2609585.5635 | 1231293.6198 | 2609606.1651 | 1231299.3495
131 | 2609566.7252 | 1231288.3805 | 2609551.6496 | 1231284.1877
132 | 2609616.2282 | 1231302.1482 | 2609606.1651 | 1231299.3495
133 | 2609551.6496 | 1231284.1877 | 2609546.9558 | 1231282.8823
134 | 2609615.2674 | 1231306.2602 | 2609616.2282 | 1231302.1482
135 | 2609616.2282 | 1231302.1482 | 2609620.4669 | 1231303.3891
136 | 2609620.4669 | 1231303.3891 | 2609633.3809 | 1231307.1577
137 | 2609620.4669 | 1231303.3891 | 2609611.6278 | 1231337.4731 | 2609629.4585 | 1231342.1257
138 | 2609633.3809 | 1231307.1577 | 2609645.3172 | 1231310.641
139 | 2609784.9418 | 1231171.5768 | 2609786.9798 | 1231161.7186 | 2609791.197 | 1231148.4065
140 | 2609791.197 | 1231148.4065 | 2609789.1832 | 1231147.6784
141 | 2609601.5868 | 1231267.7124 | 2609619.7351 | 1231272.5519
142 | 2609601.5868 | 1231267.7124 | 2609585.0459 | 1231263.3015
143 | 2609634.2061 | 1231276.4109 | 2609619.7351 | 1231272.5519
144 | 2609585.0459 | 1231263.3015 | 2609567.7142 | 1231258.6796
145 | 2609634.2061 | 1231276.4109 | 2609660.0589 | 1231283.305
146 | 2609553.0172 | 1231254.7604 | 2609567.7142 | 1231258.6796
147 | 2609538.5989 | 1231250.9155 | 2609553.0172 | 1231254.7604
148 | 2609628.4698 | 1231238.4186 | 2609585.2336 | 1231227.191
149 | 2609785.1423 | 1231146.2175 | 2609789.1832 | 1231147.6784
150 | 2609806.6485 | 1231354.5664 | 2609806.2875 | 1231353.0204

## bus_geodata
| x | y | coords
0 | 2609713.76 | 1231109.9984
1 | 2609710.002 | 1231124.1597
2 | 2609717.1034 | 1231097.3996
3 | 2609681.7761 | 1231123.9444
4 | 2609728.3516 | 1231126.924
5 | 2609721.8698 | 1231081.5646
6 | 2609706.9215 | 1231094.0945
7 | 2609680.8764 | 1231123.89
8 | 2609735.3564 | 1231128.6369
9 | 2609726.2688 | 1231068.1563
10 | 2609697.9993 | 1231091.1983
11 | 2609670.0038 | 1231122.9609
12 | 2609758.404 | 1231136.6007
13 | 2609729.9231 | 1231149.4405
14 | 2609755.8569 | 1231044.6867
15 | 2609710.3411 | 1231306.988
16 | 2609731.006 | 1231316.8325
17 | 2609708.6369 | 1231305.9377
18 | 2609759.9988 | 1231323.4937
19 | 2609694.3215 | 1231297.0634
20 | 2609770.3268 | 1231303.3982
21 | 2609781.0027 | 1231327.3862
22 | 2609744.2086 | 1231353.9408
23 | 2609686.6322 | 1231292.4003
24 | 2609777.8741 | 1231288.7132
25 | 2609795.9505 | 1231330.1564
26 | 2609737.5806 | 1231390.4973
27 | 2609672.4049 | 1231340.2831
28 | 2609677.6083 | 1231288.7035
29 | 2609861.423 | 1231246.0281
30 | 2609828.5122 | 1231237.0902
31 | 2609807.373 | 1231231.3493
32 | 2609795.3328 | 1231256.1136
33 | 2609812.2602 | 1231208.061
34 | 2609843.8355 | 1231263.7857
35 | 2609787.599 | 1231224.4618
36 | 2609872.2288 | 1231179.4137
37 | 2609853.2172 | 1231172.4449
38 | 2609869.4386 | 1231192.0344
39 | 2609857.7528 | 1231158.9998
40 | 2609850.8355 | 1231156.3758
41 | 2609878.0541 | 1231149.525
42 | 2609905.6747 | 1231176.8786
43 | 2609927.0767 | 1231167.8215
44 | 2609899.1608 | 1231172.6002
45 | 2609842.508 | 1231168.1579
46 | 2609895.2987 | 1231118.0929
47 | 2609879.7011 | 1231148.552
48 | 2609867.1068 | 1231107.6385
49 | 2609779.9701 | 1231284.7994
50 | 2609815.8927 | 1231157.3189
51 | 2609751.1998 | 1231211.7569
52 | 2609833.4126 | 1231095.1438
53 | 2609820.855 | 1231091.5099
54 | 2609865.911 | 1231207.9907
55 | 2609898.6795 | 1231056.6172
56 | 2609873.2943 | 1231041.0591
57 | 2609932.985 | 1231075.322
58 | 2609893.356 | 1231075.5394
59 | 2609799.2993 | 1230982.3981
60 | 2609828.6396 | 1231008.0443
61 | 2609784.6542 | 1231000.3871
62 | 2609786.765 | 1230970.5685
63 | 2609853.6748 | 1231028.0258
64 | 2609656.9716 | 1231107.0268
65 | 2609578.2065 | 1231103.0125
66 | 2609574.5109 | 1231117.1595
67 | 2609583.7465 | 1231084.3444
68 | 2609653.0077 | 1231103.0576
69 | 2609595.9112 | 1231122.408
70 | 2609588.4626 | 1231068.4526
71 | 2609642.6788 | 1231092.7147
72 | 2609768.099 | 1231202.6864
73 | 2609753.3397 | 1231199.7532
74 | 2609738.8855 | 1231193.6816
75 | 2609715.7621 | 1231228.4982
76 | 2609676.9952 | 1231248.3584
77 | 2609658.3294 | 1231242.9917
78 | 2609694.501 | 1231254.546
79 | 2609654.7119 | 1231208.7653
80 | 2609726.4059 | 1231244.6807
81 | 2609757.1746 | 1231244.3551
82 | 2609659.4406 | 1231178.5549
83 | 2609637.4633 | 1231203.4333
84 | 2609694.8896 | 1231253.0568
85 | 2609704.36 | 1231188.6201
86 | 2609672.6783 | 1231179.1443
87 | 2609610.4976 | 1231195.5252
88 | 2609761.9018 | 1231394.462
89 | 2609718.9096 | 1231387.1289
90 | 2609792.7018 | 1231399.4828
91 | 2609687.6749 | 1231381.494
92 | 2609807.5264 | 1231294.757
93 | 2609820.6853 | 1231324.0155
94 | 2609809.9179 | 1231332.6919
95 | 2609664.1405 | 1231377.2482
96 | 2609777.1978 | 1230961.3719
97 | 2609754.6225 | 1230938.7264
98 | 2609742.6594 | 1230927.017
99 | 2609726.0433 | 1230941.343
100 | 2609757.3361 | 1231061.766
101 | 2609751.427 | 1231076.9877
102 | 2609770.0662 | 1231066.4144
103 | 2609820.4411 | 1231094.9638
104 | 2609595.1978 | 1231343.2428
105 | 2609574.1694 | 1231336.4921
106 | 2609537.9829 | 1231327.4729
107 | 2609524.1109 | 1231323.0802
108 | 2609531.2321 | 1231278.5092
109 | 2609524.4941 | 1231338.4613
110 | 2609597.2895 | 1231037.4038
111 | 2609623.177 | 1231067.4794
112 | 2609634.2522 | 1231080.4889
113 | 2609557.2656 | 1231179.9139
114 | 2609570.0803 | 1231183.6721
115 | 2609547.1795 | 1231217.3091
116 | 2609657.2459 | 1231072.582
117 | 2609651.4539 | 1231079.0189
118 | 2609666.4378 | 1231052.1238
119 | 2609778.6823 | 1231086.171
120 | 2609585.5635 | 1231293.6198
121 | 2609566.7252 | 1231288.3805
122 | 2609606.1651 | 1231299.3495
123 | 2609551.6496 | 1231284.1877
124 | 2609616.2282 | 1231302.1482
125 | 2609546.9558 | 1231282.8823
126 | 2609615.2674 | 1231306.2602
127 | 2609620.4669 | 1231303.3891
128 | 2609633.3809 | 1231307.1577
129 | 2609629.4585 | 1231342.1257
130 | 2609791.197 | 1231148.4065
131 | 2609645.3172 | 1231310.641
132 | 2609601.5868 | 1231267.7124
133 | 2609619.7351 | 1231272.5519
134 | 2609585.0459 | 1231263.3015
135 | 2609634.2061 | 1231276.4109
136 | 2609567.7142 | 1231258.6796
137 | 2609660.0589 | 1231283.305
138 | 2609553.0172 | 1231254.7605
139 | 2609538.5989 | 1231250.9155
140 | 2609585.2336 | 1231227.191
141 | 2609628.4698 | 1231238.4186
142 | 2609594.0209 | 1231190.6931
143 | 2609845.2111 | 1231301.7807
144 | 2609709.5082 | 1231153.4438
145 | 2609760.9918 | 1231168.4953
146 | 2609785.1423 | 1231146.2175
147 | 2609789.1832 | 1231147.6784
148 | 2609865.8291 | 1231208.3613
149 | 2609806.2875 | 1231353.0204
150 | 2609806.6485 | 1231354.5664
151 | 2609784.9418 | 1231171.5768
152 | 2609753.3397 | 1231199.7532

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97895 | -0.40418 | 0.0019709 | 0.00049396
1 | 0.97927 | -0.3978 | 0 | 0
2 | 0.97868 | -0.4094 | 0 | 0
3 | 0.97857 | -0.41154 | 0.0015463 | 0.00038755
4 | 0.98015 | -0.38069 | 0.0034969 | 0.00087642
5 | 0.97839 | -0.41509 | 0 | 0
6 | 0.97865 | -0.41001 | 0.0010442 | 0.00026171
7 | 0.97855 | -0.41195 | 0.0016412 | 0.00041131
8 | 0.98051 | -0.3736 | 0 | 0
9 | 0.97814 | -0.41994 | 0.0018255 | 0.00045751
10 | 0.97863 | -0.41036 | 0.0020628 | 0.00051698
11 | 0.97831 | -0.41663 | 0 | 0
12 | 0.98198 | -0.34494 | 0.0042015 | 0.001053
13 | 0.9803 | -0.37776 | 0 | 0
14 | 0.9775 | -0.43254 | 0 | 0
15 | 0.98665 | -0.25436 | 0.0019108 | 0.0004789
16 | 0.9872 | -0.24374 | 0.0025651 | 0.00064288
17 | 0.98651 | -0.25708 | 0.0013015 | 0.00032619
18 | 0.98794 | -0.22952 | 0 | 0
19 | 0.98534 | -0.27953 | 0.0030292 | 0.00075918
20 | 0.98868 | -0.21525 | 0.0024674 | 0.00061838
21 | 0.98776 | -0.233 | 0.0026446 | 0.0006628
22 | 0.98741 | -0.2399 | 0.002996 | 0.00075087
23 | 0.98474 | -0.29106 | 0 | 0
24 | 0.98924 | -0.20459 | 0 | 0
25 | 0.98767 | -0.23476 | 0 | 0
26 | 0.98693 | -0.24917 | 0 | 0
27 | 0.98469 | -0.29221 | 0.0012702 | 0.00031835
28 | 0.98411 | -0.30336 | 0.0020144 | 0.00050485
29 | 0.99142 | -0.16273 | 0.00186 | 0.00046616
30 | 0.99148 | -0.16161 | 0.0021 | 0.00052631
31 | 0.99156 | -0.16007 | 0 | 0
32 | 0.99055 | -0.17929 | 0.0021365 | 0.00053546
33 | 0.99025 | -0.18515 | 0.0028327 | 0.00070994
34 | 0.9914 | -0.1631 | 0.0034943 | 0.00087575
35 | 0.99352 | -0.12264 | 0.0012222 | 0.00030631
36 | 0.98371 | -0.31124 | 0 | 0
37 | 0.98384 | -0.30866 | 0 | 0
38 | 0.98362 | -0.31289 | 0.003411 | 0.00085487
39 | 0.98272 | -0.33034 | 0 | 0
40 | 0.98267 | -0.33121 | 0.0065221 | 0.0016346
41 | 0.98102 | -0.3633 | 0.013632 | 0.0034164
42 | 0.98033 | -0.37688 | 0 | 0
43 | 0.98013 | -0.38077 | 0.0089942 | 0.0022542
44 | 0.98041 | -0.37536 | 0.0063336 | 0.0015873
45 | 0.98482 | -0.2896 | 0.0051006 | 0.0012783
46 | 0.97927 | -0.39741 | 0 | 0
47 | 0.98091 | -0.36553 | 0 | 0
48 | 0.97789 | -0.42437 | 0.0042138 | 0.0010561
49 | 0.98939 | -0.20161 | 0.002646 | 0.00066315
50 | 0.98612 | -0.2646 | 0 | 0
51 | 0.99715 | -0.053826 | 0 | 0
52 | 0.97638 | -0.45393 | 0 | 0
53 | 0.97583 | -0.46468 | 0 | 0
54 | 0.98357 | -0.31397 | 0.0015554 | 0.00038981
55 | 0.97212 | -0.53777 | 0 | 0
56 | 0.97256 | -0.52896 | 0.0018544 | 0.00046476
57 | 0.97156 | -0.54875 | 0.015232 | 0.0038175
58 | 0.9721 | -0.53806 | 0.00080239 | 0.0002011
59 | 0.97143 | -0.55136 | 0 | 0
60 | 0.97222 | -0.53565 | 0.0026382 | 0.00066119
61 | 0.97136 | -0.55263 | 0.0029485 | 0.00073896
62 | 0.97112 | -0.55738 | 0.0013569 | 0.00034006
63 | 0.97295 | -0.5212 | 0 | 0
64 | 0.97786 | -0.42557 | 0.0012364 | 0.00030987
65 | 0.9759 | -0.46405 | 0 | 0
66 | 0.97578 | -0.46646 | 0 | 0
67 | 0.97606 | -0.46083 | 0.0019949 | 0.00049996
68 | 0.97774 | -0.42785 | 0.00098212 | 0.00024614
69 | 0.97559 | -0.47009 | 0.0090236 | 0.0022615
70 | 0.97623 | -0.45749 | 0 | 0
71 | 0.97745 | -0.43354 | 0.0022375 | 0.00056077
72 | 0.99827 | -0.032624 | 0.0069865 | 0.001751
73 | 0.99837 | -0.030753 | 0 | 0
74 | 1 | 0 | -0.33852 | -0.086755
75 | 0.9961 | -0.073953 | 0 | 0
76 | 0.97026 | -0.57432 | 0 | 0
77 | 0.97014 | -0.57671 | 0.0060116 | 0.0015067
78 | 0.97016 | -0.57639 | 0 | 0
79 | 0.97097 | -0.56018 | 0 | 0
80 | 0.99591 | -0.077768 | 0.010051 | 0.0025191
81 | 0.99572 | -0.081356 | 0.0094954 | 0.0023798
82 | 0.97061 | -0.56734 | 0 | 0
83 | 0.97137 | -0.55239 | 0.002525 | 0.00063282
84 | 0.97015 | -0.57656 | 0.0060196 | 0.0015087
85 | 0.97023 | -0.57489 | 0.006465 | 0.0016203
86 | 0.97044 | -0.5708 | 0.0048241 | 0.001209
87 | 0.97205 | -0.53898 | 0.0026605 | 0.00066679
88 | 0.98674 | -0.25289 | 0.0036176 | 0.00090666
89 | 0.98684 | -0.25103 | 0.0032389 | 0.00081175
90 | 0.9866 | -0.25559 | 0.0048324 | 0.0012111
91 | 0.98677 | -0.2523 | 0.0011491 | 0.00028798
92 | 0.98911 | -0.20696 | 0.0018458 | 0.00046261
93 | 0.9876 | -0.23612 | 0.0027493 | 0.00068905
94 | 0.98762 | -0.2357 | 0 | 0
95 | 0.98675 | -0.25277 | 0.0010913 | 0.0002735
96 | 0.97091 | -0.56168 | 0.0083776 | 0.0020996
97 | 0.97063 | -0.5671 | 0.0035536 | 0.00089063
98 | 0.97054 | -0.56883 | 0 | 0
99 | 0.97043 | -0.57113 | 0.0056027 | 0.0014042
100 | 0.97711 | -0.44027 | 0 | 0
101 | 0.97701 | -0.44233 | 0.0069296 | 0.0017367
102 | 0.97698 | -0.44277 | 0.0026313 | 0.00065948
103 | 0.97582 | -0.46485 | 0.0026749 | 0.00067039
104 | 0.9747 | -0.48676 | 0.0011656 | 0.00029213
105 | 0.97473 | -0.48629 | 0.0014897 | 0.00037335
106 | 0.97482 | -0.48447 | 0.0024193 | 0.00060633
107 | 0.97489 | -0.4831 | 0 | 0
108 | 0.97513 | -0.47825 | 0 | 0
109 | 0.97488 | -0.48326 | 0.0005577 | 0.00013977
110 | 0.97656 | -0.45099 | 0 | 0
111 | 0.97697 | -0.44295 | 0.0021961 | 0.0005504
112 | 0.97719 | -0.43877 | 0 | 0
113 | 0.97357 | -0.50898 | 0 | 0
114 | 0.97319 | -0.51641 | 0.00075797 | 0.00018996
115 | 0.97466 | -0.48747 | 0 | 0
116 | 0.97705 | -0.44142 | 0.0013704 | 0.00034346
117 | 0.97709 | -0.4407 | 0.001377 | 0.00034511
118 | 0.97698 | -0.44272 | 0.0031402 | 0.00078702
119 | 0.97677 | -0.44698 | 0.0075024 | 0.0018803
120 | 0.97439 | -0.49293 | 0.002299 | 0.00057619
121 | 0.97461 | -0.48861 | 0.0013846 | 0.000347
122 | 0.9742 | -0.49674 | 0.001773 | 0.00044435
123 | 0.9748 | -0.48476 | 0.0015463 | 0.00038754
124 | 0.97412 | -0.49827 | 0 | 0
125 | 0.97487 | -0.48343 | 0.002352 | 0.00058945
126 | 0.97412 | -0.49834 | 0.00091644 | 0.00022968
127 | 0.97409 | -0.49884 | 0 | 0
128 | 0.97404 | -0.49974 | 0.00070103 | 0.00017569
129 | 0.97392 | -0.50217 | 0.0033842 | 0.00084817
130 | 0.98422 | -0.3013 | 0 | 0
131 | 0.97401 | -0.50041 | 0.0029437 | 0.00073775
132 | 0.97931 | -0.39654 | 0.0025589 | 0.00064132
133 | 0.98041 | -0.375 | 0.00076429 | 0.00019155
134 | 0.97834 | -0.41541 | 0.0014634 | 0.00036676
135 | 0.9813 | -0.35766 | 0.0018165 | 0.00045525
136 | 0.97735 | -0.43474 | 0.0010718 | 0.00026862
137 | 0.98294 | -0.32587 | 0.0022939 | 0.00057491
138 | 0.97653 | -0.45087 | 0.0017326 | 0.00043423
139 | 0.97574 | -0.46625 | 0 | 0
140 | 0.97455 | -0.48973 | 0.0016437 | 0.00041195
141 | 0.97449 | -0.49096 | 0.001496 | 0.00037494
142 | 0.9725 | -0.52996 | 0.00096772 | 0.00024253
143 | 0.98903 | -0.2087 | 0.0025465 | 0.00063822
144 | 0.98017 | -0.38021 | 0.0052943 | 0.0013269
145 | 0.98011 | -0.38148 | 0.0053816 | 0.0013487
146 | 0.9838 | -0.30951 | 0 | 0
147 | 0.98407 | -0.30416 | 0.0051781 | 0.0012977
148 | 0.98356 | -0.31399 | 0.0021188 | 0.00053102
149 | 0.98755 | -0.23708 | 0.0025017 | 0.00062699
150 | 0.98755 | -0.23712 | 0.0012284 | 0.00030787
151 | 0.98414 | -0.30292 | 0.0037485 | 0.00093945
152 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.024002 | -0.0060267 | 0.024009 | 0.0060312 | 7.3146e-06 | 4.4971e-06 | 0.036487 | 0.036487 | 0.036487 | 0.97895 | -0.40418 | 0.97927 | -0.3978 | 10.0239
1 | 0.022031 | 0.0055327 | -0.022025 | -0.0055294 | 5.4828e-06 | 3.3452e-06 | 0.033491 | 0.033491 | 0.033491 | 0.97895 | -0.40418 | 0.97868 | -0.4094 | 9.2009
2 | 0.026809 | 0.0067398 | -0.026791 | -0.0067289 | 1.7576e-05 | 1.0894e-05 | 0.040744 | 0.040744 | 0.040744 | 0.97927 | -0.3978 | 0.97857 | -0.41154 | 11.1935
3 | -0.050818 | -0.012771 | 0.05086 | 0.012797 | 4.1529e-05 | 2.6345e-05 | 0.077231 | 0.077231 | 0.077231 | 0.97927 | -0.3978 | 0.98015 | -0.38069 | 21.2174
4 | 0.018918 | 0.0047509 | -0.018913 | -0.0047478 | 5.1314e-06 | 3.0764e-06 | 0.028767 | 0.028767 | 0.028767 | 0.97868 | -0.4094 | 0.97839 | -0.41509 | 7.9031
5 | 0.0031071 | 0.00077851 | -0.003107 | -0.00077859 | 8.9588e-08 | -7.7177e-08 | 0.0047241 | 0.0047241 | 0.0047241 | 0.97868 | -0.4094 | 0.97865 | -0.41001 | 1.2978
6 | 0.025245 | 0.0063413 | -0.025245 | -0.006341 | 4.9819e-07 | 3.0752e-07 | 0.038393 | 0.038393 | 0.038393 | 0.97857 | -0.41154 | 0.97855 | -0.41195 | 10.5475
7 | -0.054357 | -0.013674 | 0.054375 | 0.013685 | 1.8434e-05 | 1.1707e-05 | 0.08254 | 0.08254 | 0.08254 | 0.98015 | -0.38069 | 0.98051 | -0.3736 | 22.6758
8 | 0.018913 | 0.0047478 | -0.018909 | -0.0047452 | 4.3793e-06 | 2.6256e-06 | 0.028767 | 0.028767 | 0.028767 | 0.97839 | -0.41509 | 0.97814 | -0.41994 | 7.9031
9 | 0.0020628 | 0.00051688 | -0.0020628 | -0.00051698 | 3.4604e-08 | -9.5718e-08 | 0.0031364 | 0.0031364 | 0.0031364 | 0.97865 | -0.41001 | 0.97863 | -0.41036 | 0.86166
10 | 0.023603 | 0.0059297 | -0.023598 | -0.0059265 | 5.274e-06 | 3.2383e-06 | 0.035897 | 0.035897 | 0.035897 | 0.97855 | -0.41195 | 0.97831 | -0.41663 | 9.8619
11 | -0.065055 | -0.016362 | 0.065144 | 0.016419 | 8.9193e-05 | 5.6776e-05 | 0.098747 | 0.098747 | 0.098747 | 0.98051 | -0.3736 | 0.98198 | -0.34494 | 27.1284
12 | 0.01068 | 0.0026769 | -0.010677 | -0.0026758 | 2.118e-06 | 1.0844e-06 | 0.016207 | 0.016208 | 0.016208 | 0.98051 | -0.3736 | 0.9803 | -0.37776 | 4.4526
13 | 0.017083 | 0.0042877 | -0.017073 | -0.0042816 | 1.0257e-05 | 6.0568e-06 | 0.02599 | 0.025991 | 0.025991 | 0.97814 | -0.41994 | 0.9775 | -0.43254 | 7.1403
14 | 0.023598 | 0.0059265 | -0.023588 | -0.0059203 | 1.0056e-05 | 6.1748e-06 | 0.035897 | 0.035897 | 0.035897 | 0.97831 | -0.41663 | 0.97786 | -0.42557 | 9.8619
15 | -0.069345 | -0.017472 | 0.069463 | 0.017547 | 0.00011773 | 7.4989e-05 | 0.10511 | 0.10511 | 0.10511 | 0.98198 | -0.34494 | 0.9838 | -0.30951 | 28.8774
16 | 0.0053825 | 0.0013489 | -0.0053816 | -0.0013487 | 9.547e-07 | 1.3027e-07 | 0.0081702 | 0.0081704 | 0.0081704 | 0.9803 | -0.37776 | 0.98011 | -0.38148 | 2.2446
17 | 0.005295 | 0.001327 | -0.0052943 | -0.0013269 | 6.1673e-07 | 7.3779e-08 | 0.0080373 | 0.0080374 | 0.0080374 | 0.9803 | -0.37776 | 0.98017 | -0.38021 | 2.2081
18 | 0.017073 | 0.0042816 | -0.017067 | -0.0042779 | 6.2846e-06 | 3.7113e-06 | 0.025991 | 0.025991 | 0.025991 | 0.9775 | -0.43254 | 0.97711 | -0.44027 | 7.1403
19 | -0.078374 | -0.019958 | 0.078414 | 0.019983 | 4.017e-05 | 2.4828e-05 | 0.11831 | 0.11831 | 0.11831 | 0.98665 | -0.25436 | 0.9872 | -0.24374 | 10.8345
20 | 0.076463 | 0.019479 | -0.076453 | -0.019472 | 1.0002e-05 | 6.376e-06 | 0.11543 | 0.11543 | 0.11543 | 0.98665 | -0.25436 | 0.98651 | -0.25708 | 31.7118
21 | -0.080979 | -0.020625 | 0.081035 | 0.02066 | 5.5603e-05 | 3.4442e-05 | 0.12218 | 0.12218 | 0.12218 | 0.9872 | -0.24374 | 0.98794 | -0.22952 | 11.1885
22 | 0.075152 | 0.019146 | -0.07507 | -0.019094 | 8.1323e-05 | 5.1832e-05 | 0.11347 | 0.11347 | 0.11347 | 0.98651 | -0.25708 | 0.98534 | -0.27953 | 31.1725
23 | -0.1071 | -0.027197 | 0.10718 | 0.027244 | 7.3613e-05 | 4.6244e-05 | 0.16144 | 0.16144 | 0.16144 | 0.98794 | -0.22952 | 0.98868 | -0.21525 | 14.7843
24 | 0.0091267 | 0.0022871 | -0.0091252 | -0.0022864 | 1.5137e-06 | 6.953e-07 | 0.013746 | 0.013746 | 0.013746 | 0.98794 | -0.22952 | 0.98776 | -0.233 | 3.7765
25 | 0.016943 | 0.0042504 | -0.016934 | -0.0042455 | 8.3811e-06 | 4.9247e-06 | 0.02552 | 0.02552 | 0.02552 | 0.98794 | -0.22952 | 0.98741 | -0.2399 | 7.0111
26 | 0.072041 | 0.018335 | -0.072001 | -0.01831 | 4.0028e-05 | 2.5503e-05 | 0.10889 | 0.10889 | 0.10889 | 0.98534 | -0.27953 | 0.98474 | -0.29106 | 29.9158
27 | -0.10965 | -0.027862 | 0.1097 | 0.027897 | 5.6297e-05 | 3.5394e-05 | 0.16516 | 0.16516 | 0.16516 | 0.98868 | -0.21525 | 0.98924 | -0.20459 | 15.1244
28 | 0.0064806 | 0.0016236 | -0.0064801 | -0.0016235 | 5.4334e-07 | 1.5316e-07 | 0.0097625 | 0.0097626 | 0.0097626 | 0.98776 | -0.233 | 0.98767 | -0.23476 | 2.682
29 | 0.013938 | 0.0034946 | -0.013932 | -0.0034911 | 6.1513e-06 | 3.4616e-06 | 0.021005 | 0.021005 | 0.021005 | 0.98741 | -0.2399 | 0.98693 | -0.24917 | 5.7707
30 | 0.0012703 | 0.00031776 | -0.0012702 | -0.00031835 | 6.9026e-08 | -5.9142e-07 | 0.0019193 | 0.0019195 | 0.0019195 | 0.98474 | -0.29106 | 0.98469 | -0.29221 | 0.52734
31 | 0.070731 | 0.017992 | -0.070689 | -0.017965 | 4.1869e-05 | 2.6672e-05 | 0.10697 | 0.10697 | 0.10697 | 0.98474 | -0.29106 | 0.98411 | -0.30336 | 29.3886
32 | -0.11409 | -0.028998 | 0.11411 | 0.029008 | 1.6373e-05 | 1.0308e-05 | 0.17177 | 0.17177 | 0.17177 | 0.98924 | -0.20459 | 0.98939 | -0.20161 | 15.7294
33 | 0.0043931 | 0.0011004 | -0.0043926 | -0.0011005 | 4.9552e-07 | -7.1332e-08 | 0.0066079 | 0.006608 | 0.006608 | 0.98924 | -0.20459 | 0.98911 | -0.20696 | 1.8154
34 | 0.0027495 | 0.00068881 | -0.0027493 | -0.00068905 | 1.7739e-07 | -2.3926e-07 | 0.0041423 | 0.0041424 | 0.0041424 | 0.98767 | -0.23476 | 0.9876 | -0.23612 | 1.138
35 | 0.0037306 | 0.00093466 | -0.0037304 | -0.00093473 | 1.6767e-07 | -7.3832e-08 | 0.0056203 | 0.0056204 | 0.0056204 | 0.98767 | -0.23476 | 0.98762 | -0.2357 | 1.5441
36 | 0.0084521 | 0.0021184 | -0.0084506 | -0.0021178 | 1.5007e-06 | 6.4561e-07 | 0.012744 | 0.012744 | 0.012744 | 0.98693 | -0.24917 | 0.98674 | -0.25289 | 3.501
37 | 0.0054799 | 0.0013727 | -0.0054794 | -0.0013726 | 4.8565e-07 | 6.8397e-08 | 0.0082619 | 0.008262 | 0.008262 | 0.98693 | -0.24917 | 0.98684 | -0.25103 | 2.2698
38 | 0.068674 | 0.01746 | -0.0686 | -0.017413 | 7.4401e-05 | 4.7384e-05 | 0.10393 | 0.10393 | 0.10393 | 0.98411 | -0.30336 | 0.98294 | -0.32587 | 28.5518
39 | -0.00186 | -0.00046616 | 0.0018601 | 0.00046578 | 9.966e-08 | -3.76e-07 | 0.0027916 | 0.0027915 | 0.0027916 | 0.99142 | -0.16273 | 0.99148 | -0.16161 | 0.76694
40 | -0.0039601 | -0.00099209 | 0.0039604 | 0.000992 | 2.9014e-07 | -9.6834e-08 | 0.0059432 | 0.0059431 | 0.0059432 | 0.99148 | -0.16161 | 0.99156 | -0.16007 | 1.6327
41 | 0.11913 | 0.030355 | -0.11902 | -0.030286 | 0.00011037 | 6.9569e-05 | 0.17895 | 0.17895 | 0.17895 | 0.99156 | -0.16007 | 0.99055 | -0.17929 | 16.3877
42 | 0.18005 | 0.045992 | -0.17983 | -0.045853 | 0.000218 | 0.0001386 | 0.27051 | 0.27051 | 0.27051 | 0.99156 | -0.16007 | 0.99025 | -0.18515 | 24.7717
43 | 0.0034948 | 0.00087545 | -0.0034943 | -0.00087575 | 5.034e-07 | -3.0725e-07 | 0.0052444 | 0.0052447 | 0.0052447 | 0.99156 | -0.16007 | 0.9914 | -0.1631 | 1.4408
44 | -0.30663 | -0.078215 | 0.30719 | 0.078569 | 0.0005554 | 0.00035464 | 0.46065 | 0.46065 | 0.46065 | 0.99156 | -0.16007 | 0.99352 | -0.12264 | 42.1838
45 | 0.11688 | 0.02975 | -0.11676 | -0.029671 | 0.00012563 | 7.9149e-05 | 0.17574 | 0.17574 | 0.17574 | 0.99055 | -0.17929 | 0.98939 | -0.20161 | 16.0939
46 | 0.177 | 0.045143 | -0.17632 | -0.044712 | 0.00067628 | 0.00043151 | 0.26625 | 0.26625 | 0.26625 | 0.99025 | -0.18515 | 0.98612 | -0.2646 | 36.5729
47 | -0.30841 | -0.078876 | 0.30944 | 0.079534 | 0.0010307 | 0.00065817 | 0.46248 | 0.46248 | 0.46248 | 0.99352 | -0.12264 | 0.99715 | -0.053826 | 42.3514
48 | -0.0070859 | -0.0017758 | 0.0070867 | 0.0017761 | 8.7009e-07 | 3.0043e-07 | 0.010719 | 0.010718 | 0.010719 | 0.98371 | -0.31124 | 0.98384 | -0.30866 | 2.9446
49 | 0.0070859 | 0.0017758 | -0.0070853 | -0.0017756 | 5.5686e-07 | 1.9232e-07 | 0.010719 | 0.010719 | 0.010719 | 0.98371 | -0.31124 | 0.98362 | -0.31289 | 2.9447
50 | -0.092463 | -0.023415 | 0.092548 | 0.023469 | 8.4704e-05 | 5.4064e-05 | 0.13993 | 0.13993 | 0.13993 | 0.98384 | -0.30866 | 0.98482 | -0.2896 | 38.4432
51 | 0.085376 | 0.021639 | -0.085287 | -0.021582 | 8.8843e-05 | 5.6679e-05 | 0.12921 | 0.12921 | 0.12921 | 0.98384 | -0.30866 | 0.98272 | -0.33034 | 35.4986
52 | 0.0036744 | 0.00092074 | -0.0036742 | -0.00092083 | 1.8934e-07 | -8.6234e-08 | 0.0055585 | 0.0055586 | 0.0055586 | 0.98362 | -0.31289 | 0.98357 | -0.31397 | 1.5271
53 | 0.0065224 | 0.0016347 | -0.0065221 | -0.0016346 | 2.699e-07 | 7.9247e-08 | 0.009876 | 0.0098761 | 0.0098761 | 0.98272 | -0.33034 | 0.98267 | -0.33121 | 2.7132
54 | 0.078765 | 0.019947 | -0.078641 | -0.019868 | 0.00012443 | 7.9344e-05 | 0.11934 | 0.11934 | 0.11934 | 0.98272 | -0.33034 | 0.98102 | -0.3633 | 32.7854
55 | 0.065009 | 0.016452 | -0.065002 | -0.016447 | 6.983e-06 | 4.445e-06 | 0.098663 | 0.098663 | 0.098663 | 0.98102 | -0.3633 | 0.98091 | -0.36553 | 27.1051
56 | 0.0089958 | 0.0022549 | -0.0089942 | -0.0022542 | 1.6675e-06 | 7.6658e-07 | 0.013655 | 0.013655 | 0.013655 | 0.98033 | -0.37688 | 0.98013 | -0.38077 | 3.7513
57 | -0.0089958 | -0.0022549 | 0.0089965 | 0.0022552 | 6.5314e-07 | 3.0022e-07 | 0.013655 | 0.013655 | 0.013655 | 0.98033 | -0.37688 | 0.98041 | -0.37536 | 3.7513
58 | -0.01533 | -0.0038426 | 0.015337 | 0.0038467 | 7.179e-06 | 4.1484e-06 | 0.023267 | 0.023267 | 0.023267 | 0.98041 | -0.37536 | 0.98091 | -0.36553 | 6.3921
59 | -0.097648 | -0.024747 | 0.097766 | 0.024822 | 0.00011746 | 7.4439e-05 | 0.14764 | 0.14764 | 0.14764 | 0.98482 | -0.2896 | 0.98612 | -0.2646 | 20.2802
60 | -0.049589 | -0.012552 | 0.049665 | 0.0126 | 7.6006e-05 | 4.8195e-05 | 0.075396 | 0.075395 | 0.075396 | 0.97927 | -0.39741 | 0.98091 | -0.36553 | 20.7131
61 | 0.049589 | 0.012552 | -0.049525 | -0.012512 | 6.4095e-05 | 4.0643e-05 | 0.075396 | 0.075396 | 0.075396 | 0.97927 | -0.39741 | 0.97789 | -0.42437 | 20.7131
62 | 0.045311 | 0.011456 | -0.045247 | -0.011415 | 6.413e-05 | 4.0593e-05 | 0.068984 | 0.068984 | 0.068984 | 0.97789 | -0.42437 | 0.97638 | -0.45393 | 18.9516
63 | 0.078556 | 0.01989 | -0.078418 | -0.019802 | 0.00013815 | 8.8086e-05 | 0.11861 | 0.11861 | 0.11861 | 0.98612 | -0.2646 | 0.98422 | -0.3013 | 32.5854
64 | 0.01957 | 0.0049125 | -0.019552 | -0.0049013 | 1.8769e-05 | 1.1247e-05 | 0.029207 | 0.029207 | 0.029207 | 0.99715 | -0.053826 | 0.9961 | -0.073953 | 8.024
65 | -0.32901 | -0.084446 | 0.32938 | 0.084682 | 0.00036885 | 0.00023559 | 0.49168 | 0.49168 | 0.49168 | 0.99715 | -0.053826 | 0.99837 | -0.030753 | 45.026
66 | 0.045247 | 0.011415 | -0.045223 | -0.0114 | 2.3265e-05 | 1.4727e-05 | 0.068984 | 0.068984 | 0.068984 | 0.97638 | -0.45393 | 0.97583 | -0.46468 | 18.9516
67 | 0.0026749 | 0.00067037 | -0.0026749 | -0.00067039 | 2.1703e-08 | -2.9567e-08 | 0.0040789 | 0.0040789 | 0.0040789 | 0.97583 | -0.46468 | 0.97582 | -0.46485 | 1.1206
68 | 0.042549 | 0.01073 | -0.042434 | -0.010657 | 0.00011478 | 7.2555e-05 | 0.064905 | 0.064905 | 0.064905 | 0.97583 | -0.46468 | 0.97295 | -0.5212 | 17.8312
69 | 0.0021188 | 0.00053102 | -0.0021188 | -0.00053102 | 1.4624e-09 | -3.8808e-09 | 0.0032055 | 0.0032055 | 0.0032055 | 0.98357 | -0.31397 | 0.98356 | -0.31399 | 0.88063
70 | -0.016043 | -0.004023 | 0.016049 | 0.004027 | 6.7338e-06 | 3.9403e-06 | 0.024557 | 0.024557 | 0.024557 | 0.97212 | -0.53777 | 0.97256 | -0.52896 | 6.7465
71 | 0.01524 | 0.0038222 | -0.015232 | -0.0038175 | 7.9782e-06 | 4.6217e-06 | 0.023329 | 0.023329 | 0.023329 | 0.97212 | -0.53777 | 0.97156 | -0.54875 | 6.4091
72 | 0.0008024 | 0.00020086 | -0.00080239 | -0.0002011 | 1.1119e-08 | -2.3658e-07 | 0.0012282 | 0.0012282 | 0.0012282 | 0.97212 | -0.53777 | 0.9721 | -0.53806 | 0.33743
73 | -0.017904 | -0.0044917 | 0.01791 | 0.0044957 | 6.6293e-06 | 3.9503e-06 | 0.027394 | 0.027394 | 0.027394 | 0.97256 | -0.52896 | 0.97295 | -0.5212 | 7.5259
74 | -0.021852 | -0.00548 | 0.021868 | 0.00549 | 1.6376e-05 | 9.9977e-06 | 0.033474 | 0.033474 | 0.033474 | 0.97143 | -0.55136 | 0.97222 | -0.53565 | 9.1961
75 | 0.0029487 | 0.00073879 | -0.0029485 | -0.00073896 | 1.7754e-07 | -1.7366e-07 | 0.0045166 | 0.0045167 | 0.0045167 | 0.97143 | -0.55136 | 0.97136 | -0.55263 | 1.2409
76 | 0.018903 | 0.0047412 | -0.018898 | -0.004738 | 5.4195e-06 | 3.2552e-06 | 0.028957 | 0.028957 | 0.028957 | 0.97143 | -0.55136 | 0.97112 | -0.55738 | 7.9553
77 | -0.024507 | -0.0061512 | 0.024523 | 0.0061616 | 1.6905e-05 | 1.0421e-05 | 0.037511 | 0.037511 | 0.037511 | 0.97222 | -0.53565 | 0.97295 | -0.5212 | 10.3053
78 | 0.017541 | 0.0043979 | -0.017537 | -0.0043958 | 3.5953e-06 | 2.1368e-06 | 0.026878 | 0.026878 | 0.026878 | 0.97112 | -0.55738 | 0.97091 | -0.56168 | 7.3841
79 | 0.022352 | 0.0056104 | -0.022349 | -0.0056089 | 2.4341e-06 | 1.4874e-06 | 0.034016 | 0.034016 | 0.034016 | 0.97786 | -0.42557 | 0.97774 | -0.42785 | 9.3451
80 | 0.0090262 | 0.0022627 | -0.0090251 | -0.0022622 | 1.0386e-06 | 4.8202e-07 | 0.013763 | 0.013763 | 0.013763 | 0.9759 | -0.46405 | 0.97578 | -0.46646 | 3.781
81 | -0.0090262 | -0.0022627 | 0.0090275 | 0.0022634 | 1.3832e-06 | 6.4189e-07 | 0.013763 | 0.013763 | 0.013763 | 0.9759 | -0.46405 | 0.97606 | -0.46083 | 3.781
82 | 0.0090251 | 0.0022622 | -0.0090236 | -0.0022615 | 1.5609e-06 | 7.2453e-07 | 0.013763 | 0.013763 | 0.013763 | 0.97578 | -0.46646 | 0.97559 | -0.47009 | 3.7811
83 | -0.011022 | -0.0027633 | 0.011024 | 0.0027642 | 1.7553e-06 | 9.1618e-07 | 0.016804 | 0.016804 | 0.016804 | 0.97606 | -0.46083 | 0.97623 | -0.45749 | 4.6165
84 | 0.021367 | 0.0053628 | -0.021361 | -0.0053593 | 5.7974e-06 | 3.5271e-06 | 0.032521 | 0.032521 | 0.032521 | 0.97774 | -0.42785 | 0.97745 | -0.43354 | 8.9344
85 | -0.011024 | -0.0027642 | 0.011028 | 0.002766 | 3.4178e-06 | 1.7837e-06 | 0.016804 | 0.016804 | 0.016804 | 0.97623 | -0.45749 | 0.97656 | -0.45099 | 4.6165
86 | 0.019124 | 0.0047985 | -0.019119 | -0.0047956 | 4.7665e-06 | 2.8626e-06 | 0.029115 | 0.029115 | 0.029115 | 0.97745 | -0.43354 | 0.97719 | -0.43877 | 7.9987
87 | -0.0069865 | -0.001751 | 0.0069871 | 0.0017512 | 6.225e-07 | 1.9826e-07 | 0.010414 | 0.010414 | 0.010414 | 0.99827 | -0.032624 | 0.99837 | -0.030753 | 2.861
88 | -0.33637 | -0.086433 | 0.33687 | 0.086755 | 0.00050329 | 0.00032148 | 0.5021 | 0.5021 | 0.5021 | 0.99837 | -0.030753 | 1 | 0 | 45.9796
89 | 0.010053 | 0.0025199 | -0.010051 | -0.0025191 | 1.8269e-06 | 8.8808e-07 | 0.015018 | 0.015018 | 0.015018 | 0.9961 | -0.073953 | 0.99591 | -0.077768 | 4.1258
90 | 0.0094987 | 0.0023813 | -0.0094954 | -0.0023798 | 3.3494e-06 | 1.5664e-06 | 0.01419 | 0.01419 | 0.01419 | 0.9961 | -0.073953 | 0.99572 | -0.081356 | 3.8984
91 | 0.0060123 | 0.0015068 | -0.0060116 | -0.0015067 | 6.8487e-07 | 1.7305e-07 | 0.0092206 | 0.0092207 | 0.0092207 | 0.97026 | -0.57432 | 0.97014 | -0.57671 | 2.5332
92 | 0.0060203 | 0.0015088 | -0.0060197 | -0.0015087 | 5.92e-07 | 1.5019e-07 | 0.0092328 | 0.0092329 | 0.0092329 | 0.97026 | -0.57432 | 0.97016 | -0.57639 | 2.5365
93 | -0.012033 | -0.0030156 | 0.012041 | 0.0030201 | 8.1142e-06 | 4.4077e-06 | 0.018453 | 0.018453 | 0.018453 | 0.97026 | -0.57432 | 0.97097 | -0.56018 | 5.0696
94 | 0.0060197 | 0.0015087 | -0.0060196 | -0.0015087 | 4.9198e-08 | 1.2484e-08 | 0.0092329 | 0.0092329 | 0.0092329 | 0.97016 | -0.57639 | 0.97015 | -0.57656 | 2.5365
95 | 0.011296 | 0.0028327 | -0.011292 | -0.0028307 | 3.8555e-06 | 2.0434e-06 | 0.017312 | 0.017312 | 0.017312 | 0.97097 | -0.56018 | 0.97061 | -0.56734 | 4.756
96 | -0.023337 | -0.0058528 | 0.023345 | 0.0058581 | 8.6607e-06 | 5.3195e-06 | 0.035765 | 0.035765 | 0.035765 | 0.97097 | -0.56018 | 0.97137 | -0.55239 | 9.8255
97 | 0.011292 | 0.0028307 | -0.01129 | -0.0028297 | 1.8599e-06 | 9.8586e-07 | 0.017312 | 0.017312 | 0.017312 | 0.97061 | -0.56734 | 0.97044 | -0.5708 | 4.7561
98 | -0.02587 | -0.0064909 | 0.025887 | 0.0065012 | 1.6553e-05 | 1.0246e-05 | 0.039633 | 0.039633 | 0.039633 | 0.97137 | -0.55239 | 0.97205 | -0.53898 | 10.8882
99 | -0.006465 | -0.0016203 | 0.0064663 | 0.0016207 | 1.2596e-06 | 3.8411e-07 | 0.0099152 | 0.009915 | 0.0099152 | 0.97023 | -0.57489 | 0.97044 | -0.5708 | 2.724
100 | -0.028547 | -0.007168 | 0.02856 | 0.0071756 | 1.23e-05 | 7.6588e-06 | 0.043705 | 0.043705 | 0.043705 | 0.97205 | -0.53898 | 0.9725 | -0.52996 | 12.007
101 | 0.004833 | 0.0012111 | -0.0048324 | -0.0012111 | 6.2162e-07 | -7.2809e-10 | 0.0072882 | 0.0072883 | 0.0072883 | 0.98674 | -0.25289 | 0.9866 | -0.25559 | 2.0023
102 | 0.0022405 | 0.00056088 | -0.0022404 | -0.00056119 | 1.3583e-07 | -3.1854e-07 | 0.0033782 | 0.0033783 | 0.0033783 | 0.98684 | -0.25103 | 0.98677 | -0.2523 | 0.9281
103 | 0.0010913 | 0.00027321 | -0.0010913 | -0.0002735 | 2.4285e-08 | -2.8994e-07 | 0.0016456 | 0.0016457 | 0.0016457 | 0.98677 | -0.2523 | 0.98675 | -0.25277 | 0.45211
104 | 0.0025468 | 0.00063787 | -0.0025465 | -0.00063822 | 2.1102e-07 | -3.5696e-07 | 0.0038312 | 0.0038313 | 0.0038313 | 0.98911 | -0.20696 | 0.98903 | -0.2087 | 1.0526
105 | 0.0037304 | 0.00093473 | -0.0037301 | -0.00093484 | 2.448e-07 | -1.0775e-07 | 0.0056204 | 0.0056205 | 0.0056205 | 0.98762 | -0.2357 | 0.98755 | -0.23708 | 1.5441
106 | 0.0091598 | 0.0022961 | -0.0091575 | -0.002295 | 2.3635e-06 | 1.1172e-06 | 0.014039 | 0.014039 | 0.014039 | 0.97091 | -0.56168 | 0.97063 | -0.5671 | 3.8568
107 | 0.0056038 | 0.0014044 | -0.0056034 | -0.0014043 | 4.635e-07 | 8.9662e-08 | 0.0085908 | 0.0085909 | 0.0085909 | 0.97063 | -0.5671 | 0.97054 | -0.56883 | 2.3601
108 | 0.0056034 | 0.0014043 | -0.0056027 | -0.0014042 | 6.1367e-07 | 1.1878e-07 | 0.0085909 | 0.008591 | 0.008591 | 0.97054 | -0.56883 | 0.97043 | -0.57113 | 2.3602
109 | 0.0069303 | 0.001737 | -0.0069296 | -0.0017367 | 6.8186e-07 | 2.3194e-07 | 0.010554 | 0.010554 | 0.010554 | 0.97711 | -0.44027 | 0.97701 | -0.44233 | 2.8995
110 | 0.010136 | 0.0025409 | -0.010135 | -0.0025403 | 1.211e-06 | 6.0533e-07 | 0.015437 | 0.015437 | 0.015437 | 0.97711 | -0.44027 | 0.97698 | -0.44277 | 4.2409
111 | 0.0075039 | 0.0018809 | -0.0075024 | -0.0018803 | 1.5024e-06 | 5.7755e-07 | 0.011429 | 0.011429 | 0.011429 | 0.97698 | -0.44277 | 0.97677 | -0.44698 | 3.1399
112 | -0.0011656 | -0.00029213 | 0.0011656 | 0.00029187 | 2.6223e-08 | -2.5849e-07 | 0.0017794 | 0.0017793 | 0.0017794 | 0.9747 | -0.48676 | 0.97473 | -0.48629 | 0.48886
113 | -0.0026553 | -0.00066521 | 0.0026555 | 0.0006649 | 2.2993e-07 | -3.1806e-07 | 0.0040535 | 0.0040533 | 0.0040535 | 0.97473 | -0.48629 | 0.97482 | -0.48447 | 1.1136
114 | -0.0050748 | -0.0012712 | 0.0050751 | 0.0012713 | 3.3029e-07 | 2.8374e-08 | 0.0077462 | 0.0077462 | 0.0077462 | 0.97482 | -0.48447 | 0.97489 | -0.4831 | 2.1281
115 | -0.0056328 | -0.0014108 | 0.0056341 | 0.0014111 | 1.3021e-06 | 2.4744e-07 | 0.0085973 | 0.0085971 | 0.0085973 | 0.97489 | -0.4831 | 0.97513 | -0.47825 | 2.3619
116 | 0.00055771 | 0.00013958 | -0.0005577 | -0.00013977 | 4.1806e-09 | -1.8917e-07 | 0.00085118 | 0.00085125 | 0.00085125 | 0.97489 | -0.4831 | 0.97488 | -0.48326 | 0.23386
117 | -0.022948 | -0.0057533 | 0.022961 | 0.0057614 | 1.3133e-05 | 8.0485e-06 | 0.035018 | 0.035018 | 0.035018 | 0.97513 | -0.47825 | 0.97574 | -0.46625 | 9.6204
118 | 0.017314 | 0.0043423 | -0.017309 | -0.0043397 | 4.2723e-06 | 2.5308e-06 | 0.026421 | 0.026421 | 0.026421 | 0.97513 | -0.47825 | 0.97487 | -0.48343 | 7.2586
119 | -0.011028 | -0.002766 | 0.011032 | 0.0027682 | 4.2266e-06 | 2.2054e-06 | 0.016804 | 0.016804 | 0.016804 | 0.97656 | -0.45099 | 0.97697 | -0.44295 | 4.6164
120 | -0.013228 | -0.0033186 | 0.013231 | 0.0033201 | 2.6359e-06 | 1.4701e-06 | 0.020149 | 0.020148 | 0.020149 | 0.97697 | -0.44295 | 0.97719 | -0.43877 | 5.5353
121 | 0.0058886 | 0.0014755 | -0.005888 | -0.0014754 | 5.4199e-07 | 1.2171e-07 | 0.0089667 | 0.0089668 | 0.0089668 | 0.97719 | -0.43877 | 0.97709 | -0.4407 | 2.4634
122 | 0.030315 | 0.0076268 | -0.030305 | -0.00762 | 1.0756e-05 | 6.718e-06 | 0.046345 | 0.046345 | 0.046345 | 0.97357 | -0.50898 | 0.97319 | -0.51641 | 12.7321
123 | -0.030315 | -0.0076268 | 0.030347 | 0.0076462 | 3.1195e-05 | 1.9482e-05 | 0.046345 | 0.046345 | 0.046345 | 0.97357 | -0.50898 | 0.97466 | -0.48747 | 12.7321
124 | 0.029547 | 0.0074301 | -0.029528 | -0.0074182 | 1.9103e-05 | 1.1916e-05 | 0.045186 | 0.045186 | 0.045186 | 0.97319 | -0.51641 | 0.9725 | -0.52996 | 12.4138
125 | -0.033487 | -0.0084324 | 0.033521 | 0.0084537 | 3.4014e-05 | 2.1336e-05 | 0.051138 | 0.051138 | 0.051138 | 0.97466 | -0.48747 | 0.97574 | -0.46625 | 14.049
126 | 0.0031402 | 0.00078612 | -0.0031398 | -0.00078639 | 3.3882e-07 | -2.7309e-07 | 0.0047938 | 0.0047939 | 0.0047939 | 0.97466 | -0.48747 | 0.97455 | -0.48973 | 1.317
127 | -0.0045109 | -0.0011303 | 0.004511 | 0.0011303 | 1.5384e-07 | -1.0414e-08 | 0.0068698 | 0.0068698 | 0.0068698 | 0.97705 | -0.44142 | 0.97709 | -0.4407 | 1.8873
128 | 0.0031404 | 0.00078686 | -0.0031402 | -0.00078702 | 1.9479e-07 | -1.5971e-07 | 0.0047827 | 0.0047828 | 0.0047828 | 0.97705 | -0.44142 | 0.97698 | -0.44272 | 1.314
129 | -0.012021 | -0.0030125 | 0.012023 | 0.0030138 | 2.4709e-06 | 1.3378e-06 | 0.018357 | 0.018357 | 0.018357 | 0.97439 | -0.49293 | 0.97461 | -0.48861 | 5.0431
130 | 0.0097217 | 0.0024363 | -0.0097199 | -0.0024354 | 1.7674e-06 | 8.6485e-07 | 0.014846 | 0.014846 | 0.014846 | 0.97439 | -0.49293 | 0.9742 | -0.49674 | 4.0786
131 | -0.013408 | -0.0033608 | 0.01341 | 0.0033622 | 2.459e-06 | 1.3787e-06 | 0.020471 | 0.020471 | 0.020471 | 0.97461 | -0.48861 | 0.9748 | -0.48476 | 5.6239
132 | 0.0079469 | 0.0019911 | -0.0079463 | -0.0019908 | 5.7709e-07 | 2.393e-07 | 0.012138 | 0.012138 | 0.012138 | 0.9742 | -0.49674 | 0.97412 | -0.49827 | 3.3347
133 | -0.014956 | -0.0037497 | 0.014957 | 0.0037503 | 9.5235e-07 | 5.4876e-07 | 0.022831 | 0.022831 | 0.022831 | 0.9748 | -0.48476 | 0.97487 | -0.48343 | 6.2723
134 | 0.00091644 | 0.00022963 | -0.00091644 | -0.00022968 | 3.1035e-09 | -5.0586e-08 | 0.0013999 | 0.0013999 | 0.0013999 | 0.97412 | -0.49827 | 0.97412 | -0.49834 | 0.38459
135 | 0.0070299 | 0.0017612 | -0.0070297 | -0.0017611 | 1.9048e-07 | 6.707e-08 | 0.010738 | 0.010738 | 0.010738 | 0.97412 | -0.49827 | 0.97409 | -0.49884 | 2.9501
136 | 0.0036449 | 0.00091328 | -0.0036448 | -0.00091335 | 1.564e-07 | -6.736e-08 | 0.0055679 | 0.005568 | 0.005568 | 0.97409 | -0.49884 | 0.97404 | -0.49974 | 1.5297
137 | 0.0033848 | 0.00084784 | -0.0033842 | -0.00084817 | 5.3775e-07 | -3.2344e-07 | 0.0051704 | 0.0051706 | 0.0051706 | 0.97409 | -0.49884 | 0.97392 | -0.50217 | 1.4205
138 | 0.0029438 | 0.00073766 | -0.0029437 | -0.00073775 | 9.4299e-08 | -9.4413e-08 | 0.004497 | 0.0044971 | 0.0044971 | 0.97404 | -0.49974 | 0.97401 | -0.50041 | 1.2355
139 | 0.0037487 | 0.00093933 | -0.0037485 | -0.00093945 | 2.8944e-07 | -1.201e-07 | 0.0056675 | 0.0056677 | 0.0056677 | 0.98422 | -0.3013 | 0.98414 | -0.30292 | 1.557
140 | 0.074669 | 0.018863 | -0.074659 | -0.018856 | 1.0243e-05 | 6.5286e-06 | 0.11294 | 0.11294 | 0.11294 | 0.98422 | -0.3013 | 0.98407 | -0.30416 | 31.0284
141 | -0.063505 | -0.016051 | 0.063571 | 0.016093 | 6.5647e-05 | 4.1778e-05 | 0.096542 | 0.096542 | 0.096542 | 0.97931 | -0.39654 | 0.98041 | -0.375 | 26.5225
142 | 0.060946 | 0.01541 | -0.060891 | -0.015375 | 5.511e-05 | 3.5056e-05 | 0.092654 | 0.092654 | 0.092654 | 0.97931 | -0.39654 | 0.97834 | -0.41541 | 25.4543
143 | -0.064335 | -0.016284 | 0.064388 | 0.016318 | 5.3611e-05 | 3.4122e-05 | 0.097702 | 0.097702 | 0.097702 | 0.98041 | -0.375 | 0.9813 | -0.35766 | 26.8411
144 | 0.059428 | 0.015008 | -0.059373 | -0.014973 | 5.5004e-05 | 3.4978e-05 | 0.090428 | 0.090428 | 0.090428 | 0.97834 | -0.41541 | 0.97735 | -0.43474 | 24.8429
145 | -0.066205 | -0.016774 | 0.066306 | 0.016838 | 0.00010125 | 6.4463e-05 | 0.10046 | 0.10046 | 0.10046 | 0.9813 | -0.35766 | 0.98294 | -0.32587 | 27.5978
146 | 0.058301 | 0.014704 | -0.058256 | -0.014676 | 4.4974e-05 | 2.8593e-05 | 0.088796 | 0.088796 | 0.088796 | 0.97735 | -0.43474 | 0.97653 | -0.45087 | 24.3946
147 | 0.056523 | 0.014241 | -0.056482 | -0.014215 | 4.1537e-05 | 2.6397e-05 | 0.086156 | 0.086156 | 0.086156 | 0.97653 | -0.45087 | 0.97574 | -0.46625 | 23.6693
148 | 0.0014961 | 0.00037444 | -0.001496 | -0.00037494 | 8.7411e-08 | -5.0061e-07 | 0.0022842 | 0.0022844 | 0.0022844 | 0.97455 | -0.48973 | 0.97449 | -0.49096 | 0.62759
149 | -0.069463 | -0.017547 | 0.069481 | 0.017558 | 1.7804e-05 | 1.134e-05 | 0.10511 | 0.10511 | 0.10511 | 0.9838 | -0.30951 | 0.98407 | -0.30416 | 28.8774
150 | 0.0012284 | 0.00030785 | -0.0012284 | -0.00030787 | 2.0397e-09 | -1.9007e-08 | 0.0018509 | 0.0018509 | 0.0018509 | 0.98755 | -0.23708 | 0.98755 | -0.23712 | 0.5085

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34543 | 0.088486

## res_load
| p_mw | q_mvar
0 | 0.0019709 | 0.00049396
1 | 0.0015463 | 0.00038755
2 | 0.0034969 | 0.00087642
3 | 0.0010442 | 0.00026171
4 | 0.0016412 | 0.00041131
5 | 0.0018255 | 0.00045751
6 | 0.0020628 | 0.00051698
7 | 0.0042015 | 0.001053
8 | 0.0019108 | 0.0004789
9 | 0.0025651 | 0.00064288
10 | 0.0013015 | 0.00032619
11 | 0.0030292 | 0.00075918
12 | 0.0024674 | 0.00061838
13 | 0.0026446 | 0.0006628
14 | 0.002996 | 0.00075087
15 | 0.0012702 | 0.00031835
16 | 0.0020144 | 0.00050485
17 | 0.00186 | 0.00046616
18 | 0.0021 | 0.00052631
19 | 0.0021365 | 0.00053546
20 | 0.0028327 | 0.00070994
21 | 0.0034943 | 0.00087575
22 | 0.0012222 | 0.00030631
23 | 0.003411 | 0.00085487
24 | 0.0065221 | 0.0016346
25 | 0.013632 | 0.0034164
26 | 0.0089942 | 0.0022542
27 | 0.0063336 | 0.0015873
28 | 0.0051006 | 0.0012783
29 | 0.0042138 | 0.0010561
30 | 0.002646 | 0.00066315
31 | 0.0015554 | 0.00038981
32 | 0.0018544 | 0.00046476
33 | 0.015232 | 0.0038175
34 | 0.00080239 | 0.0002011
35 | 0.0026382 | 0.00066119
36 | 0.0029485 | 0.00073896
37 | 0.0013569 | 0.00034006
38 | 0.0012364 | 0.00030987
39 | 0.0019949 | 0.00049996
40 | 0.00098212 | 0.00024614
41 | 0.0090236 | 0.0022615
42 | 0.0022375 | 0.00056077
43 | 0.0069865 | 0.001751
44 | 0.0069088 | 0.0017315
45 | 0.0060116 | 0.0015067
46 | 0.010051 | 0.0025191
47 | 0.0094954 | 0.0023798
48 | 0.002525 | 0.00063282
49 | 0.0060196 | 0.0015087
50 | 0.006465 | 0.0016203
51 | 0.0048241 | 0.001209
52 | 0.0026605 | 0.00066679
53 | 0.0036176 | 0.00090666
54 | 0.0032389 | 0.00081175
55 | 0.0048324 | 0.0012111
56 | 0.0011491 | 0.00028798
57 | 0.0018458 | 0.00046261
58 | 0.0027493 | 0.00068905
59 | 0.0010913 | 0.0002735
60 | 0.0083776 | 0.0020996
61 | 0.0035536 | 0.00089063
62 | 0.0056027 | 0.0014042
63 | 0.0069296 | 0.0017367
64 | 0.0026313 | 0.00065948
65 | 0.0026749 | 0.00067039
66 | 0.0011656 | 0.00029213
67 | 0.0014897 | 0.00037335
68 | 0.0024193 | 0.00060633
69 | 0.0005577 | 0.00013977
70 | 0.0021961 | 0.0005504
71 | 0.00075797 | 0.00018996
72 | 0.0013704 | 0.00034346
73 | 0.001377 | 0.00034511
74 | 0.0031402 | 0.00078702
75 | 0.0075024 | 0.0018803
76 | 0.002299 | 0.00057619
77 | 0.0013846 | 0.000347
78 | 0.001773 | 0.00044435
79 | 0.0015463 | 0.00038754
80 | 0.002352 | 0.00058945
81 | 0.00091644 | 0.00022968
82 | 0.00070103 | 0.00017569
83 | 0.0033842 | 0.00084817
84 | 0.0029437 | 0.00073775
85 | 0.0025589 | 0.00064132
86 | 0.00076429 | 0.00019155
87 | 0.0014634 | 0.00036676
88 | 0.0018165 | 0.00045525
89 | 0.0010718 | 0.00026862
90 | 0.0022939 | 0.00057491
91 | 0.0017326 | 0.00043423
92 | 0.0016437 | 0.00041195
93 | 0.001496 | 0.00037494
94 | 0.00096772 | 0.00024253
95 | 0.0025465 | 0.00063822
96 | 0.0052943 | 0.0013269
97 | 0.0053816 | 0.0013487
98 | 0.0051781 | 0.0012977
99 | 0.0021188 | 0.00053102
100 | 0.0025017 | 0.00062699
101 | 0.0012284 | 0.00030787
102 | 0.0037485 | 0.00093945

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1