## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2556-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2556-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2556-6_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2556-6_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2556-6_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2556-6_0_4_node_50 | 0.4 | n |  | TRUE
6 | bus_LV_2556-6_0_4_node_34 | 0.4 | n |  | TRUE
7 | bus_LV_2556-6_0_4_node_51 | 0.4 | n |  | TRUE
8 | bus_LV_2556-6_0_4_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_2556-6_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2556-6_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2556-6_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2556-6_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2556-6_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2556-6_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2556-6_0_4_node_54 | 0.4 | n |  | TRUE
16 | bus_LV_2556-6_0_4_node_52 | 0.4 | n |  | TRUE
17 | bus_LV_2556-6_0_4_node_45 | 0.4 | n |  | TRUE
18 | bus_LV_2556-6_0_4_node_57 | 0.4 | n |  | TRUE
19 | bus_LV_2556-6_0_4_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_2556-6_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2556-6_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2556-6_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2556-6_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2556-6_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2556-6_0_4_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_2556-6_0_4_node_48 | 0.4 | n |  | TRUE
27 | bus_LV_2556-6_0_4_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_2556-6_0_4_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_2556-6_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_2556-6_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_2556-6_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_2556-6_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_2556-6_0_4_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_2556-6_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_2556-6_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_2556-6_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_2556-6_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_2556-6_0_4_node_58 | 0.4 | n |  | TRUE
39 | bus_LV_2556-6_0_4_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_2556-6_0_4_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_2556-6_0_4_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_2556-6_0_4_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_2556-6_0_4_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_2556-6_0_4_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_2556-6_0_4_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_2556-6_0_4_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_2556-6_0_4_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_2556-6_0_4_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_2556-6_0_4_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_2556-6_0_4_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_2556-6_0_4_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_2556-6_0_4_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_2556-6_0_4_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_2556-6_0_4_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_2556-6_0_4_node_55 | 0.4 | n |  | TRUE
56 | bus_MV_396_0_node_11 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2556-6_0_4_load_0 | 0 | 0.0057763 | 0.0014477 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2556-6_0_4_load_1 | 1 | 0.00050534 | 0.00012665 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2556-6_0_4_load_3 | 3 | 0.016545 | 0.0041465 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2556-6_0_4_load_4 | 4 | 0.0027089 | 0.0006789 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2556-6_0_4_load_34 | 6 | 0.0013449 | 0.00033707 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2556-6_0_4_load_51 | 7 | 0.0051252 | 0.0012845 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2556-6_0_4_load_32 | 8 | 0.0014998 | 0.00037588 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2556-6_0_4_load_5 | 9 | 0.078146 | 0.019585 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2556-6_0_4_load_8 | 11 | 0.022428 | 0.005621 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2556-6_0_4_load_52 | 16 | 0.01733 | 0.0043432 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2556-6_0_4_load_45 | 17 | 0.023107 | 0.0057911 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2556-6_0_4_load_57 | 18 | 0.014751 | 0.0036968 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2556-6_0_4_load_46 | 19 | 0.021848 | 0.0054757 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2556-6_0_4_load_11 | 20 | 0.0016821 | 0.00042158 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2556-6_0_4_load_14 | 23 | 0.0015773 | 0.00039531 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2556-6_0_4_load_15 | 24 | 0.0038474 | 0.00096425 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2556-6_0_4_load_28 | 25 | 0.0009935 | 0.00024899 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2556-6_0_4_load_48 | 26 | 0.0011754 | 0.00029457 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2556-6_0_4_load_29 | 27 | 0.0022906 | 0.00057407 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2556-6_0_4_load_49 | 28 | 0.0020162 | 0.00050531 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2556-6_0_4_load_16 | 29 | 0.017935 | 0.0044949 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2556-6_0_4_load_17 | 30 | 0.0019987 | 0.00050092 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2556-6_0_4_load_20 | 33 | 0.00081225 | 0.00020357 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2556-6_0_4_load_21 | 34 | 0.0022018 | 0.00055183 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2556-6_0_4_load_23 | 36 | 0.0015349 | 0.00038467 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2556-6_0_4_load_58 | 38 | 0.0020428 | 0.00051196 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2556-6_0_4_load_24 | 40 | 0.0027 | 0.00067669 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2556-6_0_4_load_30 | 41 | 0.0010395 | 0.00026052 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2556-6_0_4_load_26 | 42 | 0.0013678 | 0.00034281 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2556-6_0_4_load_41 | 43 | 0.0019532 | 0.00048952 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2556-6_0_4_load_25 | 44 | 0.0030662 | 0.00076847 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2556-6_0_4_load_31 | 45 | 0.0012257 | 0.00030719 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2556-6_0_4_load_33 | 46 | 0.007124 | 0.0017854 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2556-6_0_4_load_35 | 47 | 0.011377 | 0.0028512 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2556-6_0_4_load_36 | 48 | 0.0042839 | 0.0010736 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2556-6_0_4_load_42 | 50 | 0.0089787 | 0.0022503 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2556-6_0_4_load_40 | 51 | 0.019799 | 0.0049622 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2556-6_0_4_load_38 | 52 | 0.0024886 | 0.00062369 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2556-6_0_4_load_39 | 53 | 0.019085 | 0.0047831 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2556-6_0_4_load_43 | 54 | 0.0037623 | 0.00094291 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2556-6_0_4_load_55 | 55 | 0.0018342 | 0.0004597 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2556-6_0_4_line_0 |  | 0 | 1 | 0.026028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2556-6_0_4_line_1 |  | 0 | 2 | 0.027805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2556-6_0_4_line_2 |  | 1 | 3 | 0.024354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2556-6_0_4_line_3 |  | 2 | 4 | 0.083794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2556-6_0_4_line_4 |  | 3 | 5 | 0.07637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2556-6_0_4_line_5 |  | 4 | 6 | 0.0098488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2556-6_0_4_line_6 |  | 5 | 7 | 0.1109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2556-6_0_4_line_7 |  | 6 | 8 | 0.0039189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2556-6_0_4_line_8 |  | 7 | 54 | 0.038562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2556-6_0_4_line_9 |  | 8 | 46 | 0.0054182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2556-6_0_4_line_10 |  | 9 | 10 | 0.053343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2556-6_0_4_line_11 |  | 10 | 11 | 0.0030569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2556-6_0_4_line_12 |  | 11 | 14 | 0.060889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2556-6_0_4_line_13 |  | 12 | 13 | 0.077034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2556-6_0_4_line_14 |  | 12 | 14 | 0.096657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2556-6_0_4_line_15 |  | 13 | 15 | 0.041417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2556-6_0_4_line_16 |  | 13 | 16 | 0.032674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2556-6_0_4_line_17 |  | 14 | 17 | 0.028673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2556-6_0_4_line_18 |  | 15 | 18 | 0.08462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2556-6_0_4_line_19 |  | 17 | 19 | 0.041202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2556-6_0_4_line_20 |  | 19 | 39 | 0.03145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2556-6_0_4_line_21 |  | 20 | 21 | 0.059289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2556-6_0_4_line_22 |  | 20 | 22 | 0.039164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2556-6_0_4_line_23 |  | 21 | 23 | 0.015324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2556-6_0_4_line_24 |  | 22 | 24 | 0.00066896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2556-6_0_4_line_25 |  | 23 | 25 | 0.0025786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2556-6_0_4_line_26 |  | 24 | 26 | 0.028779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2556-6_0_4_line_27 |  | 25 | 27 | 0.021766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2556-6_0_4_line_28 |  | 26 | 28 | 0.019345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2556-6_0_4_line_29 |  | 27 | 45 | 0.00073864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2556-6_0_4_line_30 |  | 28 | 55 | 0.018169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2556-6_0_4_line_31 |  | 29 | 30 | 0.00094951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2556-6_0_4_line_32 |  | 29 | 31 | 0.011767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2556-6_0_4_line_33 |  | 30 | 32 | 0.037231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2556-6_0_4_line_34 |  | 31 | 33 | 0.013111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2556-6_0_4_line_35 |  | 31 | 34 | 0.031091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2556-6_0_4_line_36 |  | 32 | 35 | 0.030833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2556-6_0_4_line_37 |  | 33 | 36 | 0.016095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2556-6_0_4_line_38 |  | 34 | 37 | 0.0047936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2556-6_0_4_line_39 |  | 35 | 38 | 0.046904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2556-6_0_4_line_40 |  | 35 | 39 | 0.12109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2556-6_0_4_line_41 |  | 36 | 40 | 0.017507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2556-6_0_4_line_42 |  | 37 | 41 | 0.02019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2556-6_0_4_line_43 |  | 37 | 42 | 0.02157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2556-6_0_4_line_44 |  | 39 | 43 | 0.051875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2556-6_0_4_line_45 |  | 41 | 45 | 0.0031867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2556-6_0_4_line_46 |  | 42 | 44 | 0.017677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2556-6_0_4_line_47 |  | 43 | 53 | 0.039389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_2556-6_0_4_line_48 |  | 46 | 47 | 0.037082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_2556-6_0_4_line_49 |  | 47 | 48 | 0.011307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_2556-6_0_4_line_50 |  | 48 | 49 | 0.0069195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_2556-6_0_4_line_51 |  | 49 | 50 | 0.063076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_2556-6_0_4_line_52 |  | 50 | 51 | 0.059201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_2556-6_0_4_line_53 |  | 51 | 52 | 0.085348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_2556-6_0_4_line_54 |  | 52 | 53 | 0.0017779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2556-6_0_4_trafo_8 | 0.63 MVA 20/0.4 kV | 56 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2601587.2731 | 1227653.5358 | 2601576.7653 | 1227677.3485
1 | 2601598.4983 | 1227628.0977 | 2601587.2731 | 1227653.5358
2 | 2601566.9333 | 1227699.6293 | 2601576.7653 | 1227677.3485
3 | 2601598.4983 | 1227628.0977 | 2601679.204 | 1227650.6361
4 | 2601536.1018 | 1227769.4987 | 2601566.9333 | 1227699.6293
5 | 2601688.6898 | 1227653.2852 | 2601679.204 | 1227650.6361
6 | 2601536.1018 | 1227769.4987 | 2601571.8172 | 1227782.9489 | 2601641.2576 | 1227804.5786
7 | 2601692.4643 | 1227654.3393 | 2601688.6898 | 1227653.2852
8 | 2601641.2576 | 1227804.5786 | 2601660.492 | 1227838.0013
9 | 2601692.4643 | 1227654.3393 | 2601697.6828 | 1227655.7967
10 | 2601771.6997 | 1227926.0982 | 2601823.145 | 1227940.1998
11 | 2601771.6997 | 1227926.0982 | 2601770.9161 | 1227929.053
12 | 2601755.3083 | 1227987.9078 | 2601770.9161 | 1227929.053
13 | 2601848.5269 | 1228013.4611 | 2601898.5603 | 1228027.1733 | 2601922.8193 | 1228033.8291
14 | 2601755.3083 | 1227987.9078 | 2601777.3175 | 1227993.9399 | 2601794.1369 | 1227998.5474 | 2601818.0931 | 1228005.1138 | 2601848.5269 | 1228013.4611
15 | 2601922.8193 | 1228033.8291 | 2601934.6249 | 1228006.9836 | 2601938.6434 | 1227998.1464 | 2601940.1896 | 1227996.3347
16 | 2601922.8193 | 1228033.8291 | 2601932.3354 | 1228059.3249 | 2601931.1032 | 1228064.6438
17 | 2601755.3083 | 1227987.9078 | 2601727.6555 | 1227980.3276
18 | 2601940.1896 | 1227996.3347 | 2601941.0397 | 1227991.6989 | 2601961.4513 | 1227945.9561 | 2601961.9902 | 1227942.9878 | 2601960.8466 | 1227941.3309 | 2601957.7935 | 1227939.8624 | 2601937.3757 | 1227933.1854
19 | 2601727.6555 | 1227980.3276 | 2601687.9193 | 1227969.435
20 | 2601657.5886 | 1227961.1207 | 2601687.9193 | 1227969.435
21 | 2601537.3159 | 1228192.4598 | 2601560.2475 | 1228204.0167 | 2601575.2013 | 1228213.804 | 2601587.6723 | 1228223.4043
22 | 2601619.1068 | 1228246.7236 | 2601612.3875 | 1228242.4305 | 2601587.6723 | 1228223.4043
23 | 2601537.3159 | 1228192.4598 | 2601545.2503 | 1228179.3495
24 | 2601619.6825 | 1228247.0644 | 2601619.1068 | 1228246.7236
25 | 2601546.5855 | 1228177.1435 | 2601545.2503 | 1228179.3495
26 | 2601619.6825 | 1228247.0644 | 2601630.2502 | 1228253.3193 | 2601642.6892 | 1228259.782 | 2601644.9312 | 1228260.8448
27 | 2601546.5855 | 1228177.1435 | 2601557.8551 | 1228158.5224
28 | 2601644.9312 | 1228260.8448 | 2601654.9617 | 1228265.5998 | 2601662.6219 | 1228268.6471
29 | 2601558.2375 | 1228157.8904 | 2601557.8551 | 1228158.5224
30 | 2601662.6219 | 1228268.6471 | 2601669.5601 | 1228271.4071 | 2601679.5861 | 1228275.1515
31 | 2601594.3848 | 1228096.7523 | 2601594.8515 | 1228095.9254
32 | 2601588.6013 | 1228106.9999 | 2601594.3848 | 1228096.7523
33 | 2601609.8656 | 1228062.4235 | 2601608.8026 | 1228071.2062 | 2601594.8515 | 1228095.9254
34 | 2601588.6013 | 1228106.9999 | 2601576.6285 | 1228101.6573
35 | 2601588.6013 | 1228106.9999 | 2601572.7804 | 1228133.7647
36 | 2601609.8656 | 1228062.4235 | 2601614.3508 | 1228063.5476 | 2601639.7919 | 1228070.1915
37 | 2601576.6285 | 1228101.6573 | 2601561.9301 | 1228095.0985
38 | 2601570.3411 | 1228137.8913 | 2601572.7804 | 1228133.7647
39 | 2601636.628 | 1228115.6175 | 2601639.6181 | 1228097.1963 | 2601635.7412 | 1228087.9787 | 2601639.7919 | 1228070.1915
40 | 2601657.5886 | 1227961.1207 | 2601648.1536 | 1227996.4168 | 2601633.2124 | 1228052.3459 | 2601631.1267 | 1228060.1499 | 2601641.6578 | 1228062.6542 | 2601639.7919 | 1228070.1915
41 | 2601561.9301 | 1228095.0985 | 2601545.9426 | 1228087.9644
42 | 2601570.3411 | 1228137.8913 | 2601559.8875 | 1228155.1642
43 | 2601570.3411 | 1228137.8913 | 2601552.002 | 1228126.5356
44 | 2601657.5886 | 1227961.1207 | 2601666.2183 | 1227934.5073 | 2601674.4297 | 1227912.0646
45 | 2601558.2375 | 1228157.8904 | 2601559.8875 | 1228155.1642
46 | 2601552.002 | 1228126.5356 | 2601536.9727 | 1228117.2294
47 | 2601687.964 | 1227875.0737 | 2601674.4297 | 1227912.0646
48 | 2601732.9045 | 1227667.0144 | 2601727.2882 | 1227664.0645 | 2601697.6828 | 1227655.7967
49 | 2601732.9045 | 1227667.0144 | 2601739.9102 | 1227670.6941 | 2601742.4004 | 1227672.9996
50 | 2601747.4779 | 1227677.7004 | 2601742.4004 | 1227672.9996
51 | 2601747.4779 | 1227677.7004 | 2601751.2937 | 1227689.0971 | 2601751.6765 | 1227702.0048 | 2601747.4897 | 1227716.4788 | 2601739.2024 | 1227738.0165
52 | 2601739.2024 | 1227738.0165 | 2601717.9423 | 1227793.2683
53 | 2601688.5749 | 1227873.404 | 2601695.1005 | 1227855.5685 | 2601708.4766 | 1227818.8283 | 2601717.3636 | 1227794.7721 | 2601717.9423 | 1227793.2683
54 | 2601688.5749 | 1227873.404 | 2601687.964 | 1227875.0737

## bus_geodata
| x | y | coords
0 | 2601587.2731 | 1227653.5358
1 | 2601576.7653 | 1227677.3485
2 | 2601598.4983 | 1227628.0977
3 | 2601566.9333 | 1227699.6293
4 | 2601679.204 | 1227650.6361
5 | 2601536.1018 | 1227769.4987
6 | 2601688.6898 | 1227653.2852
7 | 2601641.2576 | 1227804.5786
8 | 2601692.4643 | 1227654.3393
9 | 2601823.145 | 1227940.1998
10 | 2601771.6997 | 1227926.0982
11 | 2601770.9161 | 1227929.053
12 | 2601848.5269 | 1228013.4611
13 | 2601922.8193 | 1228033.8291
14 | 2601755.3083 | 1227987.9078
15 | 2601940.1896 | 1227996.3347
16 | 2601931.1032 | 1228064.6438
17 | 2601727.6555 | 1227980.3276
18 | 2601937.3757 | 1227933.1854
19 | 2601687.9193 | 1227969.435
20 | 2601587.6723 | 1228223.4043
21 | 2601537.3159 | 1228192.4598
22 | 2601619.1068 | 1228246.7236
23 | 2601545.2503 | 1228179.3495
24 | 2601619.6825 | 1228247.0644
25 | 2601546.5855 | 1228177.1435
26 | 2601644.9312 | 1228260.8448
27 | 2601557.8551 | 1228158.5224
28 | 2601662.6219 | 1228268.6471
29 | 2601594.3848 | 1228096.7523
30 | 2601594.8515 | 1228095.9254
31 | 2601588.6013 | 1228106.9999
32 | 2601609.8656 | 1228062.4235
33 | 2601576.6285 | 1228101.6573
34 | 2601572.7804 | 1228133.7647
35 | 2601639.7919 | 1228070.1915
36 | 2601561.9301 | 1228095.0985
37 | 2601570.3411 | 1228137.8913
38 | 2601636.628 | 1228115.6175
39 | 2601657.5886 | 1227961.1207
40 | 2601545.9426 | 1228087.9644
41 | 2601559.8875 | 1228155.1642
42 | 2601552.002 | 1228126.5356
43 | 2601674.4297 | 1227912.0646
44 | 2601536.9727 | 1228117.2294
45 | 2601558.2375 | 1228157.8904
46 | 2601697.6828 | 1227655.7967
47 | 2601732.9045 | 1227667.0144
48 | 2601742.4004 | 1227672.9996
49 | 2601747.4779 | 1227677.7004
50 | 2601739.2024 | 1227738.0165
51 | 2601717.9423 | 1227793.2683
52 | 2601688.5749 | 1227873.404
53 | 2601687.964 | 1227875.0737
54 | 2601660.492 | 1227838.0013
55 | 2601679.5861 | 1228275.1515
56 | 2601771.6997 | 1227926.0982

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97674 | -0.44867 | 0.0057763 | 0.0014477
1 | 0.97611 | -0.46102 | 0.00050534 | 0.00012665
2 | 0.97756 | -0.43257 | 0 | 0
3 | 0.97554 | -0.47236 | 0.016545 | 0.0041465
4 | 0.98003 | -0.38421 | 0.0027089 | 0.0006789
5 | 0.9749 | -0.48481 | 0 | 0
6 | 0.98034 | -0.37806 | 0.0013449 | 0.00033707
7 | 0.97399 | -0.5029 | 0.0051252 | 0.0012845
8 | 0.98047 | -0.37551 | 0.0014998 | 0.00037588
9 | 0.99599 | -0.077129 | 0.078146 | 0.019585
10 | 0.99978 | -0.0041646 | 0 | 0
11 | 1 | 0 | -0.32437 | -0.082339
12 | 0.99265 | -0.14029 | 0 | 0
13 | 0.99038 | -0.18411 | 0 | 0
14 | 0.99549 | -0.085578 | 0 | 0
15 | 0.98982 | -0.19497 | 0 | 0
16 | 0.98987 | -0.19417 | 0.01733 | 0.0043432
17 | 0.99365 | -0.12073 | 0.023107 | 0.0057911
18 | 0.98868 | -0.2172 | 0.014751 | 0.0036968
19 | 0.9913 | -0.16584 | 0.021848 | 0.0054757
20 | 0.97827 | -0.41875 | 0.0016821 | 0.00042158
21 | 0.97885 | -0.40736 | 0 | 0
22 | 0.97795 | -0.42509 | 0 | 0
23 | 0.979 | -0.40441 | 0.0015773 | 0.00039531
24 | 0.97795 | -0.42519 | 0.0038474 | 0.00096425
25 | 0.97903 | -0.40384 | 0.0009935 | 0.00024899
26 | 0.97781 | -0.42783 | 0.0011754 | 0.00029457
27 | 0.9793 | -0.39865 | 0.0022906 | 0.00057407
28 | 0.97774 | -0.42919 | 0.0020162 | 0.00050531
29 | 0.98081 | -0.36908 | 0.017935 | 0.0044949
30 | 0.98085 | -0.36826 | 0.0019987 | 0.00050092
31 | 0.98049 | -0.37534 | 0 | 0
32 | 0.98255 | -0.33506 | 0 | 0
33 | 0.98043 | -0.37654 | 0.00081225 | 0.00020357
34 | 0.97979 | -0.38906 | 0.0022018 | 0.00055183
35 | 0.98395 | -0.30765 | 0 | 0
36 | 0.98036 | -0.37778 | 0.0015349 | 0.00038467
37 | 0.97969 | -0.39099 | 0 | 0
38 | 0.98387 | -0.30937 | 0.0020428 | 0.00051196
39 | 0.98971 | -0.19634 | 0 | 0
40 | 0.98032 | -0.37863 | 0.0027 | 0.00067669
41 | 0.97936 | -0.39748 | 0.0010395 | 0.00026052
42 | 0.9796 | -0.39273 | 0.0013678 | 0.00034281
43 | 0.98791 | -0.23098 | 0.0019532 | 0.00048952
44 | 0.97955 | -0.39371 | 0.0030662 | 0.00076847
45 | 0.97931 | -0.39844 | 0.0012257 | 0.00030719
46 | 0.98066 | -0.37185 | 0.007124 | 0.0017854
47 | 0.98143 | -0.35694 | 0.011377 | 0.0028512
48 | 0.98162 | -0.35314 | 0.0042839 | 0.0010736
49 | 0.98175 | -0.35063 | 0 | 0
50 | 0.98292 | -0.32782 | 0.0089787 | 0.0022503
51 | 0.98418 | -0.30327 | 0.019799 | 0.0049622
52 | 0.98652 | -0.25789 | 0.0024886 | 0.00062369
53 | 0.98657 | -0.25692 | 0.019085 | 0.0047831
54 | 0.97385 | -0.50557 | 0.0037623 | 0.00094291
55 | 0.97771 | -0.4298 | 0.0018342 | 0.0004597
56 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.02598 | 0.0065243 | -0.025965 | -0.0065148 | 1.5294e-05 | 9.4625e-06 | 0.039584 | 0.039584 | 0.039584 | 0.97674 | -0.44867 | 0.97611 | -0.46102 | 10.8748
1 | -0.031756 | -0.007972 | 0.031781 | 0.0079873 | 2.4409e-05 | 1.5274e-05 | 0.048384 | 0.048384 | 0.048384 | 0.97674 | -0.44867 | 0.97756 | -0.43257 | 13.2923
2 | 0.025459 | 0.0063882 | -0.025446 | -0.0063797 | 1.3758e-05 | 8.5012e-06 | 0.038814 | 0.038814 | 0.038814 | 0.97611 | -0.46102 | 0.97554 | -0.47236 | 10.6632
3 | -0.031781 | -0.0079873 | 0.031854 | 0.0080333 | 7.356e-05 | 4.6025e-05 | 0.048384 | 0.048384 | 0.048384 | 0.97756 | -0.43257 | 0.98003 | -0.38421 | 13.2923
4 | 0.0089009 | 0.0022332 | -0.0088956 | -0.0022308 | 5.2797e-06 | 2.4262e-06 | 0.013578 | 0.013578 | 0.013578 | 0.97554 | -0.47236 | 0.9749 | -0.48481 | 3.7302
5 | -0.034563 | -0.0087122 | 0.034573 | 0.0087186 | 1.0178e-05 | 6.39e-06 | 0.052496 | 0.052496 | 0.052496 | 0.98003 | -0.38421 | 0.98034 | -0.37806 | 14.4221
6 | 0.0088956 | 0.0022308 | -0.0088879 | -0.0022272 | 7.6671e-06 | 3.5255e-06 | 0.013578 | 0.013578 | 0.013578 | 0.9749 | -0.48481 | 0.97399 | -0.5029 | 3.7304
7 | -0.035918 | -0.0090556 | 0.035923 | 0.0090584 | 4.3711e-06 | 2.7481e-06 | 0.054538 | 0.054538 | 0.054538 | 0.98034 | -0.37806 | 0.98047 | -0.37551 | 14.9829
8 | 0.0037627 | 0.00094274 | -0.0037623 | -0.00094291 | 4.7787e-07 | -1.7403e-07 | 0.0057485 | 0.0057486 | 0.0057486 | 0.97399 | -0.5029 | 0.97385 | -0.50557 | 1.5793
9 | -0.037422 | -0.0094343 | 0.037429 | 0.0094384 | 6.5584e-06 | 4.129e-06 | 0.056814 | 0.056814 | 0.056814 | 0.98047 | -0.37551 | 0.98066 | -0.37185 | 15.6082
10 | -0.078146 | -0.019585 | 0.078419 | 0.019759 | 0.00027267 | 0.00017381 | 0.11675 | 0.11675 | 0.11675 | 0.99599 | -0.077129 | 0.99978 | -0.0041646 | 32.0745
11 | -0.078419 | -0.019759 | 0.078434 | 0.019769 | 1.5625e-05 | 9.9602e-06 | 0.11675 | 0.11675 | 0.11675 | 0.99978 | -0.0041646 | 1 | 0 | 32.0744
12 | 0.24428 | 0.06257 | -0.24328 | -0.061927 | 0.0010083 | 0.00064294 | 0.36398 | 0.36398 | 0.36398 | 1 | 0 | 0.99549 | -0.085578 | 33.3312
13 | 0.032179 | 0.0081003 | -0.032112 | -0.0080583 | 6.7253e-05 | 4.2049e-05 | 0.04825 | 0.048251 | 0.048251 | 0.99265 | -0.14029 | 0.99038 | -0.18411 | 13.2556
14 | -0.032179 | -0.0081003 | 0.032264 | 0.0081531 | 8.4384e-05 | 5.2753e-05 | 0.04825 | 0.04825 | 0.04825 | 0.99265 | -0.14029 | 0.99549 | -0.085578 | 13.2555
15 | 0.014774 | 0.0037101 | -0.014766 | -0.0037058 | 7.6544e-06 | 4.3661e-06 | 0.0222 | 0.0222 | 0.0222 | 0.99038 | -0.18411 | 0.98982 | -0.19497 | 6.0989
16 | 0.017338 | 0.0043481 | -0.01733 | -0.0043432 | 8.3151e-06 | 4.9014e-06 | 0.026051 | 0.026051 | 0.026051 | 0.99038 | -0.18411 | 0.98987 | -0.19417 | 7.1568
17 | 0.21101 | 0.053774 | -0.21065 | -0.053546 | 0.00035728 | 0.00022754 | 0.31573 | 0.31573 | 0.31573 | 0.99549 | -0.085578 | 0.99365 | -0.12073 | 28.9128
18 | 0.014766 | 0.0037058 | -0.014751 | -0.0036968 | 1.5639e-05 | 8.9228e-06 | 0.0222 | 0.0222 | 0.0222 | 0.98982 | -0.19497 | 0.98868 | -0.2172 | 6.099
19 | 0.18755 | 0.047755 | -0.18714 | -0.047496 | 0.00040703 | 0.0002589 | 0.28112 | 0.28113 | 0.28113 | 0.99365 | -0.12073 | 0.9913 | -0.16584 | 25.7441
20 | 0.16529 | 0.04202 | -0.16505 | -0.041866 | 0.00024243 | 0.00015394 | 0.24833 | 0.24833 | 0.24833 | 0.9913 | -0.16584 | 0.98971 | -0.19634 | 22.7408
21 | -0.010559 | -0.0026464 | 0.010565 | 0.0026494 | 5.7351e-06 | 2.9256e-06 | 0.016061 | 0.016061 | 0.016061 | 0.97827 | -0.41875 | 0.97885 | -0.40736 | 4.4124
22 | 0.0088769 | 0.0022248 | -0.0088742 | -0.0022236 | 2.6776e-06 | 1.2221e-06 | 0.013502 | 0.013502 | 0.013502 | 0.97827 | -0.41875 | 0.97795 | -0.42509 | 3.7095
23 | -0.010565 | -0.0026494 | 0.010566 | 0.0026501 | 1.4823e-06 | 7.5601e-07 | 0.016061 | 0.016061 | 0.016061 | 0.97885 | -0.40736 | 0.979 | -0.40441 | 4.4123
24 | 0.0088742 | 0.0022236 | -0.0088741 | -0.0022236 | 4.5736e-08 | 2.0878e-08 | 0.013502 | 0.013502 | 0.013502 | 0.97795 | -0.42509 | 0.97795 | -0.42519 | 3.7095
25 | -0.012144 | -0.0030454 | 0.012144 | 0.0030456 | 3.2945e-07 | 1.7842e-07 | 0.018458 | 0.018458 | 0.018458 | 0.979 | -0.40441 | 0.97903 | -0.40384 | 5.0709
26 | 0.0050267 | 0.0012594 | -0.0050261 | -0.0012593 | 6.3132e-07 | 4.3008e-08 | 0.0076484 | 0.0076485 | 0.0076485 | 0.97795 | -0.42519 | 0.97781 | -0.42783 | 2.1012
27 | -0.013137 | -0.0032946 | 0.013141 | 0.0032964 | 3.2544e-06 | 1.809e-06 | 0.019968 | 0.019968 | 0.019968 | 0.97903 | -0.40384 | 0.9793 | -0.39865 | 5.4857
28 | 0.0038507 | 0.00096473 | -0.0038505 | -0.00096482 | 2.491e-07 | -8.3209e-08 | 0.0058599 | 0.00586 | 0.00586 | 0.97781 | -0.42783 | 0.97774 | -0.42919 | 1.6099
29 | -0.015431 | -0.0038705 | 0.015431 | 0.0038706 | 1.523e-07 | 8.8177e-08 | 0.023448 | 0.023448 | 0.023448 | 0.9793 | -0.39865 | 0.97931 | -0.39844 | 6.4419
30 | 0.0018343 | 0.00045951 | -0.0018342 | -0.0004597 | 5.3097e-08 | -1.9389e-07 | 0.0027915 | 0.0027916 | 0.0027916 | 0.97774 | -0.42919 | 0.97771 | -0.4298 | 0.76692
31 | -0.047349 | -0.011881 | 0.047351 | 0.011882 | 1.8376e-06 | 1.1641e-06 | 0.07184 | 0.07184 | 0.07184 | 0.98081 | -0.36908 | 0.98085 | -0.36826 | 19.7362
32 | 0.029414 | 0.0073862 | -0.029405 | -0.0073807 | 8.7891e-06 | 5.4766e-06 | 0.04463 | 0.04463 | 0.04463 | 0.98081 | -0.36908 | 0.98049 | -0.37534 | 12.2609
33 | -0.049349 | -0.012383 | 0.049428 | 0.012433 | 7.8266e-05 | 4.9619e-05 | 0.074872 | 0.074872 | 0.074872 | 0.98085 | -0.36826 | 0.98255 | -0.33506 | 20.5692
34 | 0.0050478 | 0.0012648 | -0.0050475 | -0.0012647 | 2.8852e-07 | 1.9309e-08 | 0.0076605 | 0.0076606 | 0.0076606 | 0.98049 | -0.37534 | 0.98043 | -0.37654 | 2.1046
35 | 0.024357 | 0.006116 | -0.024341 | -0.0061062 | 1.5935e-05 | 9.8065e-06 | 0.036969 | 0.036969 | 0.036969 | 0.98049 | -0.37534 | 0.97979 | -0.38906 | 10.1564
36 | -0.049428 | -0.012433 | 0.049492 | 0.012474 | 6.4816e-05 | 4.1091e-05 | 0.074872 | 0.074871 | 0.074872 | 0.98255 | -0.33506 | 0.98395 | -0.30765 | 20.5691
37 | 0.0042352 | 0.0010612 | -0.004235 | -0.0010612 | 2.4938e-07 | -4.3357e-08 | 0.0064278 | 0.0064279 | 0.0064279 | 0.98043 | -0.37654 | 0.98036 | -0.37778 | 1.7659
38 | 0.022139 | 0.0055543 | -0.022137 | -0.0055531 | 2.0325e-06 | 1.2404e-06 | 0.033625 | 0.033625 | 0.033625 | 0.97979 | -0.38906 | 0.97969 | -0.39099 | 9.2378
39 | 0.0020429 | 0.00051147 | -0.0020428 | -0.00051196 | 1.6788e-07 | -4.8826e-07 | 0.0030893 | 0.0030895 | 0.0030895 | 0.98395 | -0.30765 | 0.98387 | -0.30937 | 0.84876
40 | -0.051535 | -0.012985 | 0.051811 | 0.01316 | 0.00027599 | 0.00017509 | 0.077961 | 0.07796 | 0.077961 | 0.98395 | -0.30765 | 0.98971 | -0.19634 | 21.4178
41 | 0.0027001 | 0.00067654 | -0.0027 | -0.00067669 | 1.1027e-07 | -1.5017e-07 | 0.0040983 | 0.0040983 | 0.0040983 | 0.98036 | -0.37778 | 0.98032 | -0.37863 | 1.1259
42 | 0.017703 | 0.004442 | -0.017697 | -0.0044387 | 5.4746e-06 | 3.2496e-06 | 0.02689 | 0.02689 | 0.02689 | 0.97969 | -0.39099 | 0.97936 | -0.39748 | 7.3874
43 | 0.0044346 | 0.0011111 | -0.0044342 | -0.0011111 | 3.6696e-07 | -3.6726e-08 | 0.0067354 | 0.0067355 | 0.0067355 | 0.97969 | -0.39099 | 0.9796 | -0.39273 | 1.8504
44 | 0.11324 | 0.028706 | -0.11305 | -0.028587 | 0.00018822 | 0.00011846 | 0.17037 | 0.17037 | 0.17037 | 0.98971 | -0.19634 | 0.98791 | -0.23098 | 15.6017
45 | 0.016658 | 0.0041782 | -0.016657 | -0.0041778 | 7.6556e-07 | 4.4986e-07 | 0.025311 | 0.025311 | 0.025311 | 0.97936 | -0.39748 | 0.97931 | -0.39844 | 6.9535
46 | 0.0030664 | 0.00076834 | -0.0030662 | -0.00076847 | 1.4382e-07 | -1.3049e-07 | 0.0046578 | 0.0046579 | 0.0046579 | 0.9796 | -0.39273 | 0.97955 | -0.39371 | 1.2796
47 | 0.1111 | 0.028098 | -0.11096 | -0.028011 | 0.00013802 | 8.6823e-05 | 0.16743 | 0.16743 | 0.16743 | 0.98791 | -0.23098 | 0.98657 | -0.25692 | 15.3323
48 | -0.044553 | -0.011224 | 0.044585 | 0.011243 | 3.1795e-05 | 1.9412e-05 | 0.067624 | 0.067623 | 0.067624 | 0.98066 | -0.37185 | 0.98143 | -0.35694 | 9.2889
49 | -0.055961 | -0.014094 | 0.055971 | 0.014101 | 1.0181e-05 | 6.0869e-06 | 0.084872 | 0.084872 | 0.084872 | 0.98143 | -0.35694 | 0.98162 | -0.35314 | 7.7722
50 | -0.060255 | -0.015174 | 0.060263 | 0.015179 | 7.2202e-06 | 4.3585e-06 | 0.091366 | 0.091366 | 0.091366 | 0.98162 | -0.35314 | 0.98175 | -0.35063 | 8.3668
51 | -0.060263 | -0.015179 | 0.060328 | 0.015218 | 6.5817e-05 | 3.9727e-05 | 0.091366 | 0.091365 | 0.091366 | 0.98175 | -0.35063 | 0.98292 | -0.32782 | 8.3668
52 | -0.069307 | -0.017469 | 0.069389 | 0.017518 | 8.1519e-05 | 4.9918e-05 | 0.10496 | 0.10496 | 0.10496 | 0.98292 | -0.32782 | 0.98418 | -0.30327 | 9.6115
53 | -0.089188 | -0.022481 | 0.089382 | 0.022602 | 0.00019412 | 0.00012097 | 0.13489 | 0.13489 | 0.13489 | 0.98418 | -0.30327 | 0.98652 | -0.25789 | 12.3527
54 | -0.091871 | -0.023225 | 0.091875 | 0.023228 | 4.2719e-06 | 2.6659e-06 | 0.13864 | 0.13864 | 0.13864 | 0.98652 | -0.25789 | 0.98657 | -0.25692 | 12.6963

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3468 | 0.08796

## res_load
| p_mw | q_mvar
0 | 0.0057763 | 0.0014477
1 | 0.00050534 | 0.00012665
2 | 0.016545 | 0.0041465
3 | 0.0027089 | 0.0006789
4 | 0.0013449 | 0.00033707
5 | 0.0051252 | 0.0012845
6 | 0.0014998 | 0.00037588
7 | 0.078146 | 0.019585
8 | 0.022428 | 0.005621
9 | 0.01733 | 0.0043432
10 | 0.023107 | 0.0057911
11 | 0.014751 | 0.0036968
12 | 0.021848 | 0.0054757
13 | 0.0016821 | 0.00042158
14 | 0.0015773 | 0.00039531
15 | 0.0038474 | 0.00096425
16 | 0.0009935 | 0.00024899
17 | 0.0011754 | 0.00029457
18 | 0.0022906 | 0.00057407
19 | 0.0020162 | 0.00050531
20 | 0.017935 | 0.0044949
21 | 0.0019987 | 0.00050092
22 | 0.00081225 | 0.00020357
23 | 0.0022018 | 0.00055183
24 | 0.0015349 | 0.00038467
25 | 0.0020428 | 0.00051196
26 | 0.0027 | 0.00067669
27 | 0.0010395 | 0.00026052
28 | 0.0013678 | 0.00034281
29 | 0.0019532 | 0.00048952
30 | 0.0030662 | 0.00076847
31 | 0.0012257 | 0.00030719
32 | 0.007124 | 0.0017854
33 | 0.011377 | 0.0028512
34 | 0.0042839 | 0.0010736
35 | 0.0089787 | 0.0022503
36 | 0.019799 | 0.0049622
37 | 0.0024886 | 0.00062369
38 | 0.019085 | 0.0047831
39 | 0.0037623 | 0.00094291
40 | 0.0018342 | 0.0004597

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1