## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2556-7_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2556-7_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2556-7_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2556-7_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2556-7_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2556-7_0_6_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_2556-7_0_6_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2556-7_0_6_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_2556-7_0_6_node_87 | 0.4 | n |  | TRUE
9 | bus_LV_2556-7_0_6_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_2556-7_0_6_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_2556-7_0_6_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2556-7_0_6_node_90 | 0.4 | n |  | TRUE
13 | bus_LV_2556-7_0_6_node_115 | 0.4 | n |  | TRUE
14 | bus_LV_2556-7_0_6_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_2556-7_0_6_node_86 | 0.4 | n |  | TRUE
16 | bus_LV_2556-7_0_6_node_80 | 0.4 | n |  | TRUE
17 | bus_LV_2556-7_0_6_node_85 | 0.4 | n |  | TRUE
18 | bus_LV_2556-7_0_6_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_2556-7_0_6_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2556-7_0_6_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_2556-7_0_6_node_7 | 0.4 | n |  | TRUE
22 | bus_LV_2556-7_0_6_node_9 | 0.4 | n |  | TRUE
23 | bus_LV_2556-7_0_6_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_2556-7_0_6_node_92 | 0.4 | n |  | TRUE
25 | bus_LV_2556-7_0_6_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_2556-7_0_6_node_100 | 0.4 | n |  | TRUE
27 | bus_LV_2556-7_0_6_node_101 | 0.4 | n |  | TRUE
28 | bus_LV_2556-7_0_6_node_91 | 0.4 | n |  | TRUE
29 | bus_LV_2556-7_0_6_node_57 | 0.4 | n |  | TRUE
30 | bus_LV_2556-7_0_6_node_102 | 0.4 | n |  | TRUE
31 | bus_LV_2556-7_0_6_node_96 | 0.4 | n |  | TRUE
32 | bus_LV_2556-7_0_6_node_97 | 0.4 | n |  | TRUE
33 | bus_LV_2556-7_0_6_node_14 | 0.4 | n |  | TRUE
34 | bus_LV_2556-7_0_6_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_2556-7_0_6_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_2556-7_0_6_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_2556-7_0_6_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_2556-7_0_6_node_114 | 0.4 | n |  | TRUE
39 | bus_LV_2556-7_0_6_node_103 | 0.4 | n |  | TRUE
40 | bus_LV_2556-7_0_6_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_2556-7_0_6_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_2556-7_0_6_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_2556-7_0_6_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_2556-7_0_6_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_2556-7_0_6_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_2556-7_0_6_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_2556-7_0_6_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_2556-7_0_6_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_2556-7_0_6_node_27 | 0.4 | n |  | TRUE
50 | bus_LV_2556-7_0_6_node_28 | 0.4 | n |  | TRUE
51 | bus_LV_2556-7_0_6_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_2556-7_0_6_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_2556-7_0_6_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_2556-7_0_6_node_82 | 0.4 | n |  | TRUE
55 | bus_LV_2556-7_0_6_node_83 | 0.4 | n |  | TRUE
56 | bus_LV_2556-7_0_6_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_2556-7_0_6_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_2556-7_0_6_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_2556-7_0_6_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_2556-7_0_6_node_40 | 0.4 | n |  | TRUE
61 | bus_LV_2556-7_0_6_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_2556-7_0_6_node_42 | 0.4 | n |  | TRUE
63 | bus_LV_2556-7_0_6_node_60 | 0.4 | n |  | TRUE
64 | bus_LV_2556-7_0_6_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_2556-7_0_6_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_2556-7_0_6_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_2556-7_0_6_node_79 | 0.4 | n |  | TRUE
68 | bus_LV_2556-7_0_6_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_2556-7_0_6_node_45 | 0.4 | n |  | TRUE
70 | bus_LV_2556-7_0_6_node_48 | 0.4 | n |  | TRUE
71 | bus_LV_2556-7_0_6_node_70 | 0.4 | n |  | TRUE
72 | bus_LV_2556-7_0_6_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_2556-7_0_6_node_75 | 0.4 | n |  | TRUE
74 | bus_LV_2556-7_0_6_node_67 | 0.4 | n |  | TRUE
75 | bus_LV_2556-7_0_6_node_62 | 0.4 | n |  | TRUE
76 | bus_LV_2556-7_0_6_node_50 | 0.4 | n |  | TRUE
77 | bus_LV_2556-7_0_6_node_51 | 0.4 | n |  | TRUE
78 | bus_LV_2556-7_0_6_node_52 | 0.4 | n |  | TRUE
79 | bus_LV_2556-7_0_6_node_54 | 0.4 | n |  | TRUE
80 | bus_LV_2556-7_0_6_node_89 | 0.4 | n |  | TRUE
81 | bus_LV_2556-7_0_6_node_93 | 0.4 | n |  | TRUE
82 | bus_LV_2556-7_0_6_node_55 | 0.4 | n |  | TRUE
83 | bus_LV_2556-7_0_6_node_56 | 0.4 | n |  | TRUE
84 | bus_LV_2556-7_0_6_node_61 | 0.4 | n |  | TRUE
85 | bus_LV_2556-7_0_6_node_63 | 0.4 | n |  | TRUE
86 | bus_LV_2556-7_0_6_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_2556-7_0_6_node_65 | 0.4 | n |  | TRUE
88 | bus_LV_2556-7_0_6_node_66 | 0.4 | n |  | TRUE
89 | bus_LV_2556-7_0_6_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_2556-7_0_6_node_72 | 0.4 | n |  | TRUE
91 | bus_LV_2556-7_0_6_node_71 | 0.4 | n |  | TRUE
92 | bus_LV_2556-7_0_6_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_2556-7_0_6_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_2556-7_0_6_node_74 | 0.4 | n |  | TRUE
95 | bus_LV_2556-7_0_6_node_81 | 0.4 | n |  | TRUE
96 | bus_LV_2556-7_0_6_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_2556-7_0_6_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_2556-7_0_6_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_2556-7_0_6_node_84 | 0.4 | n |  | TRUE
100 | bus_LV_2556-7_0_6_node_116 | 0.4 | n |  | TRUE
101 | bus_LV_2556-7_0_6_node_94 | 0.4 | n |  | TRUE
102 | bus_LV_2556-7_0_6_node_95 | 0.4 | n |  | TRUE
103 | bus_LV_2556-7_0_6_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_2556-7_0_6_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_2556-7_0_6_node_107 | 0.4 | n |  | TRUE
106 | bus_LV_2556-7_0_6_node_104 | 0.4 | n |  | TRUE
107 | bus_LV_2556-7_0_6_node_118 | 0.4 | n |  | TRUE
108 | bus_LV_2556-7_0_6_node_121 | 0.4 | n |  | TRUE
109 | bus_LV_2556-7_0_6_node_105 | 0.4 | n |  | TRUE
110 | bus_LV_2556-7_0_6_node_106 | 0.4 | n |  | TRUE
111 | bus_LV_2556-7_0_6_node_125 | 0.4 | n |  | TRUE
112 | bus_LV_2556-7_0_6_node_111 | 0.4 | n |  | TRUE
113 | bus_LV_2556-7_0_6_node_119 | 0.4 | n |  | TRUE
114 | bus_LV_2556-7_0_6_node_108 | 0.4 | n |  | TRUE
115 | bus_LV_2556-7_0_6_node_109 | 0.4 | n |  | TRUE
116 | bus_LV_2556-7_0_6_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_2556-7_0_6_node_112 | 0.4 | n |  | TRUE
118 | bus_LV_2556-7_0_6_node_126 | 0.4 | n |  | TRUE
119 | bus_LV_2556-7_0_6_node_123 | 0.4 | n |  | TRUE
120 | bus_LV_2556-7_0_6_node_117 | 0.4 | n |  | TRUE
121 | bus_LV_2556-7_0_6_node_120 | 0.4 | n |  | TRUE
122 | bus_LV_2556-7_0_6_node_129 | 0.4 | n |  | TRUE
123 | bus_LV_2556-7_0_6_node_127 | 0.4 | n |  | TRUE
124 | bus_LV_2556-7_0_6_node_128 | 0.4 | n |  | TRUE
125 | bus_MV_396_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2556-7_0_6_load_0 | 0 | 0.003168 | 0.00079398 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2556-7_0_6_load_1 | 1 | 0.002678 | 0.00067116 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2556-7_0_6_load_2 | 2 | 0.0021676 | 0.00054324 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2556-7_0_6_load_3 | 3 | 0.0054033 | 0.0013542 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2556-7_0_6_load_4 | 4 | 0.0041992 | 0.0010524 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2556-7_0_6_load_87 | 8 | 0.0046964 | 0.001177 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2556-7_0_6_load_11 | 9 | 0.0057471 | 0.0014404 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2556-7_0_6_load_6 | 11 | 0.0017951 | 0.0004499 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2556-7_0_6_load_115 | 13 | 0.0026796 | 0.00067158 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2556-7_0_6_load_85 | 17 | 0.0046965 | 0.001177 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2556-7_0_6_load_18 | 18 | 0.002074 | 0.00051981 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2556-7_0_6_load_13 | 19 | 0.0050422 | 0.0012637 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2556-7_0_6_load_34 | 20 | 0.0024319 | 0.00060949 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2556-7_0_6_load_9 | 22 | 0.0039589 | 0.0009922 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2556-7_0_6_load_10 | 23 | 0.0043053 | 0.001079 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2556-7_0_6_load_92 | 24 | 0.0020329 | 0.00050951 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2556-7_0_6_load_59 | 25 | 0.0029076 | 0.00072871 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2556-7_0_6_load_100 | 26 | 0.0040675 | 0.0010194 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2556-7_0_6_load_101 | 27 | 0.010279 | 0.0025763 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2556-7_0_6_load_57 | 29 | 0.003413 | 0.00085537 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2556-7_0_6_load_102 | 30 | 0.014229 | 0.0035661 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2556-7_0_6_load_96 | 31 | 0.0089664 | 0.0022472 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2556-7_0_6_load_16 | 34 | 0.0018787 | 0.00047084 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2556-7_0_6_load_32 | 37 | 0.0015738 | 0.00039442 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2556-7_0_6_load_114 | 38 | 0.0024259 | 0.00060799 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2556-7_0_6_load_103 | 39 | 0.0035849 | 0.00089847 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2556-7_0_6_load_21 | 40 | 0.0061981 | 0.0015534 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2556-7_0_6_load_22 | 41 | 0.038615 | 0.0096778 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2556-7_0_6_load_23 | 42 | 0.00071011 | 0.00017797 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2556-7_0_6_load_25 | 44 | 0.00059171 | 0.0001483 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2556-7_0_6_load_26 | 45 | 0.0017547 | 0.00043976 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2556-7_0_6_load_35 | 47 | 0.0057006 | 0.0014287 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2556-7_0_6_load_29 | 48 | 0.005471 | 0.0013712 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2556-7_0_6_load_27 | 49 | 0.011686 | 0.0029288 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2556-7_0_6_load_28 | 50 | 0.0083221 | 0.0020857 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2556-7_0_6_load_82 | 54 | 0.0020007 | 0.00050142 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2556-7_0_6_load_83 | 55 | 0.0036626 | 0.00091794 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2556-7_0_6_load_36 | 56 | 0.012991 | 0.0032558 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2556-7_0_6_load_37 | 57 | 0.0020507 | 0.00051396 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2556-7_0_6_load_38 | 58 | 0.012856 | 0.0032221 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2556-7_0_6_load_39 | 59 | 0.0013667 | 0.00034252 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2556-7_0_6_load_40 | 60 | 0.007331 | 0.0018373 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2556-7_0_6_load_42 | 62 | 0.016912 | 0.0042386 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2556-7_0_6_load_60 | 63 | 0.0046089 | 0.0011551 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2556-7_0_6_load_41 | 64 | 0.017219 | 0.0043155 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2556-7_0_6_load_43 | 65 | 0.018063 | 0.004527 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2556-7_0_6_load_44 | 66 | 0.049605 | 0.012432 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2556-7_0_6_load_79 | 67 | 0.017805 | 0.0044624 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2556-7_0_6_load_45 | 69 | 0.0016485 | 0.00041315 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2556-7_0_6_load_70 | 71 | 0.0037323 | 0.00093541 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2556-7_0_6_load_69 | 72 | 0.0033943 | 0.00085069 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2556-7_0_6_load_75 | 73 | 0.0018319 | 0.00045913 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2556-7_0_6_load_67 | 74 | 0.0010181 | 0.00025517 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2556-7_0_6_load_62 | 75 | 0.0020496 | 0.00051367 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2556-7_0_6_load_50 | 76 | 0.0020633 | 0.00051711 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2556-7_0_6_load_51 | 77 | 0.0028446 | 0.00071293 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2556-7_0_6_load_52 | 78 | 0.0051098 | 0.0012806 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2556-7_0_6_load_54 | 79 | 0.0019553 | 0.00049006 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2556-7_0_6_load_89 | 80 | 0.016492 | 0.0041332 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2556-7_0_6_load_93 | 81 | 0.008303 | 0.0020809 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2556-7_0_6_load_55 | 82 | 0.0084471 | 0.002117 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2556-7_0_6_load_56 | 83 | 0.0065734 | 0.0016474 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2556-7_0_6_load_61 | 84 | 0.0057431 | 0.0014393 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2556-7_0_6_load_63 | 85 | 0.00042324 | 0.00010607 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2556-7_0_6_load_68 | 89 | 0.00096543 | 0.00024196 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2556-7_0_6_load_72 | 90 | 0.0016162 | 0.00040507 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2556-7_0_6_load_71 | 91 | 0.0034885 | 0.00087429 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2556-7_0_6_load_73 | 92 | 0.0017986 | 0.00045077 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2556-7_0_6_load_74 | 94 | 0.0024476 | 0.00061343 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2556-7_0_6_load_81 | 95 | 0.0023312 | 0.00058424 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2556-7_0_6_load_78 | 96 | 0.00092654 | 0.00023221 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2556-7_0_6_load_77 | 97 | 0.016057 | 0.0040243 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2556-7_0_6_load_88 | 98 | 0.023448 | 0.0058765 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2556-7_0_6_load_84 | 99 | 0.0031823 | 0.00079757 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2556-7_0_6_load_116 | 100 | 0.0018068 | 0.00045283 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2556-7_0_6_load_94 | 101 | 0.002741 | 0.00068695 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2556-7_0_6_load_95 | 102 | 0.0067039 | 0.0016802 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2556-7_0_6_load_99 | 104 | 0.0053016 | 0.0013287 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2556-7_0_6_load_107 | 105 | 0.0029724 | 0.00074494 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2556-7_0_6_load_104 | 106 | 0.001467 | 0.00036766 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2556-7_0_6_load_118 | 107 | 0.0022277 | 0.00055833 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2556-7_0_6_load_105 | 109 | 0.00036084 | 9.0435e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2556-7_0_6_load_106 | 110 | 0.00012491 | 3.1305e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2556-7_0_6_load_125 | 111 | 0.00027548 | 6.9043e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2556-7_0_6_load_111 | 112 | 0.000143 | 3.584e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2556-7_0_6_load_108 | 114 | 0.0011467 | 0.00028738 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2556-7_0_6_load_109 | 115 | 0.0012718 | 0.00031875 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2556-7_0_6_load_110 | 116 | 0.00033914 | 8.4998e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2556-7_0_6_load_112 | 117 | 0.001811 | 0.00045388 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2556-7_0_6_load_117 | 120 | 0.0046988 | 0.0011776 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2556-7_0_6_load_129 | 122 | 0.0031351 | 0.00078573 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2556-7_0_6_load_127 | 123 | 0.0011753 | 0.00029456 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2556-7_0_6_load_128 | 124 | 0.007143 | 0.0017902 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 65 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2556-7_0_6_line_0 |  | 0 | 1 | 0.029973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2556-7_0_6_line_1 |  | 0 | 2 | 0.013552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2556-7_0_6_line_2 |  | 1 | 3 | 0.026817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2556-7_0_6_line_3 |  | 2 | 4 | 0.017216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2556-7_0_6_line_4 |  | 4 | 5 | 0.015325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2556-7_0_6_line_5 |  | 5 | 9 | 0.044321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2556-7_0_6_line_6 |  | 5 | 10 | 0.033643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2556-7_0_6_line_7 |  | 5 | 11 | 0.037008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2556-7_0_6_line_8 |  | 6 | 7 | 0.011479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2556-7_0_6_line_9 |  | 6 | 8 | 0.019593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2556-7_0_6_line_10 |  | 7 | 18 | 0.059671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2556-7_0_6_line_11 |  | 7 | 14 | 0.005913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2556-7_0_6_line_12 |  | 7 | 19 | 0.042319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2556-7_0_6_line_13 |  | 8 | 20 | 0.043375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2556-7_0_6_line_14 |  | 10 | 26 | 0.017382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_2556-7_0_6_line_15 |  | 10 | 27 | 0.039431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2556-7_0_6_line_16 |  | 11 | 21 | 0.013727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2556-7_0_6_line_17 |  | 12 | 13 | 0.033415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2556-7_0_6_line_18 |  | 12 | 14 | 0.019511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2556-7_0_6_line_19 |  | 13 | 100 | 0.049187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2556-7_0_6_line_20 |  | 14 | 39 | 0.031949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2556-7_0_6_line_21 |  | 15 | 16 | 0.009707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2556-7_0_6_line_22 |  | 15 | 17 | 0.025348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2556-7_0_6_line_23 |  | 16 | 80 | 0.015278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2556-7_0_6_line_24 |  | 16 | 68 | 0.038531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2556-7_0_6_line_25 |  | 17 | 99 | 0.030623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2556-7_0_6_line_26 |  | 18 | 38 | 0.00065642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2556-7_0_6_line_27 |  | 20 | 35 | 0.037628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2556-7_0_6_line_28 |  | 21 | 22 | 0.021655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2556-7_0_6_line_29 |  | 21 | 23 | 0.034755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2556-7_0_6_line_30 |  | 22 | 24 | 0.013425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2556-7_0_6_line_31 |  | 23 | 25 | 0.03572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2556-7_0_6_line_32 |  | 24 | 28 | 0.0040054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_2556-7_0_6_line_33 |  | 25 | 29 | 0.026156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2556-7_0_6_line_34 |  | 26 | 30 | 0.029144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_2556-7_0_6_line_35 |  | 28 | 81 | 0.039172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2556-7_0_6_line_36 |  | 28 | 79 | 0.015794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_2556-7_0_6_line_37 |  | 29 | 82 | 0.036123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2556-7_0_6_line_38 |  | 30 | 39 | 0.03607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_2556-7_0_6_line_39 |  | 31 | 32 | 0.015398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2556-7_0_6_line_40 |  | 32 | 103 | 0.005872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2556-7_0_6_line_41 |  | 32 | 104 | 0.015459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2556-7_0_6_line_42 |  | 33 | 34 | 0.016531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2556-7_0_6_line_43 |  | 33 | 35 | 0.020177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2556-7_0_6_line_44 |  | 34 | 36 | 0.045168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2556-7_0_6_line_45 |  | 35 | 37 | 0.025732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2556-7_0_6_line_46 |  | 36 | 40 | 0.046708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2556-7_0_6_line_47 |  | 41 | 42 | 0.010598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2556-7_0_6_line_48 |  | 41 | 43 | 0.06356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2556-7_0_6_line_49 |  | 42 | 44 | 0.032262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2556-7_0_6_line_50 |  | 43 | 45 | 0.088268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2556-7_0_6_line_51 |  | 44 | 46 | 0.048135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2556-7_0_6_line_52 |  | 45 | 47 | 0.042914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2556-7_0_6_line_53 |  | 46 | 48 | 0.020034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2556-7_0_6_line_54 |  | 48 | 49 | 0.054024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2556-7_0_6_line_55 |  | 49 | 50 | 0.054205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2556-7_0_6_line_56 |  | 50 | 51 | 0.048425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2556-7_0_6_line_57 |  | 51 | 52 | 0.049184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2556-7_0_6_line_58 |  | 52 | 53 | 0.003507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2556-7_0_6_line_59 |  | 53 | 70 | 0.026177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2556-7_0_6_line_60 |  | 53 | 61 | 0.034003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2556-7_0_6_line_61 |  | 53 | 69 | 0.0045107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2556-7_0_6_line_62 |  | 54 | 55 | 0.0062758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2556-7_0_6_line_63 |  | 55 | 99 | 0.020952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2556-7_0_6_line_64 |  | 56 | 57 | 0.032664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_2556-7_0_6_line_65 |  | 56 | 58 | 0.016008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_2556-7_0_6_line_66 |  | 57 | 59 | 0.0001517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2556-7_0_6_line_67 |  | 58 | 60 | 0.0047051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2556-7_0_6_line_68 |  | 59 | 61 | 0.032788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2556-7_0_6_line_69 |  | 60 | 62 | 0.0064174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_2556-7_0_6_line_70 |  | 61 | 63 | 0.03892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2556-7_0_6_line_71 |  | 62 | 64 | 0.0034264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_2556-7_0_6_line_72 |  | 63 | 75 | 0.0012741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2556-7_0_6_line_73 |  | 64 | 65 | 0.021451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_2556-7_0_6_line_74 |  | 65 | 66 | 0.013182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_2556-7_0_6_line_75 |  | 66 | 67 | 0.014608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_2556-7_0_6_line_76 |  | 67 | 68 | 0.014303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_2556-7_0_6_line_77 |  | 68 | 77 | 0.0032957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_2556-7_0_6_line_78 |  | 70 | 71 | 0.027361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2556-7_0_6_line_79 |  | 70 | 72 | 0.010935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2556-7_0_6_line_80 |  | 71 | 73 | 0.0049303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2556-7_0_6_line_81 |  | 72 | 74 | 0.013068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2556-7_0_6_line_82 |  | 73 | 93 | 0.019235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2556-7_0_6_line_83 |  | 74 | 87 | 0.042976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2556-7_0_6_line_84 |  | 75 | 84 | 0.031437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2556-7_0_6_line_85 |  | 76 | 77 | 0.029787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_2556-7_0_6_line_86 |  | 76 | 78 | 0.0032583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2556-7_0_6_line_87 |  | 78 | 79 | 0.014548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_2556-7_0_6_line_88 |  | 80 | 98 | 0.024629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2556-7_0_6_line_89 |  | 81 | 101 | 0.012059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2556-7_0_6_line_90 |  | 82 | 83 | 0.0040512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2556-7_0_6_line_91 |  | 85 | 86 | 0.018682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2556-7_0_6_line_92 |  | 85 | 87 | 0.017179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2556-7_0_6_line_93 |  | 86 | 88 | 0.035416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2556-7_0_6_line_94 |  | 87 | 89 | 0.027277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2556-7_0_6_line_95 |  | 88 | 90 | 0.054561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2556-7_0_6_line_96 |  | 89 | 91 | 0.038897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2556-7_0_6_line_97 |  | 90 | 92 | 0.01386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2556-7_0_6_line_98 |  | 92 | 94 | 0.014451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2556-7_0_6_line_99 |  | 93 | 96 | 0.020974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2556-7_0_6_line_100 |  | 94 | 95 | 0.0080466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2556-7_0_6_line_101 |  | 97 | 98 | 0.016567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2556-7_0_6_line_102 |  | 100 | 120 | 0.007877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2556-7_0_6_line_103 |  | 101 | 102 | 0.015672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2556-7_0_6_line_104 |  | 103 | 105 | 0.019795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2556-7_0_6_line_105 |  | 103 | 106 | 0.036543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2556-7_0_6_line_106 |  | 104 | 107 | 0.01171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2556-7_0_6_line_107 |  | 105 | 108 | 0.013435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2556-7_0_6_line_108 |  | 106 | 109 | 0.014533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2556-7_0_6_line_109 |  | 108 | 113 | 0.038424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2556-7_0_6_line_110 |  | 109 | 110 | 0.012842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2556-7_0_6_line_111 |  | 110 | 111 | 0.0091041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2556-7_0_6_line_112 |  | 111 | 112 | 0.016724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2556-7_0_6_line_113 |  | 112 | 115 | 0.017337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2556-7_0_6_line_114 |  | 113 | 121 | 0.041637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2556-7_0_6_line_115 |  | 113 | 120 | 0.041353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2556-7_0_6_line_116 |  | 114 | 115 | 0.0073365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2556-7_0_6_line_117 |  | 114 | 116 | 0.0059664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2556-7_0_6_line_118 |  | 116 | 117 | 0.0010499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2556-7_0_6_line_119 |  | 117 | 118 | 0.060151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2556-7_0_6_line_120 |  | 118 | 119 | 0.063741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2556-7_0_6_line_121 |  | 119 | 123 | 0.031787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2556-7_0_6_line_122 |  | 121 | 122 | 0.033068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2556-7_0_6_line_123 |  | 123 | 124 | 0.016783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2556-7_0_6_trafo_43 | 0.63 MVA 20/0.4 kV | 125 | 65 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2601394.2124 | 1227996.9345 | 2601371.7802 | 1227990.3575 | 2601365.403 | 1227988.6709
1 | 2601394.2124 | 1227996.9345 | 2601407.2173 | 1228000.7475
2 | 2601365.403 | 1227988.6709 | 2601339.4774 | 1227981.8143
3 | 2601423.8267 | 1228005.2721 | 2601411.1321 | 1228001.8953 | 2601407.2173 | 1228000.7475
4 | 2601438.9076 | 1228007.7828 | 2601428.9518 | 1228006.6354 | 2601423.8267 | 1228005.2721
5 | 2601438.9076 | 1228007.7828 | 2601451.6894 | 1228009.4312 | 2601474.7218 | 1228014.5507 | 2601482.2723 | 1228016.6582
6 | 2601415.8645 | 1228015.849 | 2601417.3055 | 1228009.4011 | 2601438.0273 | 1228013.6083 | 2601438.9076 | 1228007.7828
7 | 2601438.9076 | 1228007.7828 | 2601440.0306 | 1228000.3231 | 2601451.6046 | 1227973.2276
8 | 2601299.8011 | 1227983.8717 | 2601301.8784 | 1227977.9353 | 2601303.4478 | 1227972.9883
9 | 2601303.4478 | 1227972.9883 | 2601284.464 | 1227968.1393
10 | 2601299.8011 | 1227983.8717 | 2601282.8796 | 1228032.1189 | 2601288.3664 | 1228038.6657
11 | 2601305.5365 | 1227985.3738 | 2601299.8011 | 1227983.8717
12 | 2601299.8011 | 1227983.8717 | 2601267.2297 | 1227975.3489 | 2601258.8484 | 1227973.2048
13 | 2601242.6725 | 1227956.6136 | 2601249.4271 | 1227959.0135 | 2601266.4213 | 1227963.5307 | 2601284.464 | 1227968.1393
14 | 2601415.8645 | 1228015.849 | 2601398.9677 | 1228011.7727
15 | 2601415.8645 | 1228015.849 | 2601424.5546 | 1228017.9411 | 2601447.7086 | 1228021.8487 | 2601454.5099 | 1228023.5505
16 | 2601456.997 | 1227960.6036 | 2601451.6046 | 1227973.2276
17 | 2601313.3228 | 1227998.2941 | 2601313.207 | 1228008.8003 | 2601313.9395 | 1228020.3629 | 2601315.0321 | 1228031.6323
18 | 2601313.3228 | 1227998.2941 | 2601305.7007 | 1227997.203 | 2601305.5664 | 1227987.1749 | 2601305.5365 | 1227985.3738
19 | 2601315.0321 | 1228031.6323 | 2601319.7786 | 1228080.5894
20 | 2601305.5365 | 1227985.3738 | 2601336.4441 | 1227993.4632
21 | 2601322.0392 | 1227912.4008 | 2601324.8067 | 1227903.0959
22 | 2601322.0392 | 1227912.4008 | 2601314.7277 | 1227910.6872 | 2601297.3747 | 1227906.5543
23 | 2601324.8067 | 1227903.0959 | 2601328.8025 | 1227890.3003 | 2601329.3093 | 1227888.4969
24 | 2601324.8067 | 1227903.0959 | 2601333.6788 | 1227905.766 | 2601351.7411 | 1227911.8846 | 2601361.4313 | 1227915.3666
25 | 2601268.0343 | 1227897.9459 | 2601281.6027 | 1227902.7979 | 2601297.3747 | 1227906.5543
26 | 2601288.7881 | 1228039.1688 | 2601288.3664 | 1228038.6657
27 | 2601206.9004 | 1227945.1971 | 2601226.6223 | 1227950.2706 | 2601237.1231 | 1227954.6419 | 2601242.6725 | 1227956.6136
28 | 2601456.997 | 1227960.6036 | 2601437.7015 | 1227950.7746
29 | 2601456.997 | 1227960.6036 | 2601471.4704 | 1227929.006
30 | 2601425.7388 | 1227944.6809 | 2601437.7015 | 1227950.7746
31 | 2601486.3935 | 1227896.553 | 2601476.601 | 1227917.8052 | 2601471.4704 | 1227929.006
32 | 2601422.1698 | 1227942.8629 | 2601425.7388 | 1227944.6809
33 | 2601497.3396 | 1227872.7971 | 2601486.3935 | 1227896.553
34 | 2601398.9677 | 1228011.7727 | 2601391.7865 | 1228010.0402 | 2601380.2628 | 1228006.5467 | 2601371.2044 | 1228003.0352
35 | 2601422.1698 | 1227942.8629 | 2601436.9148 | 1227906.5715
36 | 2601422.1698 | 1227942.8629 | 2601414.4043 | 1227938.9033 | 2601407.9366 | 1227936.0296
37 | 2601510.9819 | 1227839.3656 | 2601506.0989 | 1227852.4959 | 2601500.7009 | 1227865.5023 | 2601497.3396 | 1227872.7971
38 | 2601336.4441 | 1227993.4632 | 2601357.0186 | 1227998.8482 | 2601368.6409 | 1228002.0415 | 2601371.2044 | 1228003.0352
39 | 2601382.099 | 1228098.0567 | 2601389.3081 | 1228084.4505
40 | 2601379.3475 | 1228103.248 | 2601382.099 | 1228098.0567
41 | 2601382.099 | 1228098.0567 | 2601368.4776 | 1228090.7474
42 | 2601196.5556 | 1227957.2689 | 2601195.2064 | 1227959.8591 | 2601187.9564 | 1227971.3782
43 | 2601196.5556 | 1227957.2689 | 2601199.9894 | 1227949.754 | 2601205.3839 | 1227951.3115 | 2601206.9004 | 1227945.1971
44 | 2601163.897 | 1228009.6048 | 2601187.9564 | 1227971.3782
45 | 2601206.9004 | 1227945.1971 | 2601200.2032 | 1227941.2046 | 2601196.3999 | 1227939.5029 | 2601191.5968 | 1227935.6997 | 2601186.0433 | 1227930.4505
46 | 2601163.897 | 1228009.6048 | 2601184.5033 | 1228024.3062 | 2601198.2002 | 1228035.004 | 2601201.1262 | 1228037.7533
47 | 2601572.8381 | 1227686.2481 | 2601568.5594 | 1227695.9444
48 | 2601598.4983 | 1227628.0977 | 2601572.8381 | 1227686.2481
49 | 2601555.5347 | 1227725.4604 | 2601568.5594 | 1227695.9444
50 | 2601598.4983 | 1227628.0977 | 2601513.9559 | 1227602.7253
51 | 2601536.1018 | 1227769.4987 | 2601555.5347 | 1227725.4604
52 | 2601472.8135 | 1227590.5233 | 2601483.8989 | 1227593.7047 | 2601513.9559 | 1227602.7253
53 | 2601536.1018 | 1227769.4987 | 2601517.0716 | 1227763.2357
54 | 2601517.0716 | 1227763.2357 | 2601471.3977 | 1227748.2039 | 2601465.7032 | 1227746.5121
55 | 2601413.7433 | 1227731.0752 | 2601465.7032 | 1227746.5121
56 | 2601367.3239 | 1227717.2843 | 2601413.7433 | 1227731.0752
57 | 2601367.3239 | 1227717.2843 | 2601365.6709 | 1227722.7872 | 2601373.1113 | 1227724.9457 | 2601377.9377 | 1227726.3476 | 2601388.1814 | 1227729.3294 | 2601382.5928 | 1227748.5283
58 | 2601382.5928 | 1227748.5283 | 2601381.6146 | 1227751.8968
59 | 2601364.0258 | 1227761.6431 | 2601367.64 | 1227761.8107 | 2601373.3382 | 1227761.2338 | 2601381.3474 | 1227760.6463 | 2601381.1898 | 1227753.6866 | 2601381.6146 | 1227751.8968
60 | 2601406.4428 | 1227762.1417 | 2601398.2294 | 1227760.9391 | 2601391.7661 | 1227760.4596 | 2601381.3474 | 1227760.6463 | 2601381.1898 | 1227753.6866 | 2601381.6146 | 1227751.8968
61 | 2601381.6146 | 1227751.8968 | 2601385.9321 | 1227753.2024
62 | 2601242.3968 | 1227888.7781 | 2601248.3061 | 1227890.8913
63 | 2601268.0343 | 1227897.9459 | 2601248.3061 | 1227890.8913
64 | 2601388.137 | 1227825.1347 | 2601397.407 | 1227793.8139
65 | 2601388.137 | 1227825.1347 | 2601383.5938 | 1227840.485
66 | 2601397.45 | 1227793.6685 | 2601397.407 | 1227793.8139
67 | 2601382.2585 | 1227844.9967 | 2601383.5938 | 1227840.485
68 | 2601406.4428 | 1227762.1417 | 2601404.0994 | 1227771.202 | 2601397.45 | 1227793.6685
69 | 2601380.4373 | 1227851.1502 | 2601382.2585 | 1227844.9967
70 | 2601406.4428 | 1227762.1417 | 2601443.7918 | 1227773.0879
71 | 2601379.4649 | 1227854.4357 | 2601380.4373 | 1227851.1502
72 | 2601445.0145 | 1227773.4462 | 2601443.7918 | 1227773.0879
73 | 2601379.4649 | 1227854.4357 | 2601373.3771 | 1227875.0048
74 | 2601373.3771 | 1227875.0048 | 2601369.6362 | 1227887.6445
75 | 2601365.4905 | 1227901.6516 | 2601369.6362 | 1227887.6445
76 | 2601361.4313 | 1227915.3666 | 2601365.4905 | 1227901.6516
77 | 2601361.4313 | 1227915.3666 | 2601364.4432 | 1227916.7048
78 | 2601364.0258 | 1227761.6431 | 2601360.9008 | 1227776.0954 | 2601357.7075 | 1227788.2575
79 | 2601364.0258 | 1227761.6431 | 2601358.4191 | 1227759.3072 | 2601354.1494 | 1227756.9839
80 | 2601356.4555 | 1227793.0262 | 2601357.7075 | 1227788.2575
81 | 2601354.1494 | 1227756.9839 | 2601353.6158 | 1227756.6935 | 2601348.1003 | 1227753.2014 | 2601342.591 | 1227751.0011
82 | 2601350.9595 | 1227811.4586 | 2601356.2598 | 1227793.7715 | 2601356.4555 | 1227793.0262
83 | 2601301.5794 | 1227738.1938 | 2601339.41 | 1227749.7308 | 2601342.591 | 1227751.0011
84 | 2601475.1828 | 1227782.2879 | 2601445.0145 | 1227773.4462
85 | 2601391.6638 | 1227928.7993 | 2601364.4432 | 1227916.7048
86 | 2601391.6638 | 1227928.7993 | 2601394.6414 | 1227930.1223
87 | 2601394.6414 | 1227930.1223 | 2601407.9366 | 1227936.0296
88 | 2601335.9726 | 1227864.7868 | 2601329.3093 | 1227888.4969
89 | 2601441.4539 | 1227895.3997 | 2601436.9148 | 1227906.5715
90 | 2601510.9819 | 1227839.3656 | 2601511.8991 | 1227836.8992 | 2601512.3167 | 1227835.5422
91 | 2601266.9307 | 1227728.948 | 2601284.9812 | 1227733.7647
92 | 2601301.5794 | 1227738.1938 | 2601284.9812 | 1227733.7647
93 | 2601266.9307 | 1227728.948 | 2601260.0057 | 1227763.6782
94 | 2601301.5794 | 1227738.1938 | 2601295.4212 | 1227764.7661
95 | 2601260.0057 | 1227763.6782 | 2601250.1642 | 1227817.3441
96 | 2601295.4212 | 1227764.7661 | 2601290.1504 | 1227787.5094 | 2601284.7542 | 1227794.0789 | 2601280.7606 | 1227796.2682 | 2601278.3264 | 1227795.7199
97 | 2601250.1642 | 1227817.3441 | 2601247.6643 | 1227830.9766
98 | 2601245.0576 | 1227845.1908 | 2601247.6643 | 1227830.9766
99 | 2601350.9595 | 1227811.4586 | 2601330.6807 | 1227806.103
100 | 2601243.6062 | 1227853.1054 | 2601245.0576 | 1227845.1908
101 | 2601340.4548 | 1227848.8379 | 2601335.9726 | 1227864.7868
102 | 2601320.5388 | 1228088.4297 | 2601319.7786 | 1228080.5894
103 | 2601441.2327 | 1227880.486 | 2601443.7006 | 1227889.8699 | 2601441.4539 | 1227895.3997
104 | 2601379.3475 | 1228103.248 | 2601369.447 | 1228120.3898
105 | 2601379.3475 | 1228103.248 | 2601390.8099 | 1228108.8539 | 2601409.9011 | 1228118.3971 | 2601412.0635 | 1228119.5267
106 | 2601358.1592 | 1228085.2105 | 2601368.4776 | 1228090.7474
107 | 2601360.324 | 1228129.8707 | 2601364.0902 | 1228127.5924 | 2601367.258 | 1228124.18 | 2601369.447 | 1228120.3898
108 | 2601412.0635 | 1228119.5267 | 2601424.9449 | 1228126.256
109 | 2601329.2825 | 1228128.5744 | 2601332.3416 | 1228137.4247 | 2601338.911 | 1228135.4583 | 2601346.2532 | 1228133.9812 | 2601352.7846 | 1228132.5595 | 2601356.5505 | 1228131.5487 | 2601360.324 | 1228129.8707
110 | 2601424.9449 | 1228126.256 | 2601436.3276 | 1228132.2023
111 | 2601444.397 | 1228136.4177 | 2601436.3276 | 1228132.2023
112 | 2601444.397 | 1228136.4177 | 2601451.5681 | 1228140.1639 | 2601458.8419 | 1228144.8149
113 | 2601473.4479 | 1228154.1542 | 2601458.8419 | 1228144.8149
114 | 2601307.9988 | 1228132.0275 | 2601315.7548 | 1228144.1363 | 2601332.3416 | 1228137.4247 | 2601329.2825 | 1228128.5744
115 | 2601329.2825 | 1228128.5744 | 2601325.7991 | 1228119.8463 | 2601323.3383 | 1228111.8633 | 2601320.9405 | 1228092.5736 | 2601320.5388 | 1228088.4297
116 | 2601479.6289 | 1228158.1064 | 2601473.4479 | 1228154.1542
117 | 2601479.6289 | 1228158.1064 | 2601484.6556 | 1228161.3205
118 | 2601485.5401 | 1228161.8861 | 2601484.6556 | 1228161.3205
119 | 2601537.3159 | 1228192.4598 | 2601528.1115 | 1228187.499 | 2601502.0969 | 1228172.4727 | 2601485.5401 | 1228161.8861
120 | 2601570.3411 | 1228137.8913 | 2601537.3159 | 1228192.4598
121 | 2601570.3411 | 1228137.8913 | 2601543.3158 | 1228121.157
122 | 2601305.5886 | 1228099.052 | 2601307.9988 | 1228132.0275
123 | 2601529.0467 | 1228112.3215 | 2601543.3158 | 1228121.157

## bus_geodata
| x | y | coords
0 | 2601394.2124 | 1227996.9345
1 | 2601365.403 | 1227988.6709
2 | 2601407.2173 | 1228000.7475
3 | 2601339.4774 | 1227981.8142
4 | 2601423.8267 | 1228005.2721
5 | 2601438.9076 | 1228007.7828
6 | 2601303.4478 | 1227972.9883
7 | 2601299.8011 | 1227983.8717
8 | 2601284.464 | 1227968.1393
9 | 2601482.2723 | 1228016.6582
10 | 2601415.8645 | 1228015.849
11 | 2601451.6046 | 1227973.2276
12 | 2601313.3228 | 1227998.2941
13 | 2601315.0321 | 1228031.6323
14 | 2601305.5365 | 1227985.3738
15 | 2601322.0392 | 1227912.4008
16 | 2601324.8067 | 1227903.0959
17 | 2601297.3747 | 1227906.5543
18 | 2601288.3664 | 1228038.6657
19 | 2601258.8484 | 1227973.2048
20 | 2601242.6725 | 1227956.6136
21 | 2601456.997 | 1227960.6036
22 | 2601437.7015 | 1227950.7746
23 | 2601471.4704 | 1227929.006
24 | 2601425.7388 | 1227944.6809
25 | 2601486.3935 | 1227896.553
26 | 2601398.9677 | 1228011.7727
27 | 2601454.5099 | 1228023.5505
28 | 2601422.1698 | 1227942.8629
29 | 2601497.3396 | 1227872.7971
30 | 2601371.2044 | 1228003.0352
31 | 2601389.3081 | 1228084.4505
32 | 2601382.099 | 1228098.0567
33 | 2601196.5556 | 1227957.2689
34 | 2601187.9564 | 1227971.3782
35 | 2601206.9004 | 1227945.1971
36 | 2601163.897 | 1228009.6048
37 | 2601186.0433 | 1227930.4505
38 | 2601288.7881 | 1228039.1688
39 | 2601336.4441 | 1227993.4632
40 | 2601201.1262 | 1228037.7533
41 | 2601572.8381 | 1227686.2481
42 | 2601568.5594 | 1227695.9444
43 | 2601598.4983 | 1227628.0977
44 | 2601555.5347 | 1227725.4604
45 | 2601513.9559 | 1227602.7253
46 | 2601536.1018 | 1227769.4987
47 | 2601472.8135 | 1227590.5233
48 | 2601517.0716 | 1227763.2357
49 | 2601465.7032 | 1227746.5121
50 | 2601413.7433 | 1227731.0752
51 | 2601367.3239 | 1227717.2843
52 | 2601382.5928 | 1227748.5283
53 | 2601381.6146 | 1227751.8968
54 | 2601242.3968 | 1227888.7781
55 | 2601248.3061 | 1227890.8913
56 | 2601388.137 | 1227825.1347
57 | 2601397.407 | 1227793.8139
58 | 2601383.5938 | 1227840.485
59 | 2601397.45 | 1227793.6685
60 | 2601382.2585 | 1227844.9967
61 | 2601406.4428 | 1227762.1417
62 | 2601380.4373 | 1227851.1502
63 | 2601443.7918 | 1227773.0879
64 | 2601379.4649 | 1227854.4357
65 | 2601373.3771 | 1227875.0048
66 | 2601369.6362 | 1227887.6445
67 | 2601365.4905 | 1227901.6516
68 | 2601361.4313 | 1227915.3666
69 | 2601385.9321 | 1227753.2024
70 | 2601364.0258 | 1227761.6431
71 | 2601357.7075 | 1227788.2575
72 | 2601354.1494 | 1227756.9839
73 | 2601356.4555 | 1227793.0262
74 | 2601342.591 | 1227751.0011
75 | 2601445.0145 | 1227773.4462
76 | 2601391.6638 | 1227928.7993
77 | 2601364.4432 | 1227916.7048
78 | 2601394.6414 | 1227930.1223
79 | 2601407.9366 | 1227936.0296
80 | 2601329.3093 | 1227888.4969
81 | 2601436.9148 | 1227906.5715
82 | 2601510.9819 | 1227839.3656
83 | 2601512.3167 | 1227835.5422
84 | 2601475.1828 | 1227782.2879
85 | 2601284.9812 | 1227733.7647
86 | 2601266.9307 | 1227728.948
87 | 2601301.5794 | 1227738.1938
88 | 2601260.0057 | 1227763.6782
89 | 2601295.4212 | 1227764.7661
90 | 2601250.1642 | 1227817.3441
91 | 2601278.3264 | 1227795.7199
92 | 2601247.6643 | 1227830.9766
93 | 2601350.9595 | 1227811.4586
94 | 2601245.0576 | 1227845.1908
95 | 2601243.6062 | 1227853.1054
96 | 2601330.6807 | 1227806.103
97 | 2601340.4548 | 1227848.8379
98 | 2601335.9726 | 1227864.7868
99 | 2601268.0343 | 1227897.9459
100 | 2601319.7786 | 1228080.5894
101 | 2601441.4539 | 1227895.3997
102 | 2601441.2327 | 1227880.486
103 | 2601379.3475 | 1228103.248
104 | 2601368.4776 | 1228090.7474
105 | 2601369.447 | 1228120.3898
106 | 2601412.0635 | 1228119.5267
107 | 2601358.1592 | 1228085.2105
108 | 2601360.324 | 1228129.8707
109 | 2601424.9449 | 1228126.256
110 | 2601436.3276 | 1228132.2023
111 | 2601444.397 | 1228136.4177
112 | 2601458.8419 | 1228144.8149
113 | 2601329.2825 | 1228128.5744
114 | 2601479.6289 | 1228158.1064
115 | 2601473.4479 | 1228154.1542
116 | 2601484.6556 | 1228161.3205
117 | 2601485.5401 | 1228161.8861
118 | 2601537.3159 | 1228192.4598
119 | 2601570.3411 | 1228137.8913
120 | 2601320.5388 | 1228088.4297
121 | 2601307.9988 | 1228132.0275
122 | 2601305.5886 | 1228099.052
123 | 2601543.3158 | 1228121.157
124 | 2601529.0467 | 1228112.3215
125 | 2601361.4313 | 1227915.3666

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98794 | -0.23084 | 0.003168 | 0.00079398
1 | 0.98772 | -0.23517 | 0.002678 | 0.00067116
2 | 0.98808 | -0.22812 | 0.0021676 | 0.00054324
3 | 0.98759 | -0.23776 | 0.0054033 | 0.0013542
4 | 0.9883 | -0.224 | 0.0041992 | 0.0010524
5 | 0.98854 | -0.21918 | 0 | 0
6 | 0.98191 | -0.34752 | 0 | 0
7 | 0.98209 | -0.34403 | 0 | 0
8 | 0.98161 | -0.35346 | 0.0046964 | 0.001177
9 | 0.98831 | -0.22373 | 0.0057471 | 0.0014404
10 | 0.98745 | -0.24032 | 0 | 0
11 | 0.99001 | -0.19085 | 0.0017951 | 0.0004499
12 | 0.98138 | -0.35782 | 0 | 0
13 | 0.97992 | -0.38633 | 0.0026796 | 0.00067158
14 | 0.98224 | -0.34122 | 0 | 0
15 | 0.99371 | -0.12042 | 0 | 0
16 | 0.99383 | -0.1181 | 0 | 0
17 | 0.99339 | -0.12648 | 0.0046965 | 0.001177
18 | 0.98185 | -0.34889 | 0.002074 | 0.00051981
19 | 0.9819 | -0.34789 | 0.0050422 | 0.0012637
20 | 0.98113 | -0.36295 | 0.0024319 | 0.00060949
21 | 0.99057 | -0.18022 | 0 | 0
22 | 0.99161 | -0.16019 | 0.0039589 | 0.0009922
23 | 0.98975 | -0.19607 | 0.0043053 | 0.001079
24 | 0.99227 | -0.14748 | 0.0020329 | 0.00050951
25 | 0.98905 | -0.20964 | 0.0029076 | 0.00072871
26 | 0.98694 | -0.25019 | 0.0040675 | 0.0010194
27 | 0.98707 | -0.24757 | 0.010279 | 0.0025763
28 | 0.99247 | -0.14364 | 0 | 0
29 | 0.98861 | -0.21824 | 0.003413 | 0.00085537
30 | 0.9857 | -0.27401 | 0.014229 | 0.0035661
31 | 0.97363 | -0.50964 | 0.0089664 | 0.0022472
32 | 0.97376 | -0.5071 | 0 | 0
33 | 0.98064 | -0.37249 | 0 | 0
34 | 0.98052 | -0.37491 | 0.0018787 | 0.00047084
35 | 0.98079 | -0.36954 | 0 | 0
36 | 0.98026 | -0.37999 | 0 | 0
37 | 0.98075 | -0.37027 | 0.0015738 | 0.00039442
38 | 0.98184 | -0.34892 | 0.0024259 | 0.00060799
39 | 0.98441 | -0.29895 | 0.0035849 | 0.00089847
40 | 0.97999 | -0.38524 | 0.0061981 | 0.0015534
41 | 0.97162 | -0.54747 | 0.038615 | 0.0096778
42 | 0.97207 | -0.53846 | 0.00071011 | 0.00017797
43 | 0.97117 | -0.55623 | 0 | 0
44 | 0.97348 | -0.51066 | 0.00059171 | 0.0001483
45 | 0.97056 | -0.5684 | 0.0017547 | 0.00043976
46 | 0.97561 | -0.4688 | 0 | 0
47 | 0.97033 | -0.57293 | 0.0057006 | 0.0014287
48 | 0.9765 | -0.45144 | 0.005471 | 0.0013712
49 | 0.97916 | -0.39939 | 0.011686 | 0.0029288
50 | 0.98242 | -0.336 | 0.0083221 | 0.0020857
51 | 0.98571 | -0.27249 | 0 | 0
52 | 0.98905 | -0.20842 | 0 | 0
53 | 0.98928 | -0.20387 | 0 | 0
54 | 0.99303 | -0.13358 | 0.0020007 | 0.00050142
55 | 0.99304 | -0.13336 | 0.0036626 | 0.00091794
56 | 0.99751 | -0.047201 | 0.012991 | 0.0032558
57 | 0.99578 | -0.079965 | 0.0020507 | 0.00051396
58 | 0.99814 | -0.035308 | 0.012856 | 0.0032221
59 | 0.99576 | -0.080264 | 0.0013667 | 0.00034252
60 | 0.99834 | -0.031463 | 0.007331 | 0.0018373
61 | 0.99239 | -0.1444 | 0 | 0
62 | 0.99863 | -0.025946 | 0.016912 | 0.0042386
63 | 0.99195 | -0.15295 | 0.0046089 | 0.0011551
64 | 0.99881 | -0.022665 | 0.017219 | 0.0043155
65 | 1 | 0 | -0.51789 | -0.13153
66 | 0.99867 | -0.025235 | 0.049605 | 0.012432
67 | 0.99742 | -0.049046 | 0.017805 | 0.0044624
68 | 0.99628 | -0.070927 | 0 | 0
69 | 0.98928 | -0.204 | 0.0016485 | 0.00041315
70 | 0.98871 | -0.21506 | 0 | 0
71 | 0.98855 | -0.21822 | 0.0037323 | 0.00093541
72 | 0.98853 | -0.21847 | 0.0033943 | 0.00085069
73 | 0.98853 | -0.21847 | 0.0018319 | 0.00045913
74 | 0.98836 | -0.22175 | 0.0010181 | 0.00025517
75 | 0.99194 | -0.15313 | 0.0020496 | 0.00051367
76 | 0.99435 | -0.1077 | 0.0020633 | 0.00051711
77 | 0.99608 | -0.074634 | 0.0028446 | 0.00071293
78 | 0.99416 | -0.11129 | 0.0051098 | 0.0012806
79 | 0.99335 | -0.12687 | 0.0019553 | 0.00049006
80 | 0.99305 | -0.13321 | 0.016492 | 0.0041332
81 | 0.99184 | -0.15595 | 0.008303 | 0.0020809
82 | 0.98811 | -0.22792 | 0.0084471 | 0.002117
83 | 0.98809 | -0.2284 | 0.0065734 | 0.0016474
84 | 0.99178 | -0.15633 | 0.0057431 | 0.0014393
85 | 0.98771 | -0.23443 | 0.00042324 | 0.00010607
86 | 0.98757 | -0.23717 | 0 | 0
87 | 0.98785 | -0.23179 | 0 | 0
88 | 0.9873 | -0.24236 | 0 | 0
89 | 0.98774 | -0.23396 | 0.00096543 | 0.00024196
90 | 0.98689 | -0.25036 | 0.0016162 | 0.00040507
91 | 0.98761 | -0.23638 | 0.0034885 | 0.00087429
92 | 0.98681 | -0.25199 | 0.0017986 | 0.00045077
93 | 0.98852 | -0.21879 | 0 | 0
94 | 0.98675 | -0.25323 | 0.0024476 | 0.00061343
95 | 0.98673 | -0.25356 | 0.0023312 | 0.00058424
96 | 0.9885 | -0.21913 | 0.00092654 | 0.00023221
97 | 0.99191 | -0.15513 | 0.016057 | 0.0040243
98 | 0.99216 | -0.15042 | 0.023448 | 0.0058765
99 | 0.99315 | -0.13127 | 0.0031823 | 0.00079757
100 | 0.97789 | -0.42604 | 0.0018068 | 0.00045283
101 | 0.99173 | -0.15797 | 0.002741 | 0.00068695
102 | 0.99164 | -0.15983 | 0.0067039 | 0.0016802
103 | 0.97385 | -0.50532 | 0 | 0
104 | 0.97365 | -0.50924 | 0.0053016 | 0.0013287
105 | 0.97444 | -0.49377 | 0.0029724 | 0.00074494
106 | 0.97333 | -0.51558 | 0.001467 | 0.00036766
107 | 0.97363 | -0.50972 | 0.0022277 | 0.00055833
108 | 0.97487 | -0.48521 | 0 | 0
109 | 0.97314 | -0.51927 | 0.00036084 | 9.0435e-05
110 | 0.97298 | -0.52245 | 0.00012491 | 3.1305e-05
111 | 0.97287 | -0.52468 | 0.00027548 | 6.9043e-05
112 | 0.97266 | -0.5287 | 0.000143 | 3.584e-05
113 | 0.97611 | -0.46076 | 0 | 0
114 | 0.97238 | -0.53439 | 0.0011467 | 0.00028738
115 | 0.97246 | -0.53282 | 0.0012718 | 0.00031875
116 | 0.97232 | -0.53554 | 0.00033914 | 8.4998e-05
117 | 0.97231 | -0.53573 | 0.001811 | 0.00045388
118 | 0.97184 | -0.54497 | 0 | 0
119 | 0.97135 | -0.55476 | 0 | 0
120 | 0.97757 | -0.43215 | 0.0046988 | 0.0011776
121 | 0.97599 | -0.46315 | 0 | 0
122 | 0.9759 | -0.46505 | 0.0031351 | 0.00078573
123 | 0.9711 | -0.55965 | 0.0011753 | 0.00029456
124 | 0.97099 | -0.56186 | 0.007143 | 0.0017902
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0080836 | 0.0020261 | -0.008082 | -0.0020254 | 1.6662e-06 | 6.8267e-07 | 0.012175 | 0.012176 | 0.012176 | 0.98794 | -0.23084 | 0.98772 | -0.23517 | 3.3449
1 | -0.011252 | -0.0028201 | 0.011253 | 0.0028209 | 1.4596e-06 | 7.6058e-07 | 0.016947 | 0.016947 | 0.016947 | 0.98794 | -0.23084 | 0.98808 | -0.22812 | 4.6558
2 | 0.005404 | 0.0013543 | -0.0054033 | -0.0013542 | 6.6653e-07 | 8.3392e-08 | 0.0081412 | 0.0081413 | 0.0081413 | 0.98772 | -0.23517 | 0.98759 | -0.23776 | 2.2366
3 | -0.013421 | -0.0033641 | 0.013423 | 0.0033656 | 2.6372e-06 | 1.4672e-06 | 0.020211 | 0.020211 | 0.020211 | 0.98808 | -0.22812 | 0.9883 | -0.224 | 5.5525
4 | -0.017622 | -0.004418 | 0.017627 | 0.0044204 | 4.046e-06 | 2.393e-06 | 0.026534 | 0.026534 | 0.026534 | 0.9883 | -0.224 | 0.98854 | -0.21918 | 7.2895
5 | 0.0057484 | 0.0014406 | -0.0057471 | -0.0014404 | 1.2444e-06 | 2.2834e-07 | 0.0086528 | 0.008653 | 0.008653 | 0.98854 | -0.21918 | 0.98831 | -0.22373 | 2.3772
6 | 0.10642 | 0.027 | -0.10631 | -0.026932 | 0.00010807 | 6.7872e-05 | 0.16031 | 0.16031 | 0.16031 | 0.98854 | -0.21918 | 0.98745 | -0.24032 | 14.68
7 | -0.12979 | -0.032861 | 0.12997 | 0.032973 | 0.00017679 | 0.00011172 | 0.19549 | 0.19549 | 0.19549 | 0.98854 | -0.21918 | 0.99001 | -0.19085 | 17.9021
8 | -0.016797 | -0.0042138 | 0.0168 | 0.0042154 | 2.7896e-06 | 1.6401e-06 | 0.025456 | 0.025456 | 0.025456 | 0.98191 | -0.34752 | 0.98209 | -0.34403 | 6.9935
9 | 0.016797 | 0.0042138 | -0.016793 | -0.004211 | 4.7614e-06 | 2.7995e-06 | 0.025456 | 0.025457 | 0.025457 | 0.98191 | -0.34752 | 0.98161 | -0.35346 | 6.9936
10 | 0.004501 | 0.0011277 | -0.0045 | -0.0011278 | 1.0407e-06 | -8.8821e-08 | 0.0068195 | 0.0068198 | 0.0068198 | 0.98209 | -0.34403 | 0.98185 | -0.34889 | 1.8736
11 | -0.026344 | -0.0066069 | 0.026348 | 0.0066091 | 3.5331e-06 | 2.1863e-06 | 0.039917 | 0.039917 | 0.039917 | 0.98209 | -0.34403 | 0.98224 | -0.34122 | 10.9662
12 | 0.0050432 | 0.0012638 | -0.0050422 | -0.0012637 | 9.2659e-07 | 5.7634e-08 | 0.0076411 | 0.0076413 | 0.0076413 | 0.98209 | -0.34403 | 0.9819 | -0.34789 | 2.0992
13 | 0.012096 | 0.0030339 | -0.012091 | -0.003031 | 5.4694e-06 | 2.9524e-06 | 0.018337 | 0.018337 | 0.018337 | 0.98161 | -0.35346 | 0.98113 | -0.36295 | 5.0378
14 | 0.096027 | 0.024354 | -0.095982 | -0.024326 | 4.5561e-05 | 2.8492e-05 | 0.14481 | 0.14481 | 0.14481 | 0.98745 | -0.24032 | 0.98694 | -0.25019 | 13.261
15 | 0.010283 | 0.002578 | -0.010279 | -0.0025763 | 3.5507e-06 | 1.7682e-06 | 0.015496 | 0.015496 | 0.015496 | 0.98745 | -0.24032 | 0.98707 | -0.24757 | 4.2572
16 | -0.13177 | -0.033423 | 0.13183 | 0.033465 | 6.74e-05 | 4.2606e-05 | 0.19819 | 0.19819 | 0.19819 | 0.99001 | -0.19085 | 0.99057 | -0.18022 | 18.1492
17 | 0.047367 | 0.011988 | -0.047302 | -0.011947 | 6.471e-05 | 4.0993e-05 | 0.071862 | 0.071862 | 0.071862 | 0.98138 | -0.35782 | 0.97992 | -0.38633 | 19.7424
18 | -0.047367 | -0.011988 | 0.047405 | 0.012012 | 3.7784e-05 | 2.3935e-05 | 0.071862 | 0.071862 | 0.071862 | 0.98138 | -0.35782 | 0.98224 | -0.34122 | 19.7424
19 | 0.044623 | 0.011276 | -0.044538 | -0.011222 | 8.4773e-05 | 5.3636e-05 | 0.067793 | 0.067794 | 0.067794 | 0.97992 | -0.38633 | 0.97789 | -0.42604 | 18.6246
20 | -0.073753 | -0.018621 | 0.073902 | 0.018717 | 0.00014969 | 9.5399e-05 | 0.11178 | 0.11178 | 0.11178 | 0.98224 | -0.34122 | 0.98441 | -0.29895 | 30.7086
21 | -0.013549 | -0.0033971 | 0.01355 | 0.0033979 | 1.4984e-06 | 8.332e-07 | 0.020289 | 0.020289 | 0.020289 | 0.99371 | -0.12042 | 0.99383 | -0.1181 | 5.5738
22 | 0.013549 | 0.0033971 | -0.013545 | -0.0033949 | 3.9128e-06 | 2.1759e-06 | 0.020289 | 0.020289 | 0.020289 | 0.99371 | -0.12042 | 0.99339 | -0.12648 | 5.5739
23 | 0.056073 | 0.014082 | -0.056032 | -0.014057 | 4.0393e-05 | 2.5654e-05 | 0.083966 | 0.083966 | 0.083966 | 0.99383 | -0.1181 | 0.99305 | -0.13321 | 23.0675
24 | -0.069623 | -0.01748 | 0.06978 | 0.01758 | 0.00015705 | 0.00010001 | 0.10425 | 0.10425 | 0.10425 | 0.99383 | -0.1181 | 0.99628 | -0.070927 | 28.6413
25 | 0.0088482 | 0.0022178 | -0.0088462 | -0.0022169 | 2.0173e-06 | 8.9473e-07 | 0.013254 | 0.013254 | 0.013254 | 0.99339 | -0.12648 | 0.99315 | -0.13127 | 3.6412
26 | 0.0024259 | 0.00060798 | -0.0024259 | -0.00060799 | 3.3272e-09 | -6.1724e-09 | 0.0036765 | 0.0036765 | 0.0036765 | 0.98185 | -0.34889 | 0.98184 | -0.34892 | 1.01
27 | 0.0096588 | 0.0024215 | -0.0096558 | -0.00242 | 3.0281e-06 | 1.463e-06 | 0.014649 | 0.014649 | 0.014649 | 0.98113 | -0.36295 | 0.98079 | -0.36954 | 4.0245
28 | -0.15753 | -0.039922 | 0.15768 | 0.040018 | 0.00015177 | 9.6298e-05 | 0.23679 | 0.23679 | 0.23679 | 0.99057 | -0.18022 | 0.99161 | -0.16019 | 21.6843
29 | 0.025694 | 0.0064565 | -0.025675 | -0.0064445 | 1.9422e-05 | 1.1983e-05 | 0.038604 | 0.038604 | 0.038604 | 0.99057 | -0.18022 | 0.98975 | -0.19607 | 10.6054
30 | -0.16164 | -0.04101 | 0.16174 | 0.041073 | 9.8876e-05 | 6.276e-05 | 0.24273 | 0.24273 | 0.24273 | 0.99161 | -0.16019 | 0.99227 | -0.14748 | 22.2283
31 | 0.021369 | 0.0053655 | -0.021356 | -0.0053571 | 1.3829e-05 | 8.3918e-06 | 0.032131 | 0.032131 | 0.032131 | 0.98975 | -0.19607 | 0.98905 | -0.20964 | 8.8272
32 | -0.16377 | -0.041583 | 0.1638 | 0.041602 | 3.0245e-05 | 1.9201e-05 | 0.24578 | 0.24578 | 0.24578 | 0.99227 | -0.14748 | 0.99247 | -0.14364 | 22.5074
33 | 0.018448 | 0.0046284 | -0.01844 | -0.0046239 | 7.5569e-06 | 4.5009e-06 | 0.027757 | 0.027757 | 0.027757 | 0.98905 | -0.20964 | 0.98861 | -0.21824 | 7.6255
34 | 0.091914 | 0.023306 | -0.091809 | -0.02324 | 0.00010509 | 6.6514e-05 | 0.13868 | 0.13868 | 0.13868 | 0.98694 | -0.25019 | 0.9857 | -0.27401 | 19.0491
35 | 0.01776 | 0.0044548 | -0.017749 | -0.0044487 | 1.0416e-05 | 6.1606e-06 | 0.026629 | 0.026629 | 0.026629 | 0.99247 | -0.14364 | 0.99184 | -0.15595 | 7.3156
36 | -0.18156 | -0.046057 | 0.18171 | 0.04615 | 0.0001465 | 9.315e-05 | 0.27241 | 0.27241 | 0.27241 | 0.99247 | -0.14364 | 0.99335 | -0.12687 | 24.9459
37 | 0.015028 | 0.0037685 | -0.015021 | -0.0037645 | 6.9309e-06 | 3.9729e-06 | 0.02262 | 0.02262 | 0.02262 | 0.98861 | -0.21824 | 0.98811 | -0.22792 | 6.2142
38 | 0.07758 | 0.019674 | -0.077487 | -0.019615 | 9.2893e-05 | 5.8533e-05 | 0.1172 | 0.1172 | 0.1172 | 0.9857 | -0.27401 | 0.98441 | -0.29895 | 16.0986
39 | -0.0089664 | -0.0022472 | 0.0089675 | 0.0022477 | 1.0843e-06 | 5.0244e-07 | 0.013704 | 0.013703 | 0.013704 | 0.97363 | -0.50964 | 0.97376 | -0.5071 | 3.7647
40 | -0.016498 | -0.0041349 | 0.016499 | 0.0041357 | 1.3995e-06 | 8.2264e-07 | 0.02521 | 0.02521 | 0.02521 | 0.97376 | -0.5071 | 0.97385 | -0.50532 | 6.9259
41 | 0.0075302 | 0.0018872 | -0.0075294 | -0.0018869 | 7.6759e-07 | 2.9897e-07 | 0.011507 | 0.011507 | 0.011507 | 0.97376 | -0.5071 | 0.97365 | -0.50924 | 3.1613
42 | 0.0080808 | 0.0020254 | -0.0080799 | -0.002025 | 9.3207e-07 | 3.8799e-07 | 0.012262 | 0.012262 | 0.012262 | 0.98064 | -0.37249 | 0.98052 | -0.37491 | 3.3686
43 | -0.0080808 | -0.0020254 | 0.0080819 | 0.0020259 | 1.1376e-06 | 4.7347e-07 | 0.012262 | 0.012262 | 0.012262 | 0.98064 | -0.37249 | 0.98079 | -0.36954 | 3.3686
44 | 0.0062012 | 0.0015542 | -0.0061997 | -0.0015538 | 1.5001e-06 | 3.9053e-07 | 0.0094108 | 0.0094111 | 0.0094111 | 0.98052 | -0.37491 | 0.98026 | -0.37999 | 2.5855
45 | 0.0015738 | 0.00039413 | -0.0015738 | -0.00039442 | 5.5012e-08 | -2.8952e-07 | 0.0023876 | 0.0023878 | 0.0023878 | 0.98079 | -0.36954 | 0.98075 | -0.37027 | 0.65598
46 | 0.0061997 | 0.0015538 | -0.0061981 | -0.0015534 | 1.5513e-06 | 4.042e-07 | 0.0094111 | 0.0094113 | 0.0094113 | 0.98026 | -0.37999 | 0.97999 | -0.38524 | 2.5855
47 | -0.046079 | -0.011549 | 0.046099 | 0.011562 | 1.9793e-05 | 1.2536e-05 | 0.070569 | 0.070569 | 0.070569 | 0.97162 | -0.54747 | 0.97207 | -0.53846 | 19.3872
48 | 0.0074639 | 0.0018716 | -0.0074608 | -0.0018704 | 3.1147e-06 | 1.2065e-06 | 0.011431 | 0.011432 | 0.011432 | 0.97162 | -0.54747 | 0.97117 | -0.55623 | 3.1405
49 | -0.046809 | -0.01174 | 0.046871 | 0.011779 | 6.212e-05 | 3.9356e-05 | 0.071656 | 0.071656 | 0.071656 | 0.97207 | -0.53846 | 0.97348 | -0.51066 | 19.6858
50 | 0.0074608 | 0.0018704 | -0.0074565 | -0.0018687 | 4.3257e-06 | 1.6769e-06 | 0.011432 | 0.011432 | 0.011432 | 0.97117 | -0.55623 | 0.97056 | -0.5684 | 3.1406
51 | -0.047463 | -0.011928 | 0.047558 | 0.011988 | 9.5038e-05 | 6.0224e-05 | 0.072561 | 0.07256 | 0.072561 | 0.97348 | -0.51066 | 0.97561 | -0.4688 | 19.9342
52 | 0.0057018 | 0.001429 | -0.0057006 | -0.0014287 | 1.2298e-06 | 2.5686e-07 | 0.0087417 | 0.0087419 | 0.0087419 | 0.97056 | -0.5684 | 0.97033 | -0.57293 | 2.4016
53 | -0.047558 | -0.011988 | 0.047597 | 0.012013 | 3.9555e-05 | 2.5065e-05 | 0.07256 | 0.07256 | 0.07256 | 0.97561 | -0.4688 | 0.9765 | -0.45144 | 19.9342
54 | -0.053068 | -0.013384 | 0.053201 | 0.013468 | 0.00013258 | 8.4175e-05 | 0.080897 | 0.080897 | 0.080897 | 0.9765 | -0.45144 | 0.97916 | -0.39939 | 22.2245
55 | -0.064887 | -0.016397 | 0.065085 | 0.016523 | 0.00019784 | 0.00012593 | 0.098656 | 0.098656 | 0.098656 | 0.97916 | -0.39939 | 0.98242 | -0.336 | 27.1034
56 | -0.073407 | -0.018609 | 0.073632 | 0.018752 | 0.00022479 | 0.00014325 | 0.11126 | 0.11126 | 0.11126 | 0.98242 | -0.336 | 0.98571 | -0.27249 | 30.5662
57 | -0.073632 | -0.018752 | 0.07386 | 0.018897 | 0.00022831 | 0.00014549 | 0.11126 | 0.11126 | 0.11126 | 0.98571 | -0.27249 | 0.98905 | -0.20842 | 30.5661
58 | -0.07386 | -0.018897 | 0.073876 | 0.018908 | 1.628e-05 | 1.0374e-05 | 0.11126 | 0.11126 | 0.11126 | 0.98905 | -0.20842 | 0.98928 | -0.20387 | 30.5661
59 | 0.024008 | 0.0060253 | -0.023995 | -0.0060174 | 1.2803e-05 | 7.8581e-06 | 0.036114 | 0.036115 | 0.036115 | 0.98928 | -0.20387 | 0.98871 | -0.21506 | 9.9216
60 | -0.099533 | -0.025346 | 0.099819 | 0.025529 | 0.00028635 | 0.00018282 | 0.14985 | 0.14985 | 0.14985 | 0.98928 | -0.20387 | 0.99239 | -0.1444 | 41.1687
61 | 0.0016485 | 0.0004131 | -0.0016485 | -0.00041315 | 1.04e-08 | -5.1259e-08 | 0.0024796 | 0.0024796 | 0.0024796 | 0.98928 | -0.20387 | 0.98928 | -0.204 | 0.68121
62 | -0.0020007 | -0.00050142 | 0.0020007 | 0.00050135 | 2.1152e-08 | -6.7654e-08 | 0.0029979 | 0.0029979 | 0.0029979 | 0.99303 | -0.13358 | 0.99304 | -0.13336 | 0.82361
63 | -0.0056633 | -0.0014193 | 0.0056639 | 0.0014194 | 5.658e-07 | 9.1027e-08 | 0.0084861 | 0.008486 | 0.0084861 | 0.99304 | -0.13336 | 0.99315 | -0.13127 | 2.3314
64 | 0.11618 | 0.029838 | -0.11599 | -0.02972 | 0.0001845 | 0.00011723 | 0.17356 | 0.17356 | 0.17356 | 0.99751 | -0.047201 | 0.99578 | -0.079965 | 23.8413
65 | -0.12917 | -0.033094 | 0.12924 | 0.033141 | 7.4494e-05 | 4.7049e-05 | 0.19294 | 0.19294 | 0.19294 | 0.99751 | -0.047201 | 0.99814 | -0.035308 | 17.6688
66 | 0.11394 | 0.029206 | -0.11394 | -0.029205 | 1.6538e-06 | 1.0564e-06 | 0.1705 | 0.1705 | 0.1705 | 0.99578 | -0.079965 | 0.99576 | -0.080264 | 46.8408
67 | -0.1421 | -0.036363 | 0.14213 | 0.036379 | 2.646e-05 | 1.675e-05 | 0.21211 | 0.21211 | 0.21211 | 0.99814 | -0.035308 | 0.99834 | -0.031463 | 19.4239
68 | 0.11258 | 0.028863 | -0.11223 | -0.02864 | 0.00034893 | 0.00022289 | 0.16846 | 0.16846 | 0.16846 | 0.99576 | -0.080264 | 0.99239 | -0.1444 | 46.2798
69 | -0.14946 | -0.038217 | 0.1495 | 0.038242 | 3.9904e-05 | 2.5287e-05 | 0.22304 | 0.22304 | 0.22304 | 0.99834 | -0.031463 | 0.99863 | -0.025946 | 20.4245
70 | 0.012408 | 0.003111 | -0.012402 | -0.0031083 | 5.0519e-06 | 2.7306e-06 | 0.018605 | 0.018605 | 0.018605 | 0.99239 | -0.1444 | 0.99195 | -0.15295 | 5.1112
71 | -0.16641 | -0.042481 | 0.16644 | 0.042497 | 2.6392e-05 | 1.6756e-05 | 0.24824 | 0.24824 | 0.24824 | 0.99863 | -0.025946 | 0.99881 | -0.022665 | 22.7322
72 | 0.0077936 | 0.0019532 | -0.0077935 | -0.0019532 | 6.5305e-08 | 2.5348e-08 | 0.011691 | 0.011691 | 0.011691 | 0.99195 | -0.15295 | 0.99194 | -0.15313 | 3.2118
73 | -0.18366 | -0.046813 | 0.18386 | 0.046941 | 0.00020114 | 0.00012789 | 0.27389 | 0.27389 | 0.27389 | 0.99881 | -0.022665 | 1 | 0 | 25.0813
74 | 0.33238 | 0.084592 | -0.33198 | -0.084334 | 0.00040381 | 0.00025792 | 0.49505 | 0.49505 | 0.49505 | 1 | 0 | 0.99867 | -0.025235 | 45.3342
75 | 0.28238 | 0.071902 | -0.28205 | -0.071695 | 0.00032385 | 0.00020669 | 0.42114 | 0.42114 | 0.42114 | 0.99867 | -0.025235 | 0.99742 | -0.049046 | 38.5659
76 | 0.26425 | 0.067233 | -0.26397 | -0.067055 | 0.00027836 | 0.00017759 | 0.39458 | 0.39458 | 0.39458 | 0.99742 | -0.049046 | 0.99628 | -0.070927 | 36.1334
77 | 0.19419 | 0.049475 | -0.19415 | -0.049453 | 3.4724e-05 | 2.2094e-05 | 0.29032 | 0.29032 | 0.29032 | 0.99628 | -0.070927 | 0.99608 | -0.074634 | 26.5864
78 | 0.0064918 | 0.0016265 | -0.0064909 | -0.0016262 | 9.794e-07 | 2.7598e-07 | 0.0097701 | 0.0097702 | 0.0097702 | 0.98871 | -0.21506 | 0.98855 | -0.21822 | 2.6841
79 | 0.017504 | 0.0043909 | -0.017501 | -0.0043892 | 2.8459e-06 | 1.6812e-06 | 0.026344 | 0.026344 | 0.026344 | 0.98871 | -0.21506 | 0.98853 | -0.21847 | 7.2375
80 | 0.0027585 | 0.0006908 | -0.0027585 | -0.00069085 | 3.1875e-08 | -4.2808e-08 | 0.0041521 | 0.0041522 | 0.0041522 | 0.98855 | -0.21822 | 0.98853 | -0.21847 | 1.1407
81 | 0.014106 | 0.0035385 | -0.014104 | -0.0035373 | 2.2098e-06 | 1.2468e-06 | 0.021235 | 0.021235 | 0.021235 | 0.98853 | -0.21847 | 0.98836 | -0.22175 | 5.8338
82 | 0.00092657 | 0.00023172 | -0.00092656 | -0.00023195 | 1.4029e-08 | -2.3761e-07 | 0.0013946 | 0.0013947 | 0.0013947 | 0.98853 | -0.21847 | 0.98852 | -0.21879 | 0.38315
83 | 0.013086 | 0.0032821 | -0.01308 | -0.0032787 | 6.256e-06 | 3.4533e-06 | 0.019702 | 0.019703 | 0.019703 | 0.98836 | -0.22175 | 0.98785 | -0.23179 | 5.4128
84 | 0.0057439 | 0.0014395 | -0.0057431 | -0.0014393 | 8.7527e-07 | 1.5443e-07 | 0.0086165 | 0.0086166 | 0.0086166 | 0.99194 | -0.15313 | 0.99178 | -0.15633 | 2.3672
85 | -0.191 | -0.048546 | 0.19131 | 0.04874 | 0.00030471 | 0.00019385 | 0.28607 | 0.28607 | 0.28607 | 0.99435 | -0.1077 | 0.99608 | -0.074634 | 26.1972
86 | 0.18894 | 0.048029 | -0.18891 | -0.048008 | 3.2616e-05 | 2.0748e-05 | 0.28299 | 0.28299 | 0.28299 | 0.99435 | -0.1077 | 0.99416 | -0.11129 | 25.9145
87 | 0.1838 | 0.046728 | -0.18366 | -0.04664 | 0.00013787 | 8.7669e-05 | 0.27534 | 0.27534 | 0.27534 | 0.99416 | -0.11129 | 0.99335 | -0.12687 | 25.2141
88 | 0.039541 | 0.0099234 | -0.039508 | -0.0099029 | 3.2427e-05 | 2.0435e-05 | 0.059254 | 0.059254 | 0.059254 | 0.99305 | -0.13321 | 0.99216 | -0.15042 | 16.2786
89 | 0.0094464 | 0.0023677 | -0.0094455 | -0.0023673 | 9.0826e-07 | 4.2567e-07 | 0.014172 | 0.014172 | 0.014172 | 0.99184 | -0.15595 | 0.99173 | -0.15797 | 3.8935
90 | 0.0065735 | 0.0016475 | -0.0065734 | -0.0016474 | 1.4887e-07 | 4.3387e-08 | 0.0098992 | 0.0098992 | 0.0098992 | 0.98811 | -0.22792 | 0.98809 | -0.2284 | 2.7196
91 | 0.0082007 | 0.0020562 | -0.0081996 | -0.0020557 | 1.0694e-06 | 4.4533e-07 | 0.012355 | 0.012355 | 0.012355 | 0.98771 | -0.23443 | 0.98757 | -0.23717 | 3.3942
92 | -0.0086239 | -0.0021622 | 0.008625 | 0.0021627 | 1.0875e-06 | 4.7607e-07 | 0.012992 | 0.012992 | 0.012992 | 0.98771 | -0.23443 | 0.98785 | -0.23179 | 3.5694
93 | 0.0081996 | 0.0020557 | -0.0081976 | -0.0020549 | 2.0273e-06 | 8.4444e-07 | 0.012355 | 0.012355 | 0.012355 | 0.98757 | -0.23717 | 0.9873 | -0.24236 | 3.3943
94 | 0.0044548 | 0.001116 | -0.0044543 | -0.001116 | 4.6056e-07 | -5.4405e-08 | 0.0067101 | 0.0067102 | 0.0067102 | 0.98785 | -0.23179 | 0.98774 | -0.23396 | 1.8435
95 | 0.0081976 | 0.0020549 | -0.0081944 | -0.0020536 | 3.1233e-06 | 1.3015e-06 | 0.012355 | 0.012355 | 0.012355 | 0.9873 | -0.24236 | 0.98689 | -0.25036 | 3.3943
96 | 0.0034889 | 0.00087405 | -0.0034885 | -0.00087429 | 4.0295e-07 | -2.3992e-07 | 0.0052558 | 0.005256 | 0.005256 | 0.98774 | -0.23396 | 0.98761 | -0.23638 | 1.444
97 | 0.0065782 | 0.0016485 | -0.0065777 | -0.0016484 | 5.113e-07 | 1.5015e-07 | 0.0099184 | 0.0099185 | 0.0099185 | 0.98689 | -0.25036 | 0.98681 | -0.25199 | 2.7249
98 | 0.0047791 | 0.0011976 | -0.0047788 | -0.0011976 | 2.8143e-07 | -4.4936e-09 | 0.0072064 | 0.0072064 | 0.0072064 | 0.98681 | -0.25199 | 0.98675 | -0.25323 | 1.9798
99 | 0.00092656 | 0.00023195 | -0.00092654 | -0.00023221 | 1.53e-08 | -2.5909e-07 | 0.0013947 | 0.0013947 | 0.0013947 | 0.98852 | -0.21879 | 0.9885 | -0.21913 | 0.38317
100 | 0.0023312 | 0.00058416 | -0.0023312 | -0.00058424 | 3.7291e-08 | -7.8918e-08 | 0.0035154 | 0.0035154 | 0.0035154 | 0.98675 | -0.25323 | 0.98673 | -0.25356 | 0.96578
101 | -0.016057 | -0.0040243 | 0.016061 | 0.0040264 | 3.6047e-06 | 2.0931e-06 | 0.024088 | 0.024088 | 0.024088 | 0.99191 | -0.15513 | 0.99216 | -0.15042 | 6.6176
102 | 0.042731 | 0.010769 | -0.042719 | -0.010761 | 1.2497e-05 | 7.8994e-06 | 0.065044 | 0.065044 | 0.065044 | 0.97789 | -0.42604 | 0.97757 | -0.43215 | 17.8693
103 | 0.0067045 | 0.0016803 | -0.0067039 | -0.0016802 | 5.9472e-07 | 1.7843e-07 | 0.01006 | 0.01006 | 0.01006 | 0.99173 | -0.15797 | 0.99164 | -0.15983 | 2.7637
104 | -0.031787 | -0.0079755 | 0.031805 | 0.0079864 | 1.7514e-05 | 1.0963e-05 | 0.048574 | 0.048574 | 0.048574 | 0.97385 | -0.50532 | 0.97444 | -0.49377 | 13.3444
105 | 0.015288 | 0.0038397 | -0.015281 | -0.0038354 | 7.48e-06 | 4.3328e-06 | 0.023363 | 0.023363 | 0.023363 | 0.97385 | -0.50532 | 0.97333 | -0.51558 | 6.4185
106 | 0.0022278 | 0.00055821 | -0.0022277 | -0.00055833 | 5.0903e-08 | -1.1306e-07 | 0.0034047 | 0.0034047 | 0.0034047 | 0.97365 | -0.50924 | 0.97363 | -0.50972 | 0.93536
107 | -0.034777 | -0.0087314 | 0.034792 | 0.0087403 | 1.4212e-05 | 8.9282e-06 | 0.053112 | 0.053112 | 0.053112 | 0.97444 | -0.49377 | 0.97487 | -0.48521 | 14.5913
108 | 0.013814 | 0.0034677 | -0.013811 | -0.0034664 | 2.4311e-06 | 1.3753e-06 | 0.021121 | 0.021121 | 0.021121 | 0.97333 | -0.51558 | 0.97314 | -0.51927 | 5.8024
109 | -0.034792 | -0.0087403 | 0.034832 | 0.0087659 | 4.0647e-05 | 2.5534e-05 | 0.053112 | 0.053112 | 0.053112 | 0.97487 | -0.48521 | 0.97611 | -0.46076 | 14.5913
110 | 0.013451 | 0.0033759 | -0.013449 | -0.0033748 | 2.0375e-06 | 1.1445e-06 | 0.020569 | 0.020569 | 0.020569 | 0.97314 | -0.51927 | 0.97298 | -0.52245 | 5.6508
111 | 0.013324 | 0.0033435 | -0.013322 | -0.0033427 | 1.4177e-06 | 7.9429e-07 | 0.020378 | 0.020378 | 0.020378 | 0.97298 | -0.52245 | 0.97287 | -0.52468 | 5.5984
112 | 0.013047 | 0.0032736 | -0.013044 | -0.0032723 | 2.4978e-06 | 1.391e-06 | 0.019957 | 0.019957 | 0.019957 | 0.97287 | -0.52468 | 0.97266 | -0.5287 | 5.4826
113 | 0.012901 | 0.0032364 | -0.012899 | -0.003235 | 2.5328e-06 | 1.4059e-06 | 0.019738 | 0.019738 | 0.019738 | 0.97266 | -0.5287 | 0.97246 | -0.53282 | 5.4225
114 | 0.0031357 | 0.0007852 | -0.0031354 | -0.0007855 | 3.5676e-07 | -2.9207e-07 | 0.00478 | 0.0047801 | 0.0047801 | 0.97611 | -0.46076 | 0.97599 | -0.46315 | 1.3132
115 | -0.037968 | -0.0095511 | 0.03802 | 0.0095838 | 5.1972e-05 | 3.2745e-05 | 0.057892 | 0.057892 | 0.057892 | 0.97611 | -0.46076 | 0.97757 | -0.43215 | 15.9044
116 | -0.011626 | -0.0029158 | 0.011627 | 0.0029163 | 8.709e-07 | 4.6636e-07 | 0.017792 | 0.017792 | 0.017792 | 0.97238 | -0.53439 | 0.97246 | -0.53282 | 4.8879
117 | 0.010479 | 0.0026284 | -0.010479 | -0.0026281 | 5.7544e-07 | 2.9428e-07 | 0.016037 | 0.016037 | 0.016037 | 0.97238 | -0.53439 | 0.97232 | -0.53554 | 4.4058
118 | 0.01014 | 0.0025431 | -0.01014 | -0.0025431 | 9.4814e-08 | 4.7659e-08 | 0.015518 | 0.015518 | 0.015518 | 0.97232 | -0.53554 | 0.97231 | -0.53573 | 4.2633
119 | 0.0083286 | 0.0020892 | -0.0083249 | -0.0020876 | 3.665e-06 | 1.5999e-06 | 0.012747 | 0.012747 | 0.012747 | 0.97231 | -0.53573 | 0.97184 | -0.54497 | 3.5019
120 | 0.0083249 | 0.0020876 | -0.008321 | -0.0020859 | 3.8839e-06 | 1.6963e-06 | 0.012747 | 0.012747 | 0.012747 | 0.97184 | -0.54497 | 0.97135 | -0.55476 | 3.502
121 | 0.008321 | 0.0020859 | -0.0083191 | -0.002085 | 1.9369e-06 | 8.4627e-07 | 0.012747 | 0.012747 | 0.012747 | 0.97135 | -0.55476 | 0.9711 | -0.55965 | 3.502
122 | 0.0031354 | 0.0007855 | -0.0031351 | -0.00078573 | 2.8336e-07 | -2.3186e-07 | 0.0047801 | 0.0047803 | 0.0047803 | 0.97599 | -0.46315 | 0.9759 | -0.46505 | 1.3133
123 | 0.0071438 | 0.0017905 | -0.007143 | -0.0017902 | 7.5414e-07 | 2.7503e-07 | 0.010946 | 0.010947 | 0.010947 | 0.9711 | -0.55965 | 0.97099 | -0.56186 | 3.0073

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53596 | 0.13606

## res_load
| p_mw | q_mvar
0 | 0.003168 | 0.00079398
1 | 0.002678 | 0.00067116
2 | 0.0021676 | 0.00054324
3 | 0.0054033 | 0.0013542
4 | 0.0041992 | 0.0010524
5 | 0.0046964 | 0.001177
6 | 0.0057471 | 0.0014404
7 | 0.0017951 | 0.0004499
8 | 0.0026796 | 0.00067158
9 | 0.0046965 | 0.001177
10 | 0.002074 | 0.00051981
11 | 0.0050422 | 0.0012637
12 | 0.0024319 | 0.00060949
13 | 0.0039589 | 0.0009922
14 | 0.0043053 | 0.001079
15 | 0.0020329 | 0.00050951
16 | 0.0029076 | 0.00072871
17 | 0.0040675 | 0.0010194
18 | 0.010279 | 0.0025763
19 | 0.003413 | 0.00085537
20 | 0.014229 | 0.0035661
21 | 0.0089664 | 0.0022472
22 | 0.0018787 | 0.00047084
23 | 0.0015738 | 0.00039442
24 | 0.0024259 | 0.00060799
25 | 0.0035849 | 0.00089847
26 | 0.0061981 | 0.0015534
27 | 0.038615 | 0.0096778
28 | 0.00071011 | 0.00017797
29 | 0.00059171 | 0.0001483
30 | 0.0017547 | 0.00043976
31 | 0.0057006 | 0.0014287
32 | 0.005471 | 0.0013712
33 | 0.011686 | 0.0029288
34 | 0.0083221 | 0.0020857
35 | 0.0020007 | 0.00050142
36 | 0.0036626 | 0.00091794
37 | 0.012991 | 0.0032558
38 | 0.0020507 | 0.00051396
39 | 0.012856 | 0.0032221
40 | 0.0013667 | 0.00034252
41 | 0.007331 | 0.0018373
42 | 0.016912 | 0.0042386
43 | 0.0046089 | 0.0011551
44 | 0.017219 | 0.0043155
45 | 0.018063 | 0.004527
46 | 0.049605 | 0.012432
47 | 0.017805 | 0.0044624
48 | 0.0016485 | 0.00041315
49 | 0.0037323 | 0.00093541
50 | 0.0033943 | 0.00085069
51 | 0.0018319 | 0.00045913
52 | 0.0010181 | 0.00025517
53 | 0.0020496 | 0.00051367
54 | 0.0020633 | 0.00051711
55 | 0.0028446 | 0.00071293
56 | 0.0051098 | 0.0012806
57 | 0.0019553 | 0.00049006
58 | 0.016492 | 0.0041332
59 | 0.008303 | 0.0020809
60 | 0.0084471 | 0.002117
61 | 0.0065734 | 0.0016474
62 | 0.0057431 | 0.0014393
63 | 0.00042324 | 0.00010607
64 | 0.00096543 | 0.00024196
65 | 0.0016162 | 0.00040507
66 | 0.0034885 | 0.00087429
67 | 0.0017986 | 0.00045077
68 | 0.0024476 | 0.00061343
69 | 0.0023312 | 0.00058424
70 | 0.00092654 | 0.00023221
71 | 0.016057 | 0.0040243
72 | 0.023448 | 0.0058765
73 | 0.0031823 | 0.00079757
74 | 0.0018068 | 0.00045283
75 | 0.002741 | 0.00068695
76 | 0.0067039 | 0.0016802
77 | 0.0053016 | 0.0013287
78 | 0.0029724 | 0.00074494
79 | 0.001467 | 0.00036766
80 | 0.0022277 | 0.00055833
81 | 0.00036084 | 9.0435e-05
82 | 0.00012491 | 3.1305e-05
83 | 0.00027548 | 6.9043e-05
84 | 0.000143 | 3.584e-05
85 | 0.0011467 | 0.00028738
86 | 0.0012718 | 0.00031875
87 | 0.00033914 | 8.4998e-05
88 | 0.001811 | 0.00045388
89 | 0.0046988 | 0.0011776
90 | 0.0031351 | 0.00078573
91 | 0.0011753 | 0.00029456
92 | 0.007143 | 0.0017902

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1