## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2571-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2571-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2571-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2571-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2571-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2571-1_0_4_node_121 | 0.4 | n |  | TRUE
6 | bus_LV_2571-1_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2571-1_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2571-1_0_4_node_232 | 0.4 | n |  | TRUE
9 | bus_LV_2571-1_0_4_node_60 | 0.4 | n |  | TRUE
10 | bus_LV_2571-1_0_4_node_233 | 0.4 | n |  | TRUE
11 | bus_LV_2571-1_0_4_node_58 | 0.4 | n |  | TRUE
12 | bus_LV_2571-1_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2571-1_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2571-1_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2571-1_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2571-1_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2571-1_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2571-1_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_2571-1_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2571-1_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_2571-1_0_4_node_191 | 0.4 | n |  | TRUE
22 | bus_LV_2571-1_0_4_node_74 | 0.4 | n |  | TRUE
23 | bus_LV_2571-1_0_4_node_90 | 0.4 | n |  | TRUE
24 | bus_LV_2571-1_0_4_node_150 | 0.4 | n |  | TRUE
25 | bus_LV_2571-1_0_4_node_75 | 0.4 | n |  | TRUE
26 | bus_LV_2571-1_0_4_node_91 | 0.4 | n |  | TRUE
27 | bus_LV_2571-1_0_4_node_92 | 0.4 | n |  | TRUE
28 | bus_LV_2571-1_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_2571-1_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2571-1_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2571-1_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_2571-1_0_4_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_2571-1_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_2571-1_0_4_node_172 | 0.4 | n |  | TRUE
35 | bus_LV_2571-1_0_4_node_184 | 0.4 | n |  | TRUE
36 | bus_LV_2571-1_0_4_node_173 | 0.4 | n |  | TRUE
37 | bus_LV_2571-1_0_4_node_174 | 0.4 | n |  | TRUE
38 | bus_LV_2571-1_0_4_node_185 | 0.4 | n |  | TRUE
39 | bus_LV_2571-1_0_4_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_2571-1_0_4_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_2571-1_0_4_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_2571-1_0_4_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_2571-1_0_4_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_2571-1_0_4_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_2571-1_0_4_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_2571-1_0_4_node_201 | 0.4 | n |  | TRUE
47 | bus_LV_2571-1_0_4_node_102 | 0.4 | n |  | TRUE
48 | bus_LV_2571-1_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_2571-1_0_4_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_2571-1_0_4_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_2571-1_0_4_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_2571-1_0_4_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_2571-1_0_4_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_2571-1_0_4_node_103 | 0.4 | n |  | TRUE
55 | bus_LV_2571-1_0_4_node_32 | 0.4 | n |  | TRUE
56 | bus_LV_2571-1_0_4_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_2571-1_0_4_node_200 | 0.4 | n |  | TRUE
58 | bus_LV_2571-1_0_4_node_198 | 0.4 | n |  | TRUE
59 | bus_LV_2571-1_0_4_node_37 | 0.4 | n |  | TRUE
60 | bus_LV_2571-1_0_4_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_2571-1_0_4_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_2571-1_0_4_node_96 | 0.4 | n |  | TRUE
63 | bus_LV_2571-1_0_4_node_94 | 0.4 | n |  | TRUE
64 | bus_LV_2571-1_0_4_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_2571-1_0_4_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_2571-1_0_4_node_236 | 0.4 | n |  | TRUE
67 | bus_LV_2571-1_0_4_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_2571-1_0_4_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_2571-1_0_4_node_199 | 0.4 | n |  | TRUE
70 | bus_LV_2571-1_0_4_node_197 | 0.4 | n |  | TRUE
71 | bus_LV_2571-1_0_4_node_119 | 0.4 | n |  | TRUE
72 | bus_LV_2571-1_0_4_node_238 | 0.4 | n |  | TRUE
73 | bus_LV_2571-1_0_4_node_234 | 0.4 | n |  | TRUE
74 | bus_LV_2571-1_0_4_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_2571-1_0_4_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_2571-1_0_4_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_2571-1_0_4_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_2571-1_0_4_node_230 | 0.4 | n |  | TRUE
79 | bus_LV_2571-1_0_4_node_222 | 0.4 | n |  | TRUE
80 | bus_LV_2571-1_0_4_node_247 | 0.4 | n |  | TRUE
81 | bus_LV_2571-1_0_4_node_95 | 0.4 | n |  | TRUE
82 | bus_LV_2571-1_0_4_node_250 | 0.4 | n |  | TRUE
83 | bus_LV_2571-1_0_4_node_239 | 0.4 | n |  | TRUE
84 | bus_LV_2571-1_0_4_node_104 | 0.4 | n |  | TRUE
85 | bus_LV_2571-1_0_4_node_105 | 0.4 | n |  | TRUE
86 | bus_LV_2571-1_0_4_node_149 | 0.4 | n |  | TRUE
87 | bus_LV_2571-1_0_4_node_170 | 0.4 | n |  | TRUE
88 | bus_LV_2571-1_0_4_node_120 | 0.4 | n |  | TRUE
89 | bus_LV_2571-1_0_4_node_122 | 0.4 | n |  | TRUE
90 | bus_LV_2571-1_0_4_node_124 | 0.4 | n |  | TRUE
91 | bus_LV_2571-1_0_4_node_123 | 0.4 | n |  | TRUE
92 | bus_LV_2571-1_0_4_node_125 | 0.4 | n |  | TRUE
93 | bus_LV_2571-1_0_4_node_129 | 0.4 | n |  | TRUE
94 | bus_LV_2571-1_0_4_node_127 | 0.4 | n |  | TRUE
95 | bus_LV_2571-1_0_4_node_126 | 0.4 | n |  | TRUE
96 | bus_LV_2571-1_0_4_node_128 | 0.4 | n |  | TRUE
97 | bus_LV_2571-1_0_4_node_130 | 0.4 | n |  | TRUE
98 | bus_LV_2571-1_0_4_node_131 | 0.4 | n |  | TRUE
99 | bus_LV_2571-1_0_4_node_132 | 0.4 | n |  | TRUE
100 | bus_LV_2571-1_0_4_node_133 | 0.4 | n |  | TRUE
101 | bus_LV_2571-1_0_4_node_134 | 0.4 | n |  | TRUE
102 | bus_LV_2571-1_0_4_node_135 | 0.4 | n |  | TRUE
103 | bus_LV_2571-1_0_4_node_136 | 0.4 | n |  | TRUE
104 | bus_LV_2571-1_0_4_node_186 | 0.4 | n |  | TRUE
105 | bus_LV_2571-1_0_4_node_211 | 0.4 | n |  | TRUE
106 | bus_LV_2571-1_0_4_node_205 | 0.4 | n |  | TRUE
107 | bus_LV_2571-1_0_4_node_148 | 0.4 | n |  | TRUE
108 | bus_LV_2571-1_0_4_node_235 | 0.4 | n |  | TRUE
109 | bus_LV_2571-1_0_4_node_168 | 0.4 | n |  | TRUE
110 | bus_LV_2571-1_0_4_node_165 | 0.4 | n |  | TRUE
111 | bus_LV_2571-1_0_4_node_166 | 0.4 | n |  | TRUE
112 | bus_LV_2571-1_0_4_node_167 | 0.4 | n |  | TRUE
113 | bus_LV_2571-1_0_4_node_169 | 0.4 | n |  | TRUE
114 | bus_LV_2571-1_0_4_node_171 | 0.4 | n |  | TRUE
115 | bus_LV_2571-1_0_4_node_196 | 0.4 | n |  | TRUE
116 | bus_LV_2571-1_0_4_node_175 | 0.4 | n |  | TRUE
117 | bus_LV_2571-1_0_4_node_195 | 0.4 | n |  | TRUE
118 | bus_LV_2571-1_0_4_node_194 | 0.4 | n |  | TRUE
119 | bus_LV_2571-1_0_4_node_202 | 0.4 | n |  | TRUE
120 | bus_LV_2571-1_0_4_node_203 | 0.4 | n |  | TRUE
121 | bus_LV_2571-1_0_4_node_204 | 0.4 | n |  | TRUE
122 | bus_LV_2571-1_0_4_node_251 | 0.4 | n |  | TRUE
123 | bus_LV_2571-1_0_4_node_252 | 0.4 | n |  | TRUE
124 | bus_MV_397_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2571-1_0_4_load_0 | 0 | 0.0018087 | 0.00045331 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2571-1_0_4_load_1 | 1 | 0.0026879 | 0.00067365 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2571-1_0_4_load_2 | 2 | 0.0018123 | 0.0004542 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2571-1_0_4_load_3 | 3 | 0.0022897 | 0.00057385 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2571-1_0_4_load_4 | 4 | 0.0017287 | 0.00043325 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2571-1_0_4_load_6 | 7 | 0.0018555 | 0.00046504 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2571-1_0_4_load_232 | 8 | 0.0014426 | 0.00036155 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2571-1_0_4_load_60 | 9 | 0.0016469 | 0.00041274 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2571-1_0_4_load_233 | 10 | 0.0019541 | 0.00048973 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2571-1_0_4_load_58 | 11 | 0.0023002 | 0.00057648 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2571-1_0_4_load_7 | 12 | 0.00069437 | 0.00017402 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2571-1_0_4_load_8 | 13 | 0.00096034 | 0.00024068 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2571-1_0_4_load_10 | 15 | 0.00072212 | 0.00018098 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2571-1_0_4_load_11 | 16 | 0.0025584 | 0.0006412 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2571-1_0_4_load_12 | 17 | 0.0011201 | 0.00028073 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2571-1_0_4_load_15 | 20 | 0.00093829 | 0.00023516 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2571-1_0_4_load_191 | 21 | 0.0029594 | 0.0007417 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2571-1_0_4_load_150 | 24 | 0.0021177 | 0.00053075 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2571-1_0_4_load_75 | 25 | 0.003955 | 0.00099122 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2571-1_0_4_load_91 | 26 | 0.0017483 | 0.00043816 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2571-1_0_4_load_92 | 27 | 0.0027731 | 0.000695 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2571-1_0_4_load_16 | 28 | 0.00064742 | 0.00016226 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2571-1_0_4_load_18 | 30 | 0.011309 | 0.0028343 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2571-1_0_4_load_19 | 31 | 0.0020482 | 0.00051332 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2571-1_0_4_load_20 | 32 | 0.0043101 | 0.0010802 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2571-1_0_4_load_21 | 33 | 0.0013594 | 0.0003407 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2571-1_0_4_load_184 | 35 | 0.0083603 | 0.0020953 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2571-1_0_4_load_173 | 36 | 0.0035723 | 0.0008953 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2571-1_0_4_load_174 | 37 | 0.0013486 | 0.000338 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2571-1_0_4_load_185 | 38 | 0.0048335 | 0.0012114 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2571-1_0_4_load_22 | 39 | 0.0010707 | 0.00026835 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2571-1_0_4_load_23 | 40 | 0.0014737 | 0.00036935 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2571-1_0_4_load_25 | 42 | 0.00051805 | 0.00012983 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2571-1_0_4_load_26 | 43 | 0.001165 | 0.00029199 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2571-1_0_4_load_27 | 44 | 0.0010961 | 0.00027471 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2571-1_0_4_load_30 | 45 | 0.0010991 | 0.00027547 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2571-1_0_4_load_201 | 46 | 0.00088404 | 0.00022156 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2571-1_0_4_load_102 | 47 | 0.00072832 | 0.00018253 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2571-1_0_4_load_38 | 48 | 0.00066987 | 0.00016789 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2571-1_0_4_load_28 | 49 | 0.0027728 | 0.00069492 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2571-1_0_4_load_31 | 53 | 0.0011281 | 0.00028273 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2571-1_0_4_load_103 | 54 | 0.0008561 | 0.00021456 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2571-1_0_4_load_32 | 55 | 0.0009403 | 0.00023566 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2571-1_0_4_load_36 | 56 | 0.0045829 | 0.0011486 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2571-1_0_4_load_200 | 57 | 0.0063142 | 0.0015825 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2571-1_0_4_load_198 | 58 | 0.0023115 | 0.00057931 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2571-1_0_4_load_37 | 59 | 0.00067393 | 0.0001689 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2571-1_0_4_load_39 | 60 | 0.00095529 | 0.00023942 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2571-1_0_4_load_40 | 61 | 0.0010522 | 0.00026371 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2571-1_0_4_load_96 | 62 | 0.0010227 | 0.0002563 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2571-1_0_4_load_94 | 63 | 0.0025525 | 0.00063972 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2571-1_0_4_load_52 | 64 | 0.0024684 | 0.00061865 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2571-1_0_4_load_55 | 65 | 0.0027515 | 0.0006896 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2571-1_0_4_load_53 | 67 | 0.0015511 | 0.00038875 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2571-1_0_4_load_54 | 68 | 0.0015734 | 0.00039433 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2571-1_0_4_load_199 | 69 | 0.011883 | 0.0029782 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2571-1_0_4_load_197 | 70 | 0.0063193 | 0.0015838 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2571-1_0_4_load_119 | 71 | 0.0019625 | 0.00049184 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2571-1_0_4_load_238 | 72 | 0.0028805 | 0.00072193 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2571-1_0_4_load_234 | 73 | 0.0017459 | 0.00043756 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2571-1_0_4_load_56 | 74 | 0.0028974 | 0.00072616 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2571-1_0_4_load_57 | 75 | 0.0010622 | 0.00026622 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2571-1_0_4_load_59 | 76 | 0.0015308 | 0.00038365 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2571-1_0_4_load_61 | 77 | 0.0032153 | 0.00080584 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2571-1_0_4_load_230 | 78 | 0.0011234 | 0.00028155 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2571-1_0_4_load_222 | 79 | 0.0019282 | 0.00048325 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2571-1_0_4_load_95 | 81 | 0.0025569 | 0.00064083 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2571-1_0_4_load_250 | 82 | 0.0023551 | 0.00059024 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2571-1_0_4_load_239 | 83 | 0.0023595 | 0.00059135 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2571-1_0_4_load_104 | 84 | 0.005906 | 0.0014802 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2571-1_0_4_load_105 | 85 | 0.0011466 | 0.00028738 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2571-1_0_4_load_170 | 87 | 0.0012712 | 0.0003186 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2571-1_0_4_load_120 | 88 | 0.0064653 | 0.0016204 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2571-1_0_4_load_122 | 89 | 0.0040047 | 0.0010037 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2571-1_0_4_load_124 | 90 | 0.011971 | 0.0030003 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2571-1_0_4_load_123 | 91 | 0.014561 | 0.0036493 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2571-1_0_4_load_125 | 92 | 0.0012426 | 0.00031142 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2571-1_0_4_load_129 | 93 | 0.0026852 | 0.00067298 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2571-1_0_4_load_126 | 95 | 0.0026588 | 0.00066636 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2571-1_0_4_load_130 | 97 | 0.0030188 | 0.00075658 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2571-1_0_4_load_131 | 98 | 0.0026163 | 0.00065571 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2571-1_0_4_load_132 | 99 | 0.002401 | 0.00060175 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2571-1_0_4_load_133 | 100 | 0.0058626 | 0.0014693 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2571-1_0_4_load_134 | 101 | 0.0016926 | 0.00042421 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2571-1_0_4_load_135 | 102 | 0.0024986 | 0.00062621 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2571-1_0_4_load_136 | 103 | 0.001682 | 0.00042156 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2571-1_0_4_load_186 | 104 | 0.0025168 | 0.00063078 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2571-1_0_4_load_211 | 105 | 0.0016643 | 0.00041711 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2571-1_0_4_load_205 | 106 | 0.0024547 | 0.0006152 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2571-1_0_4_load_148 | 107 | 0.0021235 | 0.00053221 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2571-1_0_4_load_235 | 108 | 0.0015436 | 0.00038685 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2571-1_0_4_load_165 | 110 | 0.00091372 | 0.000229 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2571-1_0_4_load_166 | 111 | 0.0045855 | 0.0011492 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2571-1_0_4_load_169 | 113 | 0.0011571 | 0.00028999 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2571-1_0_4_load_171 | 114 | 0.001662 | 0.00041654 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2571-1_0_4_load_196 | 115 | 0.0010871 | 0.00027245 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2571-1_0_4_load_175 | 116 | 0.0013324 | 0.00033394 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2571-1_0_4_load_195 | 117 | 0.0017348 | 0.00043479 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2571-1_0_4_load_194 | 118 | 0.0024498 | 0.00061397 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2571-1_0_4_load_202 | 119 | 0.0018527 | 0.00046432 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2571-1_0_4_load_203 | 120 | 0.0015972 | 0.0004003 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2571-1_0_4_load_204 | 121 | 0.0041821 | 0.0010481 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2571-1_0_4_load_251 | 122 | 0.0032187 | 0.00080667 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2571-1_0_4_load_252 | 123 | 0.0065146 | 0.0016327 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2571-1_0_4_line_0 |  | 0 | 1 | 0.020018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2571-1_0_4_line_1 |  | 0 | 2 | 0.017269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2571-1_0_4_line_2 |  | 1 | 3 | 0.024016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2571-1_0_4_line_3 |  | 2 | 4 | 0.010067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2571-1_0_4_line_4 |  | 2 | 5 | 0.04232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_2571-1_0_4_line_5 |  | 3 | 6 | 0.012869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2571-1_0_4_line_6 |  | 4 | 7 | 0.0019583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2571-1_0_4_line_7 |  | 5 | 71 | 0.029597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2571-1_0_4_line_8 |  | 5 | 68 | 0.031161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_2571-1_0_4_line_9 |  | 6 | 8 | 0.03941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2571-1_0_4_line_10 |  | 7 | 9 | 0.010483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2571-1_0_4_line_11 |  | 8 | 10 | 0.024532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2571-1_0_4_line_12 |  | 9 | 11 | 0.010928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2571-1_0_4_line_13 |  | 10 | 108 | 0.050701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2571-1_0_4_line_14 |  | 10 | 107 | 0.028458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2571-1_0_4_line_15 |  | 11 | 74 | 0.020979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2571-1_0_4_line_16 |  | 12 | 13 | 0.02464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2571-1_0_4_line_17 |  | 12 | 14 | 0.014477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2571-1_0_4_line_18 |  | 13 | 15 | 0.0024628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2571-1_0_4_line_19 |  | 14 | 16 | 0.035253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2571-1_0_4_line_20 |  | 14 | 17 | 0.013338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2571-1_0_4_line_21 |  | 15 | 18 | 0.053887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2571-1_0_4_line_22 |  | 16 | 19 | 0.0079234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2571-1_0_4_line_23 |  | 17 | 20 | 0.021918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2571-1_0_4_line_24 |  | 18 | 21 | 0.019077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2571-1_0_4_line_25 |  | 18 | 22 | 0.048372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2571-1_0_4_line_26 |  | 19 | 23 | 0.010654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2571-1_0_4_line_27 |  | 20 | 24 | 0.0054116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2571-1_0_4_line_28 |  | 22 | 25 | 0.016163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2571-1_0_4_line_29 |  | 23 | 26 | 0.038679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2571-1_0_4_line_30 |  | 23 | 27 | 0.012039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2571-1_0_4_line_31 |  | 25 | 79 | 0.027013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2571-1_0_4_line_32 |  | 26 | 80 | 0.016047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2571-1_0_4_line_33 |  | 27 | 81 | 0.024491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2571-1_0_4_line_34 |  | 28 | 29 | 0.03584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2571-1_0_4_line_35 |  | 29 | 30 | 0.029791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2571-1_0_4_line_36 |  | 29 | 31 | 0.016667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2571-1_0_4_line_37 |  | 30 | 32 | 0.035197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2571-1_0_4_line_38 |  | 31 | 33 | 0.010801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2571-1_0_4_line_39 |  | 32 | 34 | 0.036976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2571-1_0_4_line_40 |  | 33 | 35 | 0.022669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2571-1_0_4_line_41 |  | 34 | 36 | 0.034607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2571-1_0_4_line_42 |  | 34 | 37 | 0.026963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2571-1_0_4_line_43 |  | 35 | 38 | 0.0021447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2571-1_0_4_line_44 |  | 36 | 116 | 0.019532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2571-1_0_4_line_45 |  | 37 | 92 | 0.022965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2571-1_0_4_line_46 |  | 38 | 101 | 0.014647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2571-1_0_4_line_47 |  | 39 | 40 | 0.0012061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2571-1_0_4_line_48 |  | 39 | 41 | 0.019435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2571-1_0_4_line_49 |  | 40 | 42 | 0.011675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2571-1_0_4_line_50 |  | 41 | 43 | 0.029644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2571-1_0_4_line_51 |  | 42 | 44 | 0.01809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2571-1_0_4_line_52 |  | 43 | 45 | 0.0049631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2571-1_0_4_line_53 |  | 44 | 46 | 0.016979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2571-1_0_4_line_54 |  | 45 | 47 | 0.020477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2571-1_0_4_line_55 |  | 46 | 48 | 0.020487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2571-1_0_4_line_56 |  | 47 | 54 | 0.025247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2571-1_0_4_line_57 |  | 48 | 59 | 0.0022516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2571-1_0_4_line_58 |  | 49 | 50 | 0.024017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2571-1_0_4_line_59 |  | 50 | 51 | 0.061194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2571-1_0_4_line_60 |  | 51 | 52 | 0.050664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2571-1_0_4_line_61 |  | 51 | 53 | 0.016096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2571-1_0_4_line_62 |  | 52 | 56 | 0.013278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2571-1_0_4_line_63 |  | 53 | 55 | 0.0092064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2571-1_0_4_line_64 |  | 54 | 84 | 0.014635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2571-1_0_4_line_65 |  | 56 | 57 | 0.02638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2571-1_0_4_line_66 |  | 57 | 58 | 0.00035195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_2571-1_0_4_line_67 |  | 58 | 70 | 0.020322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2571-1_0_4_line_68 |  | 59 | 60 | 0.045929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2571-1_0_4_line_69 |  | 60 | 61 | 0.022165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2571-1_0_4_line_70 |  | 61 | 62 | 0.039125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2571-1_0_4_line_71 |  | 62 | 63 | 0.01427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2571-1_0_4_line_72 |  | 63 | 81 | 0.00024367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2571-1_0_4_line_73 |  | 64 | 65 | 0.023857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2571-1_0_4_line_74 |  | 65 | 66 | 0.040294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2571-1_0_4_line_75 |  | 66 | 72 | 0.016879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_2571-1_0_4_line_76 |  | 66 | 73 | 0.052045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_2571-1_0_4_line_77 |  | 67 | 68 | 0.00075678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_2571-1_0_4_line_78 |  | 67 | 69 | 0.048143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_2571-1_0_4_line_79 |  | 69 | 70 | 0.0031622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2571-1_0_4_line_80 |  | 71 | 88 | 0.0044807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2571-1_0_4_line_81 |  | 72 | 83 | 0.022334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_2571-1_0_4_line_82 |  | 73 | 108 | 0.012727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_2571-1_0_4_line_83 |  | 74 | 75 | 0.016119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2571-1_0_4_line_84 |  | 75 | 76 | 0.006631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2571-1_0_4_line_85 |  | 76 | 77 | 0.01546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2571-1_0_4_line_86 |  | 77 | 78 | 0.0097821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2571-1_0_4_line_87 |  | 80 | 82 | 0.033189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2571-1_0_4_line_88 |  | 80 | 83 | 0.016138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2571-1_0_4_line_89 |  | 82 | 122 | 0.0022612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2571-1_0_4_line_90 |  | 84 | 85 | 0.0018438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2571-1_0_4_line_91 |  | 85 | 86 | 0.022753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2571-1_0_4_line_92 |  | 86 | 87 | 0.045004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2571-1_0_4_line_93 |  | 87 | 109 | 0.06013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2571-1_0_4_line_94 |  | 88 | 89 | 0.018629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2571-1_0_4_line_95 |  | 89 | 90 | 0.029994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2571-1_0_4_line_96 |  | 90 | 93 | 0.0015133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2571-1_0_4_line_97 |  | 91 | 92 | 0.0078291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2571-1_0_4_line_98 |  | 93 | 94 | 0.026182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2571-1_0_4_line_99 |  | 94 | 97 | 0.013828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2571-1_0_4_line_100 |  | 94 | 98 | 0.023401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2571-1_0_4_line_101 |  | 94 | 95 | 0.040345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2571-1_0_4_line_102 |  | 95 | 96 | 0.017044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2571-1_0_4_line_103 |  | 96 | 99 | 0.023206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2571-1_0_4_line_104 |  | 96 | 100 | 0.037877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2571-1_0_4_line_105 |  | 97 | 101 | 0.025718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2571-1_0_4_line_106 |  | 98 | 102 | 0.010698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2571-1_0_4_line_107 |  | 99 | 103 | 0.033505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2571-1_0_4_line_108 |  | 99 | 104 | 0.059527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2571-1_0_4_line_109 |  | 102 | 105 | 0.018596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2571-1_0_4_line_110 |  | 105 | 106 | 0.0031569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2571-1_0_4_line_111 |  | 106 | 121 | 0.019325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2571-1_0_4_line_112 |  | 109 | 114 | 0.034513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2571-1_0_4_line_113 |  | 109 | 112 | 0.019232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2571-1_0_4_line_114 |  | 110 | 111 | 0.0072743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2571-1_0_4_line_115 |  | 110 | 112 | 0.020882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2571-1_0_4_line_116 |  | 112 | 113 | 0.033863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2571-1_0_4_line_117 |  | 114 | 115 | 0.0056814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2571-1_0_4_line_118 |  | 116 | 117 | 0.050323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2571-1_0_4_line_119 |  | 117 | 118 | 0.013783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2571-1_0_4_line_120 |  | 119 | 120 | 0.015934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2571-1_0_4_line_121 |  | 120 | 121 | 0.0043608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2571-1_0_4_line_122 |  | 122 | 123 | 0.016696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2571-1_0_4_trafo_200 | 0.63 MVA 20/0.4 kV | 124 | 57 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2631428.0604 | 1239587.4637 | 2631416.4327 | 1239603.7585
1 | 2631428.0604 | 1239587.4637 | 2631434.6016 | 1239578.2969 | 2631438.165 | 1239573.4599
2 | 2631416.4327 | 1239603.7585 | 2631402.4828 | 1239623.3075
3 | 2631438.165 | 1239573.4599 | 2631438.5016 | 1239573.0031 | 2631442.5983 | 1239569.1001 | 2631445.4805 | 1239566.5603
4 | 2631400.8993 | 1239553.4031 | 2631438.165 | 1239573.4599
5 | 2631396.304 | 1239634.4968 | 2631398.7021 | 1239628.6057 | 2631402.4828 | 1239623.3075
6 | 2631446.9629 | 1239565.2821 | 2631446.7999 | 1239565.3977 | 2631445.4805 | 1239566.5603
7 | 2631400.8993 | 1239553.4031 | 2631387.4018 | 1239537.3996 | 2631381.7281 | 1239530.8548
8 | 2631400.8993 | 1239553.4031 | 2631380.3627 | 1239576.8395
9 | 2631396.304 | 1239634.4968 | 2631412.8023 | 1239640.6989 | 2631433.5481 | 1239647.3439
10 | 2631456.4041 | 1239561.1014 | 2631452.899 | 1239561.8055 | 2631449.8969 | 1239563.2016 | 2631446.9629 | 1239565.2821
11 | 2631433.5481 | 1239647.3439 | 2631450.6024 | 1239652.8064 | 2631457.016 | 1239654.4642
12 | 2631456.4041 | 1239561.1014 | 2631456.4041 | 1239561.1014 | 2631460.3015 | 1239562.0003 | 2631466.8 | 1239564.4029
13 | 2631459.8832 | 1239705.0836 | 2631457.016 | 1239654.4642
14 | 2631484.9656 | 1239659.5519 | 2631479.601 | 1239658.9971 | 2631467.2015 | 1239657.0969 | 2631457.016 | 1239654.4642
15 | 2631466.8 | 1239564.4029 | 2631466.8 | 1239564.4029 | 2631474.1981 | 1239569.701 | 2631483.2619 | 1239577.3806
16 | 2631310.1118 | 1239848.9859 | 2631298.2128 | 1239870.5622
17 | 2631317.0997 | 1239836.3067 | 2631312.1827 | 1239845.2309 | 2631310.1118 | 1239848.9859
18 | 2631297.0234 | 1239872.7188 | 2631298.2128 | 1239870.5622
19 | 2631317.0997 | 1239836.3067 | 2631333.675 | 1239805.1936
20 | 2631317.0997 | 1239836.3067 | 2631304.9989 | 1239830.6967
21 | 2631271.0004 | 1239919.9058 | 2631297.0234 | 1239872.7188
22 | 2631337.4004 | 1239798.2006 | 2631333.675 | 1239805.1936
23 | 2631304.9989 | 1239830.6967 | 2631285.1136 | 1239821.4778
24 | 2631271.0004 | 1239919.9058 | 2631252.4139 | 1239915.6053
25 | 2631271.0004 | 1239919.9058 | 2631291.2021 | 1239924.9041 | 2631317.8559 | 1239932.427
26 | 2631337.4004 | 1239798.2006 | 2631342.6294 | 1239788.9112
27 | 2631280.204 | 1239819.2017 | 2631285.1136 | 1239821.4778
28 | 2631317.8559 | 1239932.427 | 2631323.9445 | 1239917.4551
29 | 2631342.6294 | 1239788.9112 | 2631361.6738 | 1239755.2458
30 | 2631342.6294 | 1239788.9112 | 2631331.7232 | 1239783.8138
31 | 2631334.1207 | 1239892.4318 | 2631323.9445 | 1239917.4551
32 | 2631369.5749 | 1239741.2788 | 2631361.6738 | 1239755.2458
33 | 2631331.7232 | 1239783.8138 | 2631309.5361 | 1239773.4438
34 | 2631410.0357 | 1239402.9675 | 2631407.0982 | 1239395.0025 | 2631400.2157 | 1239368.5316
35 | 2631410.0357 | 1239402.9675 | 2631414.8448 | 1239411.6873 | 2631422.7638 | 1239424.3594 | 2631426.1749 | 1239427.8635
36 | 2631410.0357 | 1239402.9675 | 2631395.9302 | 1239411.8466
37 | 2631426.1749 | 1239427.8635 | 2631434.2193 | 1239436.1273 | 2631453.7426 | 1239449.5004
38 | 2631395.9302 | 1239411.8466 | 2631386.7891 | 1239417.6007
39 | 2631480.0103 | 1239473.2375 | 2631478.6422 | 1239467.3932 | 2631474.5618 | 1239462.4907 | 2631470.1033 | 1239458.9983 | 2631457.1037 | 1239451.8027 | 2631453.7426 | 1239449.5004
40 | 2631369.2635 | 1239431.9107 | 2631382.8867 | 1239420.0572 | 2631386.7891 | 1239417.6007
41 | 2631480.0103 | 1239473.2375 | 2631488.5993 | 1239473.6165 | 2631497.9445 | 1239475.4227 | 2631507.2743 | 1239480.1195 | 2631511.7275 | 1239484.2087
42 | 2631480.0103 | 1239473.2375 | 2631476.9262 | 1239482.9828 | 2631471.4541 | 1239489.5247 | 2631464.9454 | 1239494.5333
43 | 2631367.6455 | 1239433.3185 | 2631369.2635 | 1239431.9107
44 | 2631525.5641 | 1239497.9647 | 2631520.0005 | 1239491.8055 | 2631511.7275 | 1239484.2087
45 | 2631464.9454 | 1239494.5333 | 2631460.0033 | 1239498.3363 | 2631447.3542 | 1239509.2838
46 | 2631358.8306 | 1239444.0716 | 2631360.8984 | 1239442.2997 | 2631361.2188 | 1239438.9103 | 2631367.6455 | 1239433.3185
47 | 2631174.8734 | 1239800.3363 | 2631173.8467 | 1239799.7034
48 | 2631157.303 | 1239789.5043 | 2631173.8467 | 1239799.7034
49 | 2631174.8734 | 1239800.3363 | 2631184.8114 | 1239806.463
50 | 2631157.303 | 1239789.5043 | 2631147.1031 | 1239807.9959 | 2631144.4998 | 1239812.6963 | 2631142.188 | 1239814.8403
51 | 2631200.2106 | 1239815.9565 | 2631184.8114 | 1239806.463
52 | 2631138.0625 | 1239817.5895 | 2631141.901 | 1239815.1065 | 2631142.188 | 1239814.8403
53 | 2631201.8558 | 1239830.3526 | 2631205.1682 | 1239821.6756 | 2631201.9033 | 1239817 | 2631200.2106 | 1239815.9565
54 | 2631138.0625 | 1239817.5895 | 2631120.8691 | 1239828.712
55 | 2631201.8558 | 1239830.3526 | 2631222.3288 | 1239831.1052
56 | 2631120.8691 | 1239828.712 | 2631106.2008 | 1239838.2009 | 2631103.103 | 1239840.5973 | 2631100.803 | 1239843.6983 | 2631100.803 | 1239843.6983
57 | 2631223.5466 | 1239829.2114 | 2631222.3288 | 1239831.1052
58 | 2631231.9771 | 1239653.032 | 2631228.0226 | 1239655.8019 | 2631225.3775 | 1239658.3674 | 2631218.0007 | 1239672.0039
59 | 2631231.9771 | 1239653.032 | 2631240.4893 | 1239607.548 | 2631242.1843 | 1239598.718 | 2631243.3039 | 1239592.898
60 | 2631292.1674 | 1239605.1627 | 2631259.4862 | 1239598.8312 | 2631251.3122 | 1239597.2428 | 2631246.7314 | 1239595.4287 | 2631243.3039 | 1239592.898
61 | 2631243.3039 | 1239592.898 | 2631231.9447 | 1239594.4393 | 2631227.4807 | 1239595.6764
62 | 2631292.1674 | 1239605.1627 | 2631295.3846 | 1239595.9404 | 2631297.7063 | 1239593.3069
63 | 2631218.6567 | 1239598.3007 | 2631225.8028 | 1239596.1414 | 2631227.4807 | 1239595.6764
64 | 2631100.803 | 1239843.6983 | 2631094.0495 | 1239856.682
65 | 2631317.0204 | 1239575.4062 | 2631302.1555 | 1239588.2601 | 2631297.7063 | 1239593.3069
66 | 2631317.2866 | 1239575.176 | 2631317.0204 | 1239575.4062
67 | 2631317.2866 | 1239575.176 | 2631332.6583 | 1239561.8838
68 | 2631223.5466 | 1239829.2114 | 2631230.2667 | 1239818.7611 | 2631239.4468 | 1239802.9771 | 2631246.7489 | 1239789.5942
69 | 2631257.3655 | 1239770.1368 | 2631246.7489 | 1239789.5942
70 | 2631296.3878 | 1239767.2984 | 2631257.3655 | 1239770.1368
71 | 2631296.3878 | 1239767.2984 | 2631309.3154 | 1239773.3406
72 | 2631309.3154 | 1239773.3406 | 2631309.5361 | 1239773.4438
73 | 2631360.1432 | 1239676.3886 | 2631347.729 | 1239670.8301 | 2631338.2493 | 1239666.9169
74 | 2631396.8112 | 1239693.092 | 2631375.0925 | 1239683.0822 | 2631360.1432 | 1239676.3886
75 | 2631396.8112 | 1239693.092 | 2631388.5064 | 1239707.7867
76 | 2631396.8112 | 1239693.092 | 2631406.9001 | 1239697.2035 | 2631412.1009 | 1239698.9988 | 2631421.5998 | 1239701.7062 | 2631428.2408 | 1239702.8754 | 2631439.3649 | 1239704.2684 | 2631447.1612 | 1239704.8454
77 | 2631380.3627 | 1239576.8395 | 2631379.864 | 1239577.4087
78 | 2631379.864 | 1239577.4087 | 2631335.0503 | 1239559.8154
79 | 2631335.0503 | 1239559.8154 | 2631332.6583 | 1239561.8838
80 | 2631378.7931 | 1239527.4692 | 2631381.7281 | 1239530.8548
81 | 2631388.5064 | 1239707.7867 | 2631382.5212 | 1239718.377 | 2631377.5168 | 1239727.2297
82 | 2631459.8832 | 1239705.0836 | 2631448.5872 | 1239704.9509 | 2631447.1612 | 1239704.8454
83 | 2631495.389 | 1239587.9965 | 2631495.2011 | 1239587.8014 | 2631486.0029 | 1239579.7031 | 2631483.2619 | 1239577.3806
84 | 2631499.988 | 1239592.7735 | 2631495.389 | 1239587.9965
85 | 2631510.4744 | 1239604.1308 | 2631510.2031 | 1239603.8021 | 2631503.0981 | 1239596.004 | 2631499.988 | 1239592.7735
86 | 2631510.4744 | 1239604.1308 | 2631515.8987 | 1239610.7033 | 2631516.6611 | 1239611.7069
87 | 2631369.5749 | 1239741.2788 | 2631339.6903 | 1239726.8413
88 | 2631369.5749 | 1239741.2788 | 2631377.5168 | 1239727.2297
89 | 2631339.6903 | 1239726.8413 | 2631337.6542 | 1239725.8577
90 | 2631093.1987 | 1239858.3177 | 2631094.0495 | 1239856.682
91 | 2631082.699 | 1239878.5034 | 2631093.1987 | 1239858.3177
92 | 2631082.699 | 1239878.5034 | 2631038.6313 | 1239869.3712
93 | 2630979.3485 | 1239859.9301 | 2630986.4931 | 1239860.212 | 2630996.3189 | 1239861.1193 | 2631016.9284 | 1239864.8736 | 2631038.6313 | 1239869.3712
94 | 2631378.7931 | 1239527.4692 | 2631366.5904 | 1239513.3931
95 | 2631346.9433 | 1239490.7299 | 2631366.5904 | 1239513.3931
96 | 2631346.9433 | 1239490.7299 | 2631345.9521 | 1239489.5865
97 | 2631441.4343 | 1239514.4072 | 2631447.3542 | 1239509.2838
98 | 2631328.8019 | 1239469.8034 | 2631345.9521 | 1239489.5865
99 | 2631328.8019 | 1239469.8034 | 2631339.302 | 1239460.8058
100 | 2631328.8019 | 1239469.8034 | 2631311.0378 | 1239485.0366
101 | 2631328.8019 | 1239469.8034 | 2631302.0863 | 1239439.5705
102 | 2631290.8001 | 1239426.7984 | 2631302.0863 | 1239439.5705
103 | 2631290.8001 | 1239426.7984 | 2631288.3992 | 1239428.8982 | 2631273.0095 | 1239441.6965
104 | 2631319.5997 | 1239402.1011 | 2631290.8001 | 1239426.7984
105 | 2631358.8306 | 1239444.0716 | 2631339.302 | 1239460.8058
106 | 2631302.9169 | 1239492.0006 | 2631311.0378 | 1239485.0366
107 | 2631247.4034 | 1239463.3043 | 2631264.1004 | 1239449.1054 | 2631273.0095 | 1239441.6965
108 | 2631273.0095 | 1239441.6965 | 2631237.0105 | 1239394.2885
109 | 2631288.8003 | 1239504.106 | 2631302.9169 | 1239492.0006
110 | 2631286.4038 | 1239506.1611 | 2631288.8003 | 1239504.106
111 | 2631271.7338 | 1239518.7411 | 2631286.4038 | 1239506.1611
112 | 2630979.3485 | 1239859.9301 | 2630981.993 | 1239848.748 | 2630990.6609 | 1239836.7856 | 2630996.8111 | 1239831.2871
113 | 2630960.0979 | 1239860.9639 | 2630968.1552 | 1239860.2387 | 2630974.8793 | 1239859.9513 | 2630979.3485 | 1239859.9301
114 | 2630953.4429 | 1239833.6048 | 2630955.1623 | 1239840.6731
115 | 2630960.0979 | 1239860.9639 | 2630955.1623 | 1239840.6731
116 | 2630960.0979 | 1239860.9639 | 2630953.8315 | 1239861.943 | 2630941.0324 | 1239864.2222 | 2630926.7596 | 1239866.8925
117 | 2631001.0466 | 1239827.5005 | 2630996.8111 | 1239831.2871
118 | 2631525.5641 | 1239497.9647 | 2631530.2028 | 1239503.1 | 2631538.2026 | 1239513.3045 | 2631544.301 | 1239522.6983 | 2631550.897 | 1239533.7959 | 2631553.9465 | 1239539.3396
119 | 2631560.2731 | 1239551.5784 | 2631557.5032 | 1239545.8052 | 2631553.9465 | 1239539.3396
120 | 2631268.4234 | 1239521.5799 | 2631256.3277 | 1239531.9523
121 | 2631268.4234 | 1239521.5799 | 2631271.7338 | 1239518.7411
122 | 2631322.6203 | 1239718.5947 | 2631337.6542 | 1239725.8577

## bus_geodata
| x | y | coords
0 | 2631428.0604 | 1239587.4637
1 | 2631416.4327 | 1239603.7585
2 | 2631438.165 | 1239573.4599
3 | 2631402.4828 | 1239623.3075
4 | 2631445.4805 | 1239566.5603
5 | 2631400.8993 | 1239553.4031
6 | 2631396.304 | 1239634.4968
7 | 2631446.9629 | 1239565.2821
8 | 2631433.5481 | 1239647.3439
9 | 2631456.4041 | 1239561.1014
10 | 2631457.016 | 1239654.4642
11 | 2631466.8 | 1239564.4029
12 | 2631310.1118 | 1239848.9859
13 | 2631298.2128 | 1239870.5622
14 | 2631317.0997 | 1239836.3067
15 | 2631297.0234 | 1239872.7188
16 | 2631333.675 | 1239805.1936
17 | 2631304.9989 | 1239830.6967
18 | 2631271.0004 | 1239919.9058
19 | 2631337.4004 | 1239798.2006
20 | 2631285.1136 | 1239821.4778
21 | 2631252.4139 | 1239915.6053
22 | 2631317.8559 | 1239932.427
23 | 2631342.6294 | 1239788.9112
24 | 2631280.204 | 1239819.2017
25 | 2631323.9445 | 1239917.4551
26 | 2631361.6738 | 1239755.2458
27 | 2631331.7232 | 1239783.8138
28 | 2631400.2157 | 1239368.5316
29 | 2631410.0357 | 1239402.9675
30 | 2631426.1749 | 1239427.8635
31 | 2631395.9302 | 1239411.8466
32 | 2631453.7426 | 1239449.5004
33 | 2631386.7891 | 1239417.6007
34 | 2631480.0103 | 1239473.2375
35 | 2631369.2635 | 1239431.9107
36 | 2631511.7275 | 1239484.2087
37 | 2631464.9454 | 1239494.5333
38 | 2631367.6455 | 1239433.3185
39 | 2631173.8467 | 1239799.7034
40 | 2631174.8734 | 1239800.3363
41 | 2631157.303 | 1239789.5043
42 | 2631184.8114 | 1239806.463
43 | 2631142.188 | 1239814.8403
44 | 2631200.2106 | 1239815.9565
45 | 2631138.0625 | 1239817.5895
46 | 2631201.8558 | 1239830.3526
47 | 2631120.8691 | 1239828.712
48 | 2631222.3288 | 1239831.1052
49 | 2631218.0007 | 1239672.0039
50 | 2631231.9771 | 1239653.032
51 | 2631243.3039 | 1239592.898
52 | 2631292.1674 | 1239605.1627
53 | 2631227.4807 | 1239595.6764
54 | 2631100.803 | 1239843.6983
55 | 2631218.6567 | 1239598.3007
56 | 2631297.7063 | 1239593.3069
57 | 2631317.0204 | 1239575.4062
58 | 2631317.2866 | 1239575.176
59 | 2631223.5466 | 1239829.2114
60 | 2631246.7489 | 1239789.5942
61 | 2631257.3655 | 1239770.1368
62 | 2631296.3878 | 1239767.2984
63 | 2631309.3154 | 1239773.3406
64 | 2631338.2493 | 1239666.9169
65 | 2631360.1432 | 1239676.3886
66 | 2631396.8112 | 1239693.092
67 | 2631379.864 | 1239577.4087
68 | 2631380.3627 | 1239576.8395
69 | 2631335.0503 | 1239559.8154
70 | 2631332.6583 | 1239561.8838
71 | 2631381.7281 | 1239530.8548
72 | 2631388.5064 | 1239707.7867
73 | 2631447.1612 | 1239704.8454
74 | 2631483.2619 | 1239577.3806
75 | 2631495.389 | 1239587.9965
76 | 2631499.988 | 1239592.7735
77 | 2631510.4744 | 1239604.1308
78 | 2631516.6611 | 1239611.7069
79 | 2631334.1207 | 1239892.4318
80 | 2631369.5749 | 1239741.2788
81 | 2631309.5361 | 1239773.4438
82 | 2631339.6903 | 1239726.8413
83 | 2631377.5168 | 1239727.2297
84 | 2631094.0495 | 1239856.682
85 | 2631093.1987 | 1239858.3177
86 | 2631082.699 | 1239878.5034
87 | 2631038.6313 | 1239869.3712
88 | 2631378.7931 | 1239527.4692
89 | 2631366.5904 | 1239513.3931
90 | 2631346.9433 | 1239490.7299
91 | 2631441.4343 | 1239514.4072
92 | 2631447.3542 | 1239509.2838
93 | 2631345.9521 | 1239489.5865
94 | 2631328.8019 | 1239469.8034
95 | 2631302.0863 | 1239439.5705
96 | 2631290.8001 | 1239426.7984
97 | 2631339.302 | 1239460.8058
98 | 2631311.0378 | 1239485.0366
99 | 2631273.0095 | 1239441.6965
100 | 2631319.5997 | 1239402.1011
101 | 2631358.8306 | 1239444.0716
102 | 2631302.9169 | 1239492.0006
103 | 2631247.4034 | 1239463.3043
104 | 2631237.0105 | 1239394.2885
105 | 2631288.8003 | 1239504.106
106 | 2631286.4038 | 1239506.1611
107 | 2631484.9656 | 1239659.5519
108 | 2631459.8832 | 1239705.0836
109 | 2630979.3485 | 1239859.9301
110 | 2630955.1623 | 1239840.6731
111 | 2630953.4429 | 1239833.6048
112 | 2630960.0979 | 1239860.9639
113 | 2630926.7596 | 1239866.8925
114 | 2630996.8111 | 1239831.2871
115 | 2631001.0466 | 1239827.5005
116 | 2631525.5641 | 1239497.9647
117 | 2631553.9465 | 1239539.3396
118 | 2631560.2731 | 1239551.5784
119 | 2631256.3277 | 1239531.9523
120 | 2631268.4234 | 1239521.5799
121 | 2631271.7338 | 1239518.7411
122 | 2631337.6542 | 1239725.8577
123 | 2631322.6203 | 1239718.5947
124 | 2631335.0503 | 1239559.8154

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99011 | -0.18801 | 0.0018087 | 0.00045331
1 | 0.98952 | -0.19929 | 0.0026879 | 0.00067365
2 | 0.99063 | -0.17811 | 0.0018123 | 0.0004542
3 | 0.98884 | -0.21245 | 0.0022897 | 0.00057385
4 | 0.99047 | -0.18122 | 0.0017287 | 0.00043325
5 | 0.99214 | -0.1491 | 0 | 0
6 | 0.98848 | -0.21933 | 0 | 0
7 | 0.99044 | -0.18176 | 0.0018555 | 0.00046504
8 | 0.98738 | -0.24044 | 0.0014426 | 0.00036155
9 | 0.99031 | -0.18433 | 0.0016469 | 0.00041274
10 | 0.98671 | -0.2534 | 0.0019541 | 0.00048973
11 | 0.99018 | -0.18668 | 0.0023002 | 0.00057648
12 | 0.97906 | -0.4022 | 0.00069437 | 0.00017402
13 | 0.97882 | -0.40692 | 0.00096034 | 0.00024068
14 | 0.97921 | -0.39925 | 0 | 0
15 | 0.9788 | -0.40735 | 0.00072212 | 0.00018098
16 | 0.97971 | -0.38938 | 0.0025584 | 0.0006412
17 | 0.97916 | -0.40026 | 0.0011201 | 0.00028073
18 | 0.97835 | -0.41603 | 0 | 0
19 | 0.97984 | -0.3868 | 0 | 0
20 | 0.97909 | -0.40148 | 0.00093829 | 0.00023516
21 | 0.9783 | -0.41705 | 0.0029594 | 0.0007417
22 | 0.97809 | -0.42121 | 0 | 0
23 | 0.98002 | -0.38332 | 0 | 0
24 | 0.97908 | -0.40169 | 0.0021177 | 0.00053075
25 | 0.978 | -0.42294 | 0.003955 | 0.00099122
26 | 0.98206 | -0.3435 | 0.0017483 | 0.00043816
27 | 0.97958 | -0.39182 | 0.0027731 | 0.000695
28 | 0.97544 | -0.47271 | 0.00064742 | 0.00016226
29 | 0.97546 | -0.47228 | 0 | 0
30 | 0.9743 | -0.49516 | 0.011309 | 0.0028343
31 | 0.97612 | -0.45931 | 0.0020482 | 0.00051332
32 | 0.9733 | -0.51493 | 0.0043101 | 0.0010802
33 | 0.97657 | -0.45051 | 0.0013594 | 0.0003407
34 | 0.97239 | -0.5328 | 0 | 0
35 | 0.97754 | -0.4315 | 0.0083603 | 0.0020953
36 | 0.9721 | -0.5386 | 0.0035723 | 0.0008953
37 | 0.97196 | -0.54133 | 0.0013486 | 0.000338
38 | 0.97765 | -0.42938 | 0.0048335 | 0.0012114
39 | 0.97377 | -0.50574 | 0.0010707 | 0.00026835
40 | 0.9738 | -0.50524 | 0.0014737 | 0.00036935
41 | 0.97338 | -0.51346 | 0 | 0
42 | 0.97406 | -0.50006 | 0.00051805 | 0.00012983
43 | 0.97278 | -0.52524 | 0.001165 | 0.00029199
44 | 0.97448 | -0.49187 | 0.0010961 | 0.00027471
45 | 0.97269 | -0.5271 | 0.0010991 | 0.00027547
46 | 0.97488 | -0.48385 | 0.00088404 | 0.00022156
47 | 0.97232 | -0.53439 | 0.00072832 | 0.00018253
48 | 0.97539 | -0.47385 | 0.00066987 | 0.00016789
49 | 0.99928 | -0.013867 | 0.0027728 | 0.00069492
50 | 0.99934 | -0.012704 | 0 | 0
51 | 0.99949 | -0.0097415 | 0 | 0
52 | 0.99972 | -0.0054591 | 0 | 0
53 | 0.99946 | -0.010323 | 0.0011281 | 0.00028273
54 | 0.97188 | -0.54305 | 0.0008561 | 0.00021456
55 | 0.99946 | -0.010474 | 0.0009403 | 0.00023566
56 | 0.99977 | -0.0043369 | 0.0045829 | 0.0011486
57 | 1 | 0 | -0.27813 | -0.071046
58 | 0.99997 | -0.00053685 | 0.0023115 | 0.00057931
59 | 0.97545 | -0.47272 | 0.00067393 | 0.0001689
60 | 0.97665 | -0.44921 | 0.00095529 | 0.00023942
61 | 0.97725 | -0.4375 | 0.0010522 | 0.00026371
62 | 0.97834 | -0.41611 | 0.0010227 | 0.0002563
63 | 0.97875 | -0.40806 | 0.0025525 | 0.00063972
64 | 0.98351 | -0.31548 | 0.0024684 | 0.00061865
65 | 0.98356 | -0.31442 | 0.0027515 | 0.0006896
66 | 0.98376 | -0.31063 | 0 | 0
67 | 0.99449 | -0.10419 | 0.0015511 | 0.00038875
68 | 0.99444 | -0.10526 | 0.0015734 | 0.00039433
69 | 0.99809 | -0.035994 | 0.011883 | 0.0029782
70 | 0.99834 | -0.031313 | 0.0063193 | 0.0015838
71 | 0.98876 | -0.21374 | 0.0019625 | 0.00049184
72 | 0.98336 | -0.31833 | 0.0028805 | 0.00072193
73 | 0.98506 | -0.2853 | 0.0017459 | 0.00043756
74 | 0.98999 | -0.19035 | 0.0028974 | 0.00072616
75 | 0.98989 | -0.19234 | 0.0010622 | 0.00026622
76 | 0.98986 | -0.19303 | 0.0015308 | 0.00038365
77 | 0.9898 | -0.19422 | 0.0032153 | 0.00080584
78 | 0.98979 | -0.19442 | 0.0011234 | 0.00028155
79 | 0.97795 | -0.42389 | 0.0019282 | 0.00048325
80 | 0.9825 | -0.335 | 0 | 0
81 | 0.97876 | -0.40791 | 0.0025569 | 0.00064083
82 | 0.98213 | -0.34225 | 0.0023551 | 0.00059024
83 | 0.98285 | -0.32814 | 0.0023595 | 0.00059135
84 | 0.97164 | -0.54784 | 0.005906 | 0.0014802
85 | 0.97162 | -0.54825 | 0.0011466 | 0.00028738
86 | 0.97139 | -0.55274 | 0 | 0
87 | 0.97094 | -0.56162 | 0.0012712 | 0.0003186
88 | 0.98826 | -0.22341 | 0.0064653 | 0.0016204
89 | 0.98628 | -0.26155 | 0.0040047 | 0.0010037
90 | 0.9832 | -0.32111 | 0.011971 | 0.0030003
91 | 0.97151 | -0.55013 | 0.014561 | 0.0036493
92 | 0.97162 | -0.54803 | 0.0012426 | 0.00031142
93 | 0.98306 | -0.3238 | 0.0026852 | 0.00067298
94 | 0.98073 | -0.36916 | 0 | 0
95 | 0.98017 | -0.38023 | 0.0026588 | 0.00066636
96 | 0.97997 | -0.38408 | 0 | 0
97 | 0.97991 | -0.38517 | 0.0030188 | 0.00075658
98 | 0.98037 | -0.37632 | 0.0026163 | 0.00065571
99 | 0.97983 | -0.38686 | 0.002401 | 0.00060175
100 | 0.97977 | -0.38811 | 0.0058626 | 0.0014693
101 | 0.97846 | -0.4136 | 0.0016926 | 0.00042421
102 | 0.98023 | -0.37908 | 0.0024986 | 0.00062621
103 | 0.97978 | -0.38789 | 0.001682 | 0.00042156
104 | 0.97969 | -0.38958 | 0.0025168 | 0.00063078
105 | 0.98003 | -0.38305 | 0.0016643 | 0.00041711
106 | 0.98 | -0.38362 | 0.0024547 | 0.0006152
107 | 0.98666 | -0.25448 | 0.0021235 | 0.00053221
108 | 0.98539 | -0.27898 | 0.0015436 | 0.00038685
109 | 0.97041 | -0.57209 | 0 | 0
110 | 0.97019 | -0.57659 | 0.00091372 | 0.000229
111 | 0.97016 | -0.5772 | 0.0045855 | 0.0011492
112 | 0.97029 | -0.57446 | 0 | 0
113 | 0.97026 | -0.57518 | 0.0011571 | 0.00028999
114 | 0.97032 | -0.57385 | 0.001662 | 0.00041654
115 | 0.97032 | -0.57396 | 0.0010871 | 0.00027245
116 | 0.972 | -0.54059 | 0.0013324 | 0.00033394
117 | 0.9718 | -0.54448 | 0.0017348 | 0.00043479
118 | 0.97177 | -0.5451 | 0.0024498 | 0.00061397
119 | 0.97982 | -0.38711 | 0.0018527 | 0.00046432
120 | 0.97985 | -0.38657 | 0.0015972 | 0.0004003
121 | 0.97986 | -0.3863 | 0.0041821 | 0.0010481
122 | 0.98211 | -0.34265 | 0.0032187 | 0.00080667
123 | 0.98201 | -0.34461 | 0.0065146 | 0.0016327
124 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.09591 | 0.0244 | -0.095858 | -0.024367 | 5.2082e-05 | 3.2561e-05 | 0.14427 | 0.14427 | 0.14427 | 0.99011 | -0.18801 | 0.98952 | -0.19929 | 13.2116
1 | -0.097719 | -0.024853 | 0.097765 | 0.024882 | 4.6639e-05 | 2.9183e-05 | 0.14699 | 0.14699 | 0.14699 | 0.99011 | -0.18801 | 0.99063 | -0.17811 | 13.4605
2 | 0.09317 | 0.023694 | -0.093111 | -0.023657 | 5.9032e-05 | 3.6855e-05 | 0.14023 | 0.14023 | 0.14023 | 0.98952 | -0.19929 | 0.98884 | -0.21245 | 12.8415
3 | 0.017369 | 0.0043553 | -0.017367 | -0.0043538 | 2.57e-06 | 1.5152e-06 | 0.026091 | 0.026091 | 0.026091 | 0.99063 | -0.17811 | 0.99047 | -0.18122 | 7.1679
4 | -0.11695 | -0.029692 | 0.11711 | 0.029795 | 0.0001635 | 0.000103 | 0.1758 | 0.1758 | 0.1758 | 0.99063 | -0.17811 | 0.99214 | -0.1491 | 16.0991
5 | 0.090821 | 0.023083 | -0.090791 | -0.023064 | 3.0098e-05 | 1.8768e-05 | 0.13678 | 0.13678 | 0.13678 | 0.98884 | -0.21245 | 0.98848 | -0.21933 | 12.526
6 | 0.015638 | 0.0039205 | -0.015638 | -0.0039203 | 4.0535e-07 | 2.3422e-07 | 0.023494 | 0.023494 | 0.023494 | 0.99047 | -0.18122 | 0.99044 | -0.18176 | 6.4544
7 | 0.1245 | 0.031818 | -0.12411 | -0.03157 | 0.00038791 | 0.00024788 | 0.18695 | 0.18695 | 0.18695 | 0.99214 | -0.1491 | 0.98876 | -0.21374 | 51.3597
8 | -0.24161 | -0.061613 | 0.24213 | 0.06194 | 0.00051255 | 0.00032682 | 0.36275 | 0.36275 | 0.36275 | 0.99214 | -0.1491 | 0.99444 | -0.10526 | 33.2189
9 | 0.090791 | 0.023064 | -0.090699 | -0.023007 | 9.2169e-05 | 5.7474e-05 | 0.13678 | 0.13678 | 0.13678 | 0.98848 | -0.21933 | 0.98738 | -0.24044 | 12.5261
10 | 0.013782 | 0.0034552 | -0.01378 | -0.0034543 | 1.6855e-06 | 9.438e-07 | 0.020706 | 0.020706 | 0.020706 | 0.99044 | -0.18176 | 0.99031 | -0.18433 | 5.6886
11 | 0.089257 | 0.022645 | -0.089201 | -0.02261 | 5.5566e-05 | 3.4621e-05 | 0.13461 | 0.13461 | 0.13461 | 0.98738 | -0.24044 | 0.98671 | -0.2534 | 12.327
12 | 0.012134 | 0.0030415 | -0.012132 | -0.0030408 | 1.3622e-06 | 7.3122e-07 | 0.018232 | 0.018232 | 0.018232 | 0.99031 | -0.18433 | 0.99018 | -0.18668 | 5.0088
13 | 0.085123 | 0.021589 | -0.085019 | -0.021524 | 0.00010459 | 6.4995e-05 | 0.12846 | 0.12846 | 0.12846 | 0.98671 | -0.2534 | 0.98539 | -0.27898 | 11.764
14 | 0.0021237 | 0.00053192 | -0.0021235 | -0.00053221 | 1.0945e-07 | -2.9342e-07 | 0.0032025 | 0.0032026 | 0.0032026 | 0.98671 | -0.2534 | 0.98666 | -0.25448 | 0.87983
15 | 0.009832 | 0.0024643 | -0.0098303 | -0.0024635 | 1.7175e-06 | 8.2939e-07 | 0.014775 | 0.014775 | 0.014775 | 0.99018 | -0.18668 | 0.98999 | -0.19035 | 4.0592
16 | 0.010533 | 0.0026408 | -0.010531 | -0.0026396 | 2.3683e-06 | 1.2059e-06 | 0.01601 | 0.01601 | 0.01601 | 0.97906 | -0.4022 | 0.97882 | -0.40692 | 4.3982
17 | -0.011228 | -0.0028148 | 0.011229 | 0.0028156 | 1.581e-06 | 8.2973e-07 | 0.017065 | 0.017065 | 0.017065 | 0.97906 | -0.4022 | 0.97921 | -0.39925 | 4.6881
18 | 0.0095707 | 0.0023989 | -0.0095705 | -0.0023988 | 1.9551e-07 | 9.4171e-08 | 0.01455 | 0.01455 | 0.01455 | 0.97882 | -0.40692 | 0.9788 | -0.40735 | 3.9972
19 | -0.015406 | -0.003862 | 0.015413 | 0.0038662 | 7.2456e-06 | 4.1935e-06 | 0.023411 | 0.023411 | 0.023411 | 0.97921 | -0.39925 | 0.97971 | -0.38938 | 6.4317
20 | 0.0041765 | 0.0010464 | -0.0041763 | -0.0010464 | 2.0146e-07 | -3.8837e-08 | 0.0063466 | 0.0063466 | 0.0063466 | 0.97921 | -0.39925 | 0.97916 | -0.40026 | 1.7436
21 | 0.0088484 | 0.0022178 | -0.0088448 | -0.0022162 | 3.6567e-06 | 1.6633e-06 | 0.013452 | 0.013452 | 0.013452 | 0.9788 | -0.40735 | 0.97835 | -0.41603 | 3.6956
22 | -0.017972 | -0.0045074 | 0.017974 | 0.0045087 | 2.214e-06 | 1.3172e-06 | 0.027297 | 0.027297 | 0.027297 | 0.97971 | -0.38938 | 0.97984 | -0.3868 | 7.4992
23 | 0.0030562 | 0.00076569 | -0.003056 | -0.00076585 | 1.773e-07 | -1.622e-07 | 0.0046444 | 0.0046445 | 0.0046445 | 0.97916 | -0.40026 | 0.97909 | -0.40148 | 1.276
24 | 0.0029595 | 0.00074155 | -0.0029594 | -0.0007417 | 1.4495e-07 | -1.4678e-07 | 0.0045012 | 0.0045013 | 0.0045013 | 0.97835 | -0.41603 | 0.9783 | -0.41705 | 1.2366
25 | 0.0058852 | 0.0014746 | -0.0058838 | -0.0014743 | 1.4534e-06 | 3.2288e-07 | 0.0089509 | 0.0089512 | 0.0089512 | 0.97835 | -0.41603 | 0.97809 | -0.42121 | 2.4591
26 | -0.017974 | -0.0045087 | 0.017977 | 0.0045105 | 2.977e-06 | 1.771e-06 | 0.027297 | 0.027297 | 0.027297 | 0.97984 | -0.3868 | 0.98002 | -0.38332 | 7.4992
27 | 0.0021177 | 0.00053069 | -0.0021177 | -0.00053075 | 2.1021e-08 | -5.4605e-08 | 0.0032185 | 0.0032185 | 0.0032185 | 0.97909 | -0.40148 | 0.97908 | -0.40169 | 0.8842
28 | 0.0058838 | 0.0014743 | -0.0058833 | -0.0014742 | 4.8563e-07 | 1.0797e-07 | 0.0089512 | 0.0089512 | 0.0089512 | 0.97809 | -0.42121 | 0.978 | -0.42294 | 2.4591
29 | -0.057083 | -0.014393 | 0.057192 | 0.014463 | 0.00010904 | 6.9295e-05 | 0.086703 | 0.086703 | 0.086703 | 0.98002 | -0.38332 | 0.98206 | -0.3435 | 23.8195
30 | 0.039106 | 0.0098827 | -0.03909 | -0.0098727 | 1.5932e-05 | 1.0045e-05 | 0.059406 | 0.059406 | 0.059406 | 0.98002 | -0.38332 | 0.97958 | -0.39182 | 16.3204
31 | 0.0019283 | 0.00048297 | -0.0019282 | -0.00048325 | 8.7191e-08 | -2.8316e-07 | 0.0029337 | 0.0029339 | 0.0029339 | 0.978 | -0.42294 | 0.97795 | -0.42389 | 0.80601
32 | -0.05894 | -0.014901 | 0.058964 | 0.014916 | 2.4022e-05 | 1.4968e-05 | 0.089352 | 0.089352 | 0.089352 | 0.98206 | -0.3435 | 0.9825 | -0.335 | 12.2736
33 | 0.036317 | 0.0091777 | -0.036289 | -0.0091601 | 2.7978e-05 | 1.7598e-05 | 0.055194 | 0.055194 | 0.055194 | 0.97958 | -0.39182 | 0.97876 | -0.40791 | 15.1632
34 | -0.00064742 | -0.00016226 | 0.00064744 | 0.00016182 | 1.3108e-08 | -4.3901e-07 | 0.00098763 | 0.00098747 | 0.00098763 | 0.97544 | -0.47271 | 0.97546 | -0.47228 | 0.27133
35 | 0.041975 | 0.010561 | -0.041929 | -0.010532 | 4.5825e-05 | 2.8956e-05 | 0.064046 | 0.064046 | 0.064046 | 0.97546 | -0.47228 | 0.9743 | -0.49516 | 17.595
36 | -0.042622 | -0.010723 | 0.042649 | 0.01074 | 2.6434e-05 | 1.671e-05 | 0.065033 | 0.065033 | 0.065033 | 0.97546 | -0.47228 | 0.97612 | -0.45931 | 17.8662
37 | 0.03062 | 0.0076978 | -0.030591 | -0.0076797 | 2.8876e-05 | 1.8043e-05 | 0.046774 | 0.046774 | 0.046774 | 0.9743 | -0.49516 | 0.9733 | -0.51493 | 12.85
38 | -0.044697 | -0.011253 | 0.044716 | 0.011265 | 1.8815e-05 | 1.1907e-05 | 0.068155 | 0.068155 | 0.068155 | 0.97612 | -0.45931 | 0.97657 | -0.45051 | 18.724
39 | 0.026281 | 0.0065995 | -0.026259 | -0.0065857 | 2.2391e-05 | 1.3871e-05 | 0.040185 | 0.040185 | 0.040185 | 0.9733 | -0.51493 | 0.97239 | -0.5328 | 11.0398
40 | -0.046075 | -0.011606 | 0.046117 | 0.011632 | 4.1925e-05 | 2.6548e-05 | 0.070227 | 0.070226 | 0.070227 | 0.97657 | -0.45051 | 0.97754 | -0.4315 | 19.293
41 | 0.0090932 | 0.002279 | -0.0090907 | -0.0022778 | 2.5128e-06 | 1.179e-06 | 0.013915 | 0.013915 | 0.013915 | 0.97239 | -0.5328 | 0.9721 | -0.5386 | 3.8228
42 | 0.017166 | 0.0043067 | -0.017159 | -0.0043025 | 6.9778e-06 | 4.1314e-06 | 0.02627 | 0.02627 | 0.02627 | 0.97239 | -0.5328 | 0.97196 | -0.54133 | 7.217
43 | -0.054477 | -0.013727 | 0.054483 | 0.013731 | 5.5342e-06 | 3.515e-06 | 0.082952 | 0.082952 | 0.082952 | 0.97754 | -0.4315 | 0.97765 | -0.42938 | 22.7891
44 | 0.0055184 | 0.0013825 | -0.0055179 | -0.0013824 | 5.2261e-07 | 9.2352e-08 | 0.0084469 | 0.008447 | 0.008447 | 0.9721 | -0.5386 | 0.972 | -0.54059 | 2.3206
45 | 0.01581 | 0.0039645 | -0.015805 | -0.0039616 | 5.0455e-06 | 2.9446e-06 | 0.024205 | 0.024205 | 0.024205 | 0.97196 | -0.54133 | 0.97162 | -0.54803 | 6.6498
46 | -0.059317 | -0.014942 | 0.059361 | 0.014971 | 4.4795e-05 | 2.8485e-05 | 0.090309 | 0.090309 | 0.090309 | 0.97765 | -0.42938 | 0.97846 | -0.4136 | 24.8102
47 | -0.022702 | -0.0057062 | 0.022703 | 0.0057065 | 5.4451e-07 | 3.3348e-07 | 0.034697 | 0.034697 | 0.034697 | 0.97377 | -0.50574 | 0.9738 | -0.50524 | 9.5322
48 | 0.021632 | 0.0054378 | -0.021624 | -0.005433 | 7.9662e-06 | 4.8567e-06 | 0.033061 | 0.033061 | 0.033061 | 0.97377 | -0.50574 | 0.97338 | -0.51346 | 9.0828
49 | -0.024177 | -0.0060759 | 0.024183 | 0.0060796 | 5.9771e-06 | 3.6801e-06 | 0.036949 | 0.036949 | 0.036949 | 0.9738 | -0.50524 | 0.97406 | -0.50006 | 10.1509
50 | 0.021624 | 0.005433 | -0.021612 | -0.0054256 | 1.2151e-05 | 7.4084e-06 | 0.033061 | 0.033061 | 0.033061 | 0.97338 | -0.51346 | 0.97278 | -0.52524 | 9.0828
51 | -0.024701 | -0.0062094 | 0.02471 | 0.0062154 | 9.6627e-06 | 5.9588e-06 | 0.037741 | 0.037741 | 0.037741 | 0.97406 | -0.50006 | 0.97448 | -0.49187 | 10.3683
52 | 0.020446 | 0.0051336 | -0.020445 | -0.0051325 | 1.8209e-06 | 1.1038e-06 | 0.031279 | 0.031279 | 0.031279 | 0.97278 | -0.52524 | 0.97269 | -0.5271 | 8.5932
53 | -0.025806 | -0.0064901 | 0.025816 | 0.0064962 | 9.8912e-06 | 6.1187e-06 | 0.039414 | 0.039414 | 0.039414 | 0.97448 | -0.49187 | 0.97488 | -0.48385 | 10.8281
54 | 0.019346 | 0.004857 | -0.019339 | -0.004853 | 6.7271e-06 | 4.0513e-06 | 0.029598 | 0.029598 | 0.029598 | 0.97269 | -0.5271 | 0.97232 | -0.53439 | 8.1313
55 | -0.0267 | -0.0067177 | 0.026713 | 0.0067257 | 1.2766e-05 | 7.9146e-06 | 0.040764 | 0.040763 | 0.040764 | 0.97488 | -0.48385 | 0.97539 | -0.47385 | 11.1988
56 | 0.018611 | 0.0046704 | -0.018603 | -0.0046658 | 7.6812e-06 | 4.603e-06 | 0.028483 | 0.028483 | 0.028483 | 0.97232 | -0.53439 | 0.97188 | -0.54305 | 7.8251
57 | -0.027383 | -0.0068935 | 0.027384 | 0.0068945 | 1.4742e-06 | 9.154e-07 | 0.041785 | 0.041785 | 0.041785 | 0.97539 | -0.47385 | 0.97545 | -0.47272 | 11.4795
58 | -0.0027728 | -0.00069492 | 0.0027729 | 0.0006947 | 1.5353e-07 | -2.1639e-07 | 0.0041289 | 0.0041288 | 0.0041289 | 0.99928 | -0.013867 | 0.99934 | -0.012704 | 1.1343
59 | -0.0027729 | -0.0006947 | 0.0027733 | 0.00069415 | 3.9116e-07 | -5.5155e-07 | 0.0041288 | 0.0041285 | 0.0041288 | 0.99934 | -0.012704 | 0.99949 | -0.0097415 | 1.1343
60 | -0.0048418 | -0.0012123 | 0.0048428 | 0.0012122 | 9.8703e-07 | -3.2449e-08 | 0.0072079 | 0.0072076 | 0.0072079 | 0.99949 | -0.0097415 | 0.99972 | -0.0054591 | 1.9802
61 | 0.0020685 | 0.00051811 | -0.0020684 | -0.00051828 | 5.7237e-08 | -1.7431e-07 | 0.0030794 | 0.0030795 | 0.0030795 | 0.99949 | -0.0097415 | 0.99946 | -0.010323 | 0.84601
62 | -0.0048428 | -0.0012122 | 0.004843 | 0.0012122 | 2.5867e-07 | -8.56e-09 | 0.0072076 | 0.0072076 | 0.0072076 | 0.99972 | -0.0054591 | 0.99977 | -0.0043369 | 1.9801
63 | 0.00094031 | 0.00023555 | -0.0009403 | -0.00023566 | 6.766e-09 | -1.1632e-07 | 0.0013999 | 0.0013999 | 0.0013999 | 0.99946 | -0.010323 | 0.99946 | -0.010474 | 0.3846
64 | 0.017747 | 0.0044513 | -0.017743 | -0.0044489 | 4.0522e-06 | 2.4121e-06 | 0.027173 | 0.027173 | 0.027173 | 0.97188 | -0.54305 | 0.97164 | -0.54784 | 7.4651
65 | -0.0094259 | -0.0023608 | 0.0094278 | 0.0023617 | 1.9468e-06 | 8.9994e-07 | 0.014028 | 0.014028 | 0.014028 | 0.99977 | -0.0043369 | 1 | 0 | 3.854
66 | 0.26705 | 0.068684 | -0.26704 | -0.06868 | 6.9687e-06 | 4.4461e-06 | 0.398 | 0.398 | 0.398 | 1 | 0 | 0.99997 | -0.00053685 | 36.4468
67 | 0.26473 | 0.0681 | -0.26434 | -0.067848 | 0.00039545 | 0.00025229 | 0.39456 | 0.39456 | 0.39456 | 0.99997 | -0.00053685 | 0.99834 | -0.031313 | 36.1318
68 | -0.028058 | -0.0070634 | 0.02809 | 0.007083 | 3.157e-05 | 1.9631e-05 | 0.042813 | 0.042813 | 0.042813 | 0.97545 | -0.47272 | 0.97665 | -0.44921 | 11.7619
69 | -0.029045 | -0.0073224 | 0.029062 | 0.0073326 | 1.6289e-05 | 1.0148e-05 | 0.044269 | 0.044269 | 0.044269 | 0.97665 | -0.44921 | 0.97725 | -0.4375 | 12.1617
70 | -0.030114 | -0.0075963 | 0.030145 | 0.0076155 | 3.0872e-05 | 1.9267e-05 | 0.045871 | 0.045871 | 0.045871 | 0.97725 | -0.4375 | 0.97834 | -0.41611 | 12.6019
71 | -0.031167 | -0.0078718 | 0.031179 | 0.0078794 | 1.2036e-05 | 7.5238e-06 | 0.047426 | 0.047426 | 0.047426 | 0.97834 | -0.41611 | 0.97875 | -0.40806 | 13.0291
72 | -0.033732 | -0.0085191 | 0.033732 | 0.0085192 | 2.4053e-07 | 1.5088e-07 | 0.051307 | 0.051307 | 0.051307 | 0.97875 | -0.40806 | 0.97876 | -0.40791 | 14.0952
73 | -0.0024684 | -0.00061865 | 0.0024686 | 0.00061843 | 1.2478e-07 | -2.2291e-07 | 0.0037347 | 0.0037346 | 0.0037347 | 0.98351 | -0.31548 | 0.98356 | -0.31442 | 1.026
74 | -0.0052201 | -0.001308 | 0.005221 | 0.0013081 | 9.4237e-07 | 9.1623e-08 | 0.0078973 | 0.0078971 | 0.0078973 | 0.98356 | -0.31442 | 0.98376 | -0.31063 | 2.1696
75 | 0.076384 | 0.019314 | -0.076355 | -0.019297 | 2.8194e-05 | 1.7402e-05 | 0.1156 | 0.1156 | 0.1156 | 0.98376 | -0.31063 | 0.98336 | -0.31833 | 10.5859
76 | -0.081605 | -0.020622 | 0.081704 | 0.020684 | 9.9218e-05 | 6.1514e-05 | 0.1235 | 0.12349 | 0.1235 | 0.98376 | -0.31063 | 0.98506 | -0.2853 | 11.3091
77 | 0.24371 | 0.062342 | -0.2437 | -0.062334 | 1.261e-05 | 8.0409e-06 | 0.3651 | 0.3651 | 0.3651 | 0.99449 | -0.10419 | 0.99444 | -0.10526 | 33.4345
78 | -0.24526 | -0.062731 | 0.24608 | 0.063249 | 0.00081243 | 0.00051807 | 0.36743 | 0.36742 | 0.36743 | 0.99449 | -0.10419 | 0.99809 | -0.035994 | 33.647
79 | -0.25796 | -0.066227 | 0.25802 | 0.066264 | 5.8633e-05 | 3.7401e-05 | 0.38514 | 0.38514 | 0.38514 | 0.99809 | -0.035994 | 0.99834 | -0.031313 | 35.2693
80 | 0.12215 | 0.031078 | -0.1221 | -0.031042 | 5.6884e-05 | 3.6348e-05 | 0.184 | 0.184 | 0.184 | 0.98876 | -0.21374 | 0.98826 | -0.22341 | 50.5484
81 | 0.073475 | 0.018575 | -0.07344 | -0.018553 | 3.4545e-05 | 2.126e-05 | 0.11124 | 0.11124 | 0.11124 | 0.98336 | -0.31833 | 0.98285 | -0.32814 | 10.1868
82 | -0.08345 | -0.021121 | 0.083475 | 0.021137 | 2.5309e-05 | 1.5711e-05 | 0.12613 | 0.12613 | 0.12613 | 0.98506 | -0.2853 | 0.98539 | -0.27898 | 11.5505
83 | 0.0069328 | 0.0017373 | -0.0069322 | -0.0017371 | 6.5634e-07 | 2.1282e-07 | 0.01042 | 0.01042 | 0.01042 | 0.98999 | -0.19035 | 0.98989 | -0.19234 | 2.8628
84 | 0.00587 | 0.0014709 | -0.0058698 | -0.0014709 | 1.936e-07 | 3.8666e-08 | 0.0088237 | 0.0088237 | 0.0088237 | 0.98989 | -0.19234 | 0.98986 | -0.19303 | 2.4241
85 | 0.004339 | 0.0010872 | -0.0043387 | -0.0010873 | 2.4665e-07 | -4.0862e-08 | 0.0065226 | 0.0065226 | 0.0065226 | 0.98986 | -0.19303 | 0.9898 | -0.19422 | 1.7919
86 | 0.0011234 | 0.00028143 | -0.0011234 | -0.00028155 | 1.0463e-08 | -1.1903e-07 | 0.0016889 | 0.0016889 | 0.0016889 | 0.9898 | -0.19422 | 0.98979 | -0.19442 | 0.46398
87 | 0.012093 | 0.0030321 | -0.012089 | -0.0030299 | 4.1754e-06 | 2.2521e-06 | 0.018316 | 0.018316 | 0.018316 | 0.9825 | -0.335 | 0.98213 | -0.34225 | 5.0319
88 | -0.071057 | -0.017948 | 0.071081 | 0.017962 | 2.3385e-05 | 1.4353e-05 | 0.10767 | 0.10767 | 0.10767 | 0.9825 | -0.335 | 0.98285 | -0.32814 | 9.8597
89 | 0.0097341 | 0.0024397 | -0.0097339 | -0.0024396 | 1.8443e-07 | 8.9423e-08 | 0.014748 | 0.014748 | 0.014748 | 0.98213 | -0.34225 | 0.98211 | -0.34265 | 4.0517
90 | 0.011837 | 0.0029687 | -0.011836 | -0.0029686 | 2.2722e-07 | 1.2258e-07 | 0.018128 | 0.018128 | 0.018128 | 0.97164 | -0.54784 | 0.97162 | -0.54825 | 4.9803
91 | 0.01069 | 0.0026812 | -0.010688 | -0.00268 | 2.2871e-06 | 1.182e-06 | 0.016372 | 0.016372 | 0.016372 | 0.97162 | -0.54825 | 0.97139 | -0.55274 | 4.4978
92 | 0.010688 | 0.00268 | -0.010683 | -0.0026777 | 4.5238e-06 | 2.3383e-06 | 0.016372 | 0.016372 | 0.016372 | 0.97139 | -0.55274 | 0.97094 | -0.56162 | 4.4979
93 | 0.0094118 | 0.0023591 | -0.0094071 | -0.0023568 | 4.6915e-06 | 2.2593e-06 | 0.014424 | 0.014424 | 0.014424 | 0.97094 | -0.56162 | 0.97041 | -0.57209 | 3.9628
94 | 0.11563 | 0.029422 | -0.11542 | -0.029286 | 0.00021214 | 0.00013553 | 0.17426 | 0.17426 | 0.17426 | 0.98826 | -0.22341 | 0.98628 | -0.26155 | 47.874
95 | 0.11141 | 0.028282 | -0.11109 | -0.028079 | 0.00031828 | 0.00020332 | 0.16822 | 0.16822 | 0.16822 | 0.98628 | -0.26155 | 0.9832 | -0.32111 | 46.2142
96 | 0.099124 | 0.025079 | -0.099111 | -0.025071 | 1.2786e-05 | 8.1637e-06 | 0.1501 | 0.1501 | 0.1501 | 0.9832 | -0.32111 | 0.98306 | -0.3238 | 41.2368
97 | -0.014561 | -0.0036493 | 0.014562 | 0.0036502 | 1.4603e-06 | 8.3763e-07 | 0.022302 | 0.022302 | 0.022302 | 0.97151 | -0.55013 | 0.97162 | -0.54803 | 6.127
98 | 0.096426 | 0.024398 | -0.096216 | -0.024264 | 0.00020939 | 0.00013368 | 0.14604 | 0.14604 | 0.14604 | 0.98306 | -0.3238 | 0.98073 | -0.36916 | 40.1202
99 | 0.064205 | 0.016236 | -0.064156 | -0.016204 | 4.9261e-05 | 3.1353e-05 | 0.097467 | 0.097467 | 0.097467 | 0.98073 | -0.36916 | 0.97991 | -0.38517 | 26.7767
100 | 0.016877 | 0.004233 | -0.016871 | -0.0042296 | 5.7546e-06 | 3.3878e-06 | 0.025608 | 0.025608 | 0.025608 | 0.98073 | -0.36916 | 0.98037 | -0.37632 | 7.0351
101 | 0.015134 | 0.0037952 | -0.015126 | -0.0037906 | 7.9777e-06 | 4.5969e-06 | 0.022963 | 0.022963 | 0.022963 | 0.98073 | -0.36916 | 0.98017 | -0.38023 | 6.3085
102 | 0.012467 | 0.0031242 | -0.012465 | -0.003123 | 2.2896e-06 | 1.2505e-06 | 0.018927 | 0.018927 | 0.018927 | 0.98017 | -0.38023 | 0.97997 | -0.38408 | 5.1996
103 | 0.0066012 | 0.0016534 | -0.0066003 | -0.0016532 | 8.7423e-07 | 2.6718e-07 | 0.010023 | 0.010023 | 0.010023 | 0.97997 | -0.38408 | 0.97983 | -0.38686 | 2.7536
104 | 0.0058637 | 0.0014695 | -0.0058626 | -0.0014693 | 1.126e-06 | 2.4354e-07 | 0.0089036 | 0.0089038 | 0.0089038 | 0.97997 | -0.38408 | 0.97977 | -0.38811 | 2.4461
105 | 0.061137 | 0.015448 | -0.061054 | -0.015395 | 8.3203e-05 | 5.2926e-05 | 0.092883 | 0.092883 | 0.092883 | 0.97991 | -0.38517 | 0.97846 | -0.4136 | 25.5174
106 | 0.014255 | 0.0035739 | -0.014253 | -0.0035728 | 1.8781e-06 | 1.0671e-06 | 0.021637 | 0.021637 | 0.021637 | 0.98037 | -0.37632 | 0.98023 | -0.37908 | 5.9442
107 | 0.0016821 | 0.00042119 | -0.001682 | -0.00042156 | 8.1989e-08 | -3.6952e-07 | 0.0025544 | 0.0025546 | 0.0025546 | 0.97983 | -0.38686 | 0.97978 | -0.38789 | 0.70181
108 | 0.0025172 | 0.00063024 | -0.0025168 | -0.00063078 | 3.2618e-07 | -5.409e-07 | 0.0038225 | 0.0038227 | 0.0038227 | 0.97983 | -0.38686 | 0.97969 | -0.38958 | 1.0502
109 | 0.011755 | 0.0029466 | -0.011752 | -0.0029454 | 2.2204e-06 | 1.1867e-06 | 0.017844 | 0.017844 | 0.017844 | 0.98023 | -0.37908 | 0.98003 | -0.38305 | 4.9022
110 | 0.010088 | 0.0025283 | -0.010088 | -0.0025281 | 2.7775e-07 | 1.3798e-07 | 0.015317 | 0.015317 | 0.015317 | 0.98003 | -0.38305 | 0.98 | -0.38362 | 4.208
111 | 0.0076331 | 0.0019129 | -0.0076321 | -0.0019126 | 9.7347e-07 | 3.7956e-07 | 0.01159 | 0.01159 | 0.01159 | 0.98 | -0.38362 | 0.97986 | -0.3863 | 3.1841
112 | 0.0027494 | 0.00068865 | -0.0027491 | -0.00068893 | 2.3002e-07 | -2.7914e-07 | 0.0042157 | 0.0042158 | 0.0042158 | 0.97041 | -0.57209 | 0.97032 | -0.57385 | 1.1582
113 | 0.0066578 | 0.0016682 | -0.006657 | -0.0016679 | 7.5163e-07 | 2.4347e-07 | 0.010209 | 0.010209 | 0.010209 | 0.97041 | -0.57209 | 0.97029 | -0.57446 | 2.8046
114 | 0.0045856 | 0.0011492 | -0.0045855 | -0.0011492 | 1.3494e-07 | -3.4667e-09 | 0.0070332 | 0.0070332 | 0.0070332 | 0.97019 | -0.57659 | 0.97016 | -0.5772 | 1.9322
115 | -0.0054993 | -0.0013782 | 0.0054999 | 0.0013783 | 5.571e-07 | 9.8645e-08 | 0.0084346 | 0.0084345 | 0.0084346 | 0.97019 | -0.57659 | 0.97029 | -0.57446 | 2.3172
116 | 0.0011571 | 0.0002896 | -0.0011571 | -0.00028999 | 3.9984e-08 | -3.9265e-07 | 0.0017744 | 0.0017745 | 0.0017745 | 0.97029 | -0.57446 | 0.97026 | -0.57518 | 0.48751
117 | 0.0010871 | 0.00027238 | -0.0010871 | -0.00027245 | 5.921e-09 | -6.6387e-08 | 0.0016671 | 0.0016671 | 0.0016671 | 0.97032 | -0.57385 | 0.97032 | -0.57396 | 0.45799
118 | 0.0041854 | 0.0010485 | -0.0041847 | -0.0010486 | 7.7475e-07 | -1.2778e-07 | 0.0064073 | 0.0064075 | 0.0064075 | 0.972 | -0.54059 | 0.9718 | -0.54448 | 1.7603
119 | 0.0024498 | 0.00061385 | -0.0024498 | -0.00061397 | 7.2727e-08 | -1.2421e-07 | 0.0037511 | 0.0037512 | 0.0037512 | 0.9718 | -0.54448 | 0.97177 | -0.5451 | 1.0305
120 | -0.0018527 | -0.00046432 | 0.0018527 | 0.00046415 | 4.73e-08 | -1.7042e-07 | 0.0028136 | 0.0028135 | 0.0028136 | 0.97982 | -0.38711 | 0.97985 | -0.38657 | 0.77296
121 | -0.0034499 | -0.00086444 | 0.0034499 | 0.00086442 | 4.4885e-08 | -2.6203e-08 | 0.005239 | 0.005239 | 0.005239 | 0.97985 | -0.38657 | 0.97986 | -0.3863 | 1.4393
122 | 0.0065152 | 0.0016329 | -0.0065146 | -0.0016327 | 6.1012e-07 | 1.7922e-07 | 0.0098714 | 0.0098714 | 0.0098714 | 0.98211 | -0.34265 | 0.98201 | -0.34461 | 2.7119

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28444 | 0.072629

## res_load
| p_mw | q_mvar
0 | 0.0018087 | 0.00045331
1 | 0.0026879 | 0.00067365
2 | 0.0018123 | 0.0004542
3 | 0.0022897 | 0.00057385
4 | 0.0017287 | 0.00043325
5 | 0.0018555 | 0.00046504
6 | 0.0014426 | 0.00036155
7 | 0.0016469 | 0.00041274
8 | 0.0019541 | 0.00048973
9 | 0.0023002 | 0.00057648
10 | 0.00069437 | 0.00017402
11 | 0.00096034 | 0.00024068
12 | 0.00072212 | 0.00018098
13 | 0.0025584 | 0.0006412
14 | 0.0011201 | 0.00028073
15 | 0.00093829 | 0.00023516
16 | 0.0029594 | 0.0007417
17 | 0.0021177 | 0.00053075
18 | 0.003955 | 0.00099122
19 | 0.0017483 | 0.00043816
20 | 0.0027731 | 0.000695
21 | 0.00064742 | 0.00016226
22 | 0.011309 | 0.0028343
23 | 0.0020482 | 0.00051332
24 | 0.0043101 | 0.0010802
25 | 0.0013594 | 0.0003407
26 | 0.0083603 | 0.0020953
27 | 0.0035723 | 0.0008953
28 | 0.0013486 | 0.000338
29 | 0.0048335 | 0.0012114
30 | 0.0010707 | 0.00026835
31 | 0.0014737 | 0.00036935
32 | 0.00051805 | 0.00012983
33 | 0.001165 | 0.00029199
34 | 0.0010961 | 0.00027471
35 | 0.0010991 | 0.00027547
36 | 0.00088404 | 0.00022156
37 | 0.00072832 | 0.00018253
38 | 0.00066987 | 0.00016789
39 | 0.0027728 | 0.00069492
40 | 0.0011281 | 0.00028273
41 | 0.0008561 | 0.00021456
42 | 0.0009403 | 0.00023566
43 | 0.0045829 | 0.0011486
44 | 0.0063142 | 0.0015825
45 | 0.0023115 | 0.00057931
46 | 0.00067393 | 0.0001689
47 | 0.00095529 | 0.00023942
48 | 0.0010522 | 0.00026371
49 | 0.0010227 | 0.0002563
50 | 0.0025525 | 0.00063972
51 | 0.0024684 | 0.00061865
52 | 0.0027515 | 0.0006896
53 | 0.0015511 | 0.00038875
54 | 0.0015734 | 0.00039433
55 | 0.011883 | 0.0029782
56 | 0.0063193 | 0.0015838
57 | 0.0019625 | 0.00049184
58 | 0.0028805 | 0.00072193
59 | 0.0017459 | 0.00043756
60 | 0.0028974 | 0.00072616
61 | 0.0010622 | 0.00026622
62 | 0.0015308 | 0.00038365
63 | 0.0032153 | 0.00080584
64 | 0.0011234 | 0.00028155
65 | 0.0019282 | 0.00048325
66 | 0.0025569 | 0.00064083
67 | 0.0023551 | 0.00059024
68 | 0.0023595 | 0.00059135
69 | 0.005906 | 0.0014802
70 | 0.0011466 | 0.00028738
71 | 0.0012712 | 0.0003186
72 | 0.0064653 | 0.0016204
73 | 0.0040047 | 0.0010037
74 | 0.011971 | 0.0030003
75 | 0.014561 | 0.0036493
76 | 0.0012426 | 0.00031142
77 | 0.0026852 | 0.00067298
78 | 0.0026588 | 0.00066636
79 | 0.0030188 | 0.00075658
80 | 0.0026163 | 0.00065571
81 | 0.002401 | 0.00060175
82 | 0.0058626 | 0.0014693
83 | 0.0016926 | 0.00042421
84 | 0.0024986 | 0.00062621
85 | 0.001682 | 0.00042156
86 | 0.0025168 | 0.00063078
87 | 0.0016643 | 0.00041711
88 | 0.0024547 | 0.0006152
89 | 0.0021235 | 0.00053221
90 | 0.0015436 | 0.00038685
91 | 0.00091372 | 0.000229
92 | 0.0045855 | 0.0011492
93 | 0.0011571 | 0.00028999
94 | 0.001662 | 0.00041654
95 | 0.0010871 | 0.00027245
96 | 0.0013324 | 0.00033394
97 | 0.0017348 | 0.00043479
98 | 0.0024498 | 0.00061397
99 | 0.0018527 | 0.00046432
100 | 0.0015972 | 0.0004003
101 | 0.0041821 | 0.0010481
102 | 0.0032187 | 0.00080667
103 | 0.0065146 | 0.0016327

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1