## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2768-2_1_5_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_2768-2_1_5_node_126 | 0.4 | n |  | TRUE
2 | bus_LV_2768-2_1_5_node_190 | 0.4 | n |  | TRUE
3 | bus_LV_2768-2_1_5_node_135 | 0.4 | n |  | TRUE
4 | bus_LV_2768-2_1_5_node_129 | 0.4 | n |  | TRUE
5 | bus_LV_2768-2_1_5_node_127 | 0.4 | n |  | TRUE
6 | bus_LV_2768-2_1_5_node_150 | 0.4 | n |  | TRUE
7 | bus_LV_2768-2_1_5_node_2 | 0.4 | n |  | TRUE
8 | bus_LV_2768-2_1_5_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_2768-2_1_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2768-2_1_5_node_130 | 0.4 | n |  | TRUE
11 | bus_LV_2768-2_1_5_node_170 | 0.4 | n |  | TRUE
12 | bus_LV_2768-2_1_5_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_2768-2_1_5_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_2768-2_1_5_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_2768-2_1_5_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2768-2_1_5_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2768-2_1_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2768-2_1_5_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2768-2_1_5_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2768-2_1_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2768-2_1_5_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2768-2_1_5_node_182 | 0.4 | n |  | TRUE
23 | bus_LV_2768-2_1_5_node_34 | 0.4 | n |  | TRUE
24 | bus_LV_2768-2_1_5_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2768-2_1_5_node_143 | 0.4 | n |  | TRUE
26 | bus_LV_2768-2_1_5_node_134 | 0.4 | n |  | TRUE
27 | bus_LV_2768-2_1_5_node_144 | 0.4 | n |  | TRUE
28 | bus_LV_2768-2_1_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_2768-2_1_5_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_2768-2_1_5_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_2768-2_1_5_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_2768-2_1_5_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_2768-2_1_5_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_2768-2_1_5_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_2768-2_1_5_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_2768-2_1_5_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_2768-2_1_5_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_2768-2_1_5_node_187 | 0.4 | n |  | TRUE
39 | bus_LV_2768-2_1_5_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_2768-2_1_5_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_2768-2_1_5_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_2768-2_1_5_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_2768-2_1_5_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_2768-2_1_5_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_2768-2_1_5_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_2768-2_1_5_node_158 | 0.4 | n |  | TRUE
47 | bus_LV_2768-2_1_5_node_133 | 0.4 | n |  | TRUE
48 | bus_LV_2768-2_1_5_node_131 | 0.4 | n |  | TRUE
49 | bus_LV_2768-2_1_5_node_132 | 0.4 | n |  | TRUE
50 | bus_LV_2768-2_1_5_node_159 | 0.4 | n |  | TRUE
51 | bus_LV_2768-2_1_5_node_148 | 0.4 | n |  | TRUE
52 | bus_LV_2768-2_1_5_node_167 | 0.4 | n |  | TRUE
53 | bus_LV_2768-2_1_5_node_168 | 0.4 | n |  | TRUE
54 | bus_LV_2768-2_1_5_node_169 | 0.4 | n |  | TRUE
55 | bus_LV_2768-2_1_5_node_171 | 0.4 | n |  | TRUE
56 | bus_LV_2768-2_1_5_node_175 | 0.4 | n |  | TRUE
57 | bus_LV_2768-2_1_5_node_172 | 0.4 | n |  | TRUE
58 | bus_LV_2768-2_1_5_node_173 | 0.4 | n |  | TRUE
59 | bus_LV_2768-2_1_5_node_174 | 0.4 | n |  | TRUE
60 | bus_LV_2768-2_1_5_node_149 | 0.4 | n |  | TRUE
61 | bus_LV_2768-2_1_5_node_177 | 0.4 | n |  | TRUE
62 | bus_LV_2768-2_1_5_node_179 | 0.4 | n |  | TRUE
63 | bus_LV_2768-2_1_5_node_181 | 0.4 | n |  | TRUE
64 | bus_LV_2768-2_1_5_node_180 | 0.4 | n |  | TRUE
65 | bus_LV_2768-2_1_5_node_186 | 0.4 | n |  | TRUE
66 | bus_LV_2768-2_1_5_node_152 | 0.4 | n |  | TRUE
67 | bus_LV_2768-2_1_5_node_185 | 0.4 | n |  | TRUE
68 | bus_LV_2768-2_1_5_node_146 | 0.4 | n |  | TRUE
69 | bus_LV_2768-2_1_5_node_147 | 0.4 | n |  | TRUE
70 | bus_LV_2768-2_1_5_node_151 | 0.4 | n |  | TRUE
71 | bus_LV_2768-2_1_5_node_125 | 0.4 | n |  | TRUE
72 | bus_MV_399_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2768-2_1_5_load_126 | 1 | 0.00091682 | 0.00022978 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2768-2_1_5_load_190 | 2 | 0.0017408 | 0.00043629 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2768-2_1_5_load_135 | 3 | 0.0028941 | 0.00072534 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2768-2_1_5_load_129 | 4 | 0.0012639 | 0.00031677 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2768-2_1_5_load_150 | 6 | 0.0015761 | 0.00039501 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2768-2_1_5_load_130 | 10 | 0.0010474 | 0.00026251 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2768-2_1_5_load_170 | 11 | 0.0010764 | 0.00026977 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2768-2_1_5_load_12 | 12 | 0.0092222 | 0.0023113 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2768-2_1_5_load_15 | 13 | 0.015762 | 0.0039503 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2768-2_1_5_load_6 | 14 | 0.017801 | 0.0044614 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2768-2_1_5_load_7 | 15 | 0.028559 | 0.0071575 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2768-2_1_5_load_10 | 18 | 0.021032 | 0.0052711 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2768-2_1_5_load_182 | 22 | 0.0040927 | 0.0010257 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2768-2_1_5_load_34 | 23 | 0.0067529 | 0.0016924 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2768-2_1_5_load_16 | 24 | 0.0010725 | 0.0002688 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2768-2_1_5_load_143 | 25 | 0.007089 | 0.0017767 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2768-2_1_5_load_134 | 26 | 0.0060545 | 0.0015174 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2768-2_1_5_load_144 | 27 | 0.0051337 | 0.0012866 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2768-2_1_5_load_19 | 28 | 0.0048438 | 0.001214 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2768-2_1_5_load_20 | 29 | 0.0036218 | 0.00090771 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2768-2_1_5_load_21 | 30 | 0.0049055 | 0.0012294 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2768-2_1_5_load_33 | 31 | 0.0066677 | 0.0016711 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2768-2_1_5_load_23 | 32 | 0.001819 | 0.00045589 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2768-2_1_5_load_24 | 33 | 0.0031341 | 0.00078547 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2768-2_1_5_load_27 | 35 | 0.039898 | 0.0099994 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2768-2_1_5_load_28 | 36 | 0.011657 | 0.0029216 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2768-2_1_5_load_35 | 37 | 0.0037989 | 0.00095209 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2768-2_1_5_load_29 | 39 | 0.0063739 | 0.0015975 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2768-2_1_5_load_32 | 42 | 0.0012256 | 0.00030715 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2768-2_1_5_load_38 | 43 | 0.0022203 | 0.00055645 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2768-2_1_5_load_36 | 44 | 0.001835 | 0.0004599 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2768-2_1_5_load_158 | 46 | 0.003353 | 0.00084035 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2768-2_1_5_load_133 | 47 | 0.0022975 | 0.00057581 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2768-2_1_5_load_131 | 48 | 0.001862 | 0.00046667 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2768-2_1_5_load_132 | 49 | 0.0056334 | 0.0014119 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2768-2_1_5_load_159 | 50 | 0.0029269 | 0.00073355 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2768-2_1_5_load_167 | 52 | 0.0012347 | 0.00030943 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2768-2_1_5_load_168 | 53 | 0.0011736 | 0.00029412 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2768-2_1_5_load_169 | 54 | 0.001524 | 0.00038194 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2768-2_1_5_load_175 | 56 | 0.0019592 | 0.00049102 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2768-2_1_5_load_172 | 57 | 0.0027096 | 0.00067909 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2768-2_1_5_load_149 | 60 | 0.0027989 | 0.00070148 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2768-2_1_5_load_177 | 61 | 0.0014164 | 0.00035498 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2768-2_1_5_load_181 | 63 | 0.0012726 | 0.00031894 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2768-2_1_5_load_180 | 64 | 0.0026842 | 0.00067272 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2768-2_1_5_load_186 | 65 | 0.0027058 | 0.00067813 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2768-2_1_5_load_185 | 67 | 0.017553 | 0.0043993 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2768-2_1_5_load_146 | 68 | 0.0018469 | 0.00046289 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2768-2_1_5_load_151 | 70 | 0.0025993 | 0.00065143 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2768-2_1_5_load_125 | 71 | 0.0040294 | 0.0010099 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 67 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2768-2_1_5_line_0 |  | 0 | 1 | 0.0059623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2768-2_1_5_line_1 |  | 0 | 2 | 0.032426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2768-2_1_5_line_2 |  | 0 | 3 | 0.0097777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2768-2_1_5_line_3 |  | 1 | 71 | 0.013786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2768-2_1_5_line_4 |  | 3 | 47 | 0.010123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2768-2_1_5_line_5 |  | 4 | 5 | 0.015834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2768-2_1_5_line_6 |  | 4 | 6 | 0.018738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2768-2_1_5_line_7 |  | 5 | 10 | 0.0015436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2768-2_1_5_line_8 |  | 5 | 71 | 0.023237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2768-2_1_5_line_9 |  | 6 | 70 | 0.010046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2768-2_1_5_line_10 |  | 7 | 8 | 0.002008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2768-2_1_5_line_11 |  | 7 | 9 | 0.053821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2768-2_1_5_line_12 |  | 8 | 12 | 0.023596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2768-2_1_5_line_13 |  | 9 | 13 | 0.0042916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2768-2_1_5_line_14 |  | 10 | 11 | 0.0097542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_2768-2_1_5_line_15 |  | 11 | 53 | 0.019718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2768-2_1_5_line_16 |  | 12 | 20 | 0.020583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2768-2_1_5_line_17 |  | 13 | 24 | 0.014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2768-2_1_5_line_18 |  | 14 | 15 | 0.016426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_2768-2_1_5_line_19 |  | 14 | 16 | 0.01737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_2768-2_1_5_line_20 |  | 15 | 17 | 0.060145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2768-2_1_5_line_21 |  | 16 | 18 | 0.0069152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2768-2_1_5_line_22 |  | 17 | 19 | 0.009258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_2768-2_1_5_line_23 |  | 18 | 20 | 0.027699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2768-2_1_5_line_24 |  | 19 | 23 | 0.0083957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_2768-2_1_5_line_25 |  | 20 | 21 | 0.021205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2768-2_1_5_line_26 |  | 21 | 22 | 0.021192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2768-2_1_5_line_27 |  | 22 | 62 | 0.019067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2768-2_1_5_line_28 |  | 23 | 32 | 0.011516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2768-2_1_5_line_29 |  | 25 | 26 | 0.017457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2768-2_1_5_line_30 |  | 25 | 27 | 0.0050396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2768-2_1_5_line_31 |  | 26 | 49 | 0.015212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2768-2_1_5_line_32 |  | 28 | 29 | 0.022697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2768-2_1_5_line_33 |  | 28 | 30 | 0.0066429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2768-2_1_5_line_34 |  | 29 | 31 | 0.082019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2768-2_1_5_line_35 |  | 30 | 32 | 0.010781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2768-2_1_5_line_36 |  | 31 | 41 | 0.026527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2768-2_1_5_line_37 |  | 33 | 34 | 0.024364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2768-2_1_5_line_38 |  | 34 | 35 | 0.036871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2768-2_1_5_line_39 |  | 34 | 36 | 0.038874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2768-2_1_5_line_40 |  | 35 | 37 | 0.0040293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2768-2_1_5_line_41 |  | 36 | 38 | 0.018677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_2768-2_1_5_line_42 |  | 37 | 44 | 0.018315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2768-2_1_5_line_43 |  | 38 | 67 | 0.013115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2768-2_1_5_line_44 |  | 39 | 40 | 0.004273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2768-2_1_5_line_45 |  | 39 | 41 | 0.016915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2768-2_1_5_line_46 |  | 40 | 42 | 0.027612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2768-2_1_5_line_47 |  | 42 | 43 | 0.0068274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2768-2_1_5_line_48 |  | 44 | 45 | 0.0040938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_2768-2_1_5_line_49 |  | 45 | 46 | 0.016171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2768-2_1_5_line_50 |  | 46 | 50 | 0.034425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_2768-2_1_5_line_51 |  | 47 | 48 | 0.0045556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2768-2_1_5_line_52 |  | 48 | 49 | 0.020315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2768-2_1_5_line_53 |  | 50 | 51 | 0.013756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2768-2_1_5_line_54 |  | 51 | 69 | 0.031693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_2768-2_1_5_line_55 |  | 52 | 53 | 0.015546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_2768-2_1_5_line_56 |  | 52 | 54 | 0.0076706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_2768-2_1_5_line_57 |  | 54 | 55 | 0.023929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2768-2_1_5_line_58 |  | 55 | 56 | 0.036434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_2768-2_1_5_line_59 |  | 56 | 59 | 0.017175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_2768-2_1_5_line_60 |  | 57 | 58 | 0.014091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_2768-2_1_5_line_61 |  | 57 | 59 | 0.019905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_2768-2_1_5_line_62 |  | 58 | 60 | 0.01585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_2768-2_1_5_line_63 |  | 60 | 69 | 0.02887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_2768-2_1_5_line_64 |  | 61 | 62 | 0.024584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2768-2_1_5_line_65 |  | 62 | 63 | 0.016621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_2768-2_1_5_line_66 |  | 63 | 66 | 0.013703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_2768-2_1_5_line_67 |  | 64 | 65 | 0.019086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2768-2_1_5_line_68 |  | 65 | 67 | 0.022879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2768-2_1_5_line_69 |  | 66 | 70 | 0.0033113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2768-2_1_5_line_70 |  | 68 | 69 | 0.030764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2768-2_1_5_trafo_185 | 0.63 MVA 20/0.4 kV | 72 | 67 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2608294.8333 | 1259074.724 | 2608292.9435 | 1259069.0691
1 | 2608262.5532 | 1259078.6819 | 2608294.8333 | 1259074.724
2 | 2608294.8333 | 1259074.724 | 2608297.9316 | 1259083.9979
3 | 2608292.9435 | 1259069.0691 | 2608288.574 | 1259055.9943
4 | 2608297.9316 | 1259083.9979 | 2608301.1393 | 1259093.599
5 | 2608281.2098 | 1259033.9554 | 2608296.8112 | 1259031.2517
6 | 2608315.2741 | 1259028.052 | 2608296.8112 | 1259031.2517
7 | 2608281.2098 | 1259033.9554 | 2608279.6853 | 1259034.1977
8 | 2608281.2098 | 1259033.9554 | 2608282.2831 | 1259037.1702 | 2608288.574 | 1259055.9943
9 | 2608315.2741 | 1259028.052 | 2608325.1723 | 1259026.3366
10 | 2608462.683 | 1259004.0122 | 2608464.6658 | 1259003.6592
11 | 2608518.109 | 1258996.0746 | 2608464.6658 | 1259003.6592
12 | 2608462.683 | 1259004.0122 | 2608453.2966 | 1259005.7111 | 2608439.4613 | 1259008.198
13 | 2608518.109 | 1258996.0746 | 2608522.3549 | 1258995.4505
14 | 2608270.052 | 1259035.7288 | 2608279.6853 | 1259034.1977
15 | 2608270.052 | 1259035.7288 | 2608250.5788 | 1259038.8237
16 | 2608419.204 | 1259011.8448 | 2608438.4442 | 1259008.3808 | 2608439.4613 | 1259008.198
17 | 2608536.2062 | 1258993.4142 | 2608522.3549 | 1258995.4505
18 | 2608435.1248 | 1259054.7677 | 2608438.597 | 1259070.823
19 | 2608431.4532 | 1259037.7907 | 2608435.1248 | 1259054.7677
20 | 2608484.2864 | 1259087.8326 | 2608466.0241 | 1259082.1473 | 2608462.3616 | 1259065.82 | 2608438.597 | 1259070.823
21 | 2608431.4532 | 1259037.7907 | 2608424.6453 | 1259039.0041
22 | 2608486.3764 | 1259096.8528 | 2608484.2864 | 1259087.8326
23 | 2608419.204 | 1259011.8448 | 2608424.6453 | 1259039.0041
24 | 2608486.3764 | 1259096.8528 | 2608488.4354 | 1259104.9921
25 | 2608398.275 | 1259015.6179 | 2608419.204 | 1259011.8448
26 | 2608398.275 | 1259015.6179 | 2608391.9423 | 1259016.6207 | 2608377.3452 | 1259018.9404
27 | 2608358.5143 | 1259021.9329 | 2608377.3452 | 1259018.9404
28 | 2608491.2596 | 1259116.1567 | 2608488.4354 | 1259104.9921
29 | 2608319.3722 | 1259148.1736 | 2608313.8404 | 1259131.6159
30 | 2608319.3722 | 1259148.1736 | 2608320.9692 | 1259152.9536
31 | 2608313.8404 | 1259131.6159 | 2608309.0201 | 1259117.1877
32 | 2608500.4 | 1259155.2224 | 2608495.2469 | 1259133.118
33 | 2608493.7387 | 1259126.6486 | 2608495.2469 | 1259133.118
34 | 2608500.4 | 1259155.2224 | 2608581.2737 | 1259141.5631
35 | 2608493.7387 | 1259126.6486 | 2608491.6829 | 1259117.83 | 2608491.2596 | 1259116.1567
36 | 2608581.2737 | 1259141.5631 | 2608607.4795 | 1259136.9756
37 | 2608395.0861 | 1259176.6107 | 2608400.4881 | 1259200.3677
38 | 2608395.0861 | 1259176.6107 | 2608358.9187 | 1259183.7801
39 | 2608395.0861 | 1259176.6107 | 2608386.4132 | 1259138.7163
40 | 2608354.9663 | 1259184.5636 | 2608358.9187 | 1259183.7801
41 | 2608382.2464 | 1259120.5104 | 2608386.4132 | 1259138.7163
42 | 2608354.9663 | 1259184.5636 | 2608337.0013 | 1259188.1247
43 | 2608382.2464 | 1259120.5104 | 2608379.1768 | 1259107.76
44 | 2608602.6554 | 1259116.3436 | 2608603.6282 | 1259120.5044
45 | 2608607.4795 | 1259136.9756 | 2608603.6282 | 1259120.5044
46 | 2608602.6554 | 1259116.3436 | 2608600.2507 | 1259106.0777 | 2608596.3606 | 1259089.4584
47 | 2608594.8045 | 1259082.8107 | 2608596.3606 | 1259089.4584
48 | 2608332.9856 | 1259188.9208 | 2608337.0013 | 1259188.1247
49 | 2608332.9856 | 1259188.9208 | 2608316.9844 | 1259191.2581
50 | 2608282.9207 | 1259196.2339 | 2608316.9844 | 1259191.2581
51 | 2608301.1393 | 1259093.599 | 2608302.5828 | 1259097.9199
52 | 2608302.5828 | 1259097.9199 | 2608309.0201 | 1259117.1877
53 | 2608269.3266 | 1259194.7027 | 2608280.9613 | 1259196.5201 | 2608282.9207 | 1259196.2339
54 | 2608269.3266 | 1259194.7027 | 2608253.9968 | 1259166.9406
55 | 2608235.2257 | 1259041.2638 | 2608250.5788 | 1259038.8237
56 | 2608227.6502 | 1259042.4678 | 2608235.2257 | 1259041.2638
57 | 2608204.0183 | 1259046.2237 | 2608227.6502 | 1259042.4678
58 | 2608204.0183 | 1259046.2237 | 2608204.7504 | 1259051.028 | 2608209.4892 | 1259082.2445
59 | 2608216.4366 | 1259097.7644 | 2608210.0463 | 1259085.9143 | 2608209.4892 | 1259082.2445
60 | 2608232.5777 | 1259127.6846 | 2608225.8874 | 1259115.283
61 | 2608216.4366 | 1259097.7644 | 2608225.8874 | 1259115.283
62 | 2608232.5777 | 1259127.6846 | 2608240.1059 | 1259141.6325
63 | 2608253.9968 | 1259166.9406 | 2608243.8621 | 1259148.592 | 2608240.1059 | 1259141.6325
64 | 2608358.5143 | 1259021.9329 | 2608352.96 | 1258997.9847
65 | 2608358.5143 | 1259021.9329 | 2608342.0274 | 1259024.0367
66 | 2608328.435 | 1259025.7712 | 2608342.0274 | 1259024.0367
67 | 2608369.3544 | 1259066.9602 | 2608373.8217 | 1259085.5162
68 | 2608373.8217 | 1259085.5162 | 2608379.1768 | 1259107.76
69 | 2608328.435 | 1259025.7712 | 2608325.1723 | 1259026.3366
70 | 2608253.9968 | 1259166.9406 | 2608284.3918 | 1259162.1911

## bus_geodata
| x | y | coords
0 | 2608294.8333 | 1259074.724
1 | 2608292.9435 | 1259069.0691
2 | 2608262.5532 | 1259078.6819
3 | 2608297.9316 | 1259083.9979
4 | 2608296.8112 | 1259031.2517
5 | 2608281.2098 | 1259033.9554
6 | 2608315.2741 | 1259028.052
7 | 2608464.6658 | 1259003.6592
8 | 2608462.683 | 1259004.0122
9 | 2608518.109 | 1258996.0746
10 | 2608279.6853 | 1259034.1977
11 | 2608270.052 | 1259035.7288
12 | 2608439.4613 | 1259008.198
13 | 2608522.3549 | 1258995.4505
14 | 2608435.1248 | 1259054.7677
15 | 2608438.597 | 1259070.823
16 | 2608431.4532 | 1259037.7907
17 | 2608484.2864 | 1259087.8326
18 | 2608424.6453 | 1259039.0041
19 | 2608486.3764 | 1259096.8528
20 | 2608419.204 | 1259011.8448
21 | 2608398.275 | 1259015.6179
22 | 2608377.3452 | 1259018.9404
23 | 2608488.4354 | 1259104.9921
24 | 2608536.2062 | 1258993.4142
25 | 2608319.3722 | 1259148.1736
26 | 2608313.8404 | 1259131.6159
27 | 2608320.9692 | 1259152.9536
28 | 2608495.2469 | 1259133.118
29 | 2608500.4 | 1259155.2224
30 | 2608493.7387 | 1259126.6486
31 | 2608581.2737 | 1259141.5631
32 | 2608491.2596 | 1259116.1567
33 | 2608400.4881 | 1259200.3677
34 | 2608395.0861 | 1259176.6107
35 | 2608358.9187 | 1259183.7801
36 | 2608386.4132 | 1259138.7163
37 | 2608354.9663 | 1259184.5636
38 | 2608382.2464 | 1259120.5104
39 | 2608603.6282 | 1259120.5044
40 | 2608602.6554 | 1259116.3436
41 | 2608607.4795 | 1259136.9756
42 | 2608596.3606 | 1259089.4584
43 | 2608594.8045 | 1259082.8107
44 | 2608337.0013 | 1259188.1247
45 | 2608332.9856 | 1259188.9208
46 | 2608316.9844 | 1259191.2581
47 | 2608301.1393 | 1259093.599
48 | 2608302.5828 | 1259097.9199
49 | 2608309.0201 | 1259117.1877
50 | 2608282.9207 | 1259196.2339
51 | 2608269.3266 | 1259194.7027
52 | 2608235.2257 | 1259041.2638
53 | 2608250.5788 | 1259038.8237
54 | 2608227.6502 | 1259042.4678
55 | 2608204.0183 | 1259046.2237
56 | 2608209.4892 | 1259082.2445
57 | 2608225.8874 | 1259115.283
58 | 2608232.5777 | 1259127.6846
59 | 2608216.4366 | 1259097.7644
60 | 2608240.1059 | 1259141.6325
61 | 2608352.96 | 1258997.9847
62 | 2608358.5143 | 1259021.9329
63 | 2608342.0274 | 1259024.0367
64 | 2608369.3544 | 1259066.9602
65 | 2608373.8217 | 1259085.5162
66 | 2608328.435 | 1259025.7712
67 | 2608379.1768 | 1259107.76
68 | 2608284.3918 | 1259162.1911
69 | 2608253.9968 | 1259166.9406
70 | 2608325.1723 | 1259026.3367
71 | 2608288.574 | 1259055.9943
72 | 2608382.2464 | 1259120.5104

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1