## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_301-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_301-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_301-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_301-9_0_4_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_301-9_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_301-9_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_301-9_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_301-9_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_301-9_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_301-9_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_301-9_0_4_node_70 | 0.4 | n |  | TRUE
11 | bus_LV_301-9_0_4_node_57 | 0.4 | n |  | TRUE
12 | bus_LV_301-9_0_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_301-9_0_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_301-9_0_4_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_301-9_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_301-9_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_301-9_0_4_node_44 | 0.4 | n |  | TRUE
18 | bus_LV_301-9_0_4_node_87 | 0.4 | n |  | TRUE
19 | bus_LV_301-9_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_301-9_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_301-9_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_301-9_0_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_301-9_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_301-9_0_4_node_177 | 0.4 | n |  | TRUE
25 | bus_LV_301-9_0_4_node_176 | 0.4 | n |  | TRUE
26 | bus_LV_301-9_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_301-9_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_301-9_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_301-9_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_301-9_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_301-9_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_301-9_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_301-9_0_4_node_65 | 0.4 | n |  | TRUE
34 | bus_LV_301-9_0_4_node_47 | 0.4 | n |  | TRUE
35 | bus_LV_301-9_0_4_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_301-9_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_301-9_0_4_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_301-9_0_4_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_301-9_0_4_node_53 | 0.4 | n |  | TRUE
40 | bus_LV_301-9_0_4_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_301-9_0_4_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_301-9_0_4_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_301-9_0_4_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_301-9_0_4_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_301-9_0_4_node_62 | 0.4 | n |  | TRUE
46 | bus_LV_301-9_0_4_node_85 | 0.4 | n |  | TRUE
47 | bus_LV_301-9_0_4_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_301-9_0_4_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_301-9_0_4_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_301-9_0_4_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_301-9_0_4_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_301-9_0_4_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_301-9_0_4_node_64 | 0.4 | n |  | TRUE
54 | bus_LV_301-9_0_4_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_301-9_0_4_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_301-9_0_4_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_301-9_0_4_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_301-9_0_4_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_301-9_0_4_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_301-9_0_4_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_301-9_0_4_node_66 | 0.4 | n |  | TRUE
62 | bus_LV_301-9_0_4_node_86 | 0.4 | n |  | TRUE
63 | bus_LV_301-9_0_4_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_301-9_0_4_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_301-9_0_4_node_58 | 0.4 | n |  | TRUE
66 | bus_LV_301-9_0_4_node_60 | 0.4 | n |  | TRUE
67 | bus_LV_301-9_0_4_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_301-9_0_4_node_68 | 0.4 | n |  | TRUE
69 | bus_LV_301-9_0_4_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_301-9_0_4_node_84 | 0.4 | n |  | TRUE
71 | bus_LV_301-9_0_4_node_69 | 0.4 | n |  | TRUE
72 | bus_LV_301-9_0_4_node_71 | 0.4 | n |  | TRUE
73 | bus_LV_301-9_0_4_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_301-9_0_4_node_73 | 0.4 | n |  | TRUE
75 | bus_LV_301-9_0_4_node_75 | 0.4 | n |  | TRUE
76 | bus_LV_301-9_0_4_node_76 | 0.4 | n |  | TRUE
77 | bus_MV_403_0_node_27 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_301-9_0_4_load_0 | 0 | 0.0018863 | 0.00047275 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_301-9_0_4_load_2 | 2 | 0.00078925 | 0.0001978 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_301-9_0_4_load_8 | 5 | 0.0012239 | 0.00030673 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_301-9_0_4_load_5 | 6 | 0.0084341 | 0.0021138 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_301-9_0_4_load_6 | 7 | 0.0048354 | 0.0012119 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_301-9_0_4_load_9 | 8 | 0.0011037 | 0.00027662 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_301-9_0_4_load_10 | 9 | 0.0024735 | 0.00061991 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_301-9_0_4_load_70 | 10 | 0.0010171 | 0.0002549 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_301-9_0_4_load_57 | 11 | 0.0028623 | 0.00071737 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_301-9_0_4_load_11 | 12 | 0.036511 | 0.0091506 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_301-9_0_4_load_13 | 14 | 0.073352 | 0.018384 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_301-9_0_4_load_14 | 16 | 0.0083949 | 0.002104 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_301-9_0_4_load_44 | 17 | 0.0032702 | 0.00081959 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_301-9_0_4_load_87 | 18 | 0.010105 | 0.0025327 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_301-9_0_4_load_16 | 19 | 0.0018772 | 0.00047048 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_301-9_0_4_load_17 | 20 | 0.00039316 | 9.8535e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_301-9_0_4_load_19 | 22 | 0.00048691 | 0.00012203 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_301-9_0_4_load_177 | 24 | 0.0027807 | 0.00069691 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_301-9_0_4_load_176 | 25 | 0.0038059 | 0.00095384 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_301-9_0_4_load_23 | 26 | 0.0024962 | 0.00062562 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_301-9_0_4_load_24 | 27 | 0.003042 | 0.0007624 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_301-9_0_4_load_27 | 30 | 0.0029146 | 0.00073046 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_301-9_0_4_load_28 | 31 | 0.0032234 | 0.00080785 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_301-9_0_4_load_32 | 32 | 0.0041352 | 0.0010364 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_301-9_0_4_load_65 | 33 | 0.0028169 | 0.00070598 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_301-9_0_4_load_47 | 34 | 0.0037874 | 0.00094922 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_301-9_0_4_load_29 | 35 | 0.0029378 | 0.00073628 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_301-9_0_4_load_30 | 36 | 0.0031185 | 0.00078157 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_301-9_0_4_load_31 | 37 | 0.002984 | 0.00074786 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_301-9_0_4_load_33 | 38 | 0.0070018 | 0.0017548 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_301-9_0_4_load_34 | 40 | 0.0021401 | 0.00053635 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_301-9_0_4_load_35 | 41 | 0.0042816 | 0.0010731 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_301-9_0_4_load_36 | 42 | 0.0019007 | 0.00047635 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_301-9_0_4_load_37 | 43 | 0.0019598 | 0.00049118 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_301-9_0_4_load_38 | 44 | 0.0034763 | 0.00087125 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_301-9_0_4_load_62 | 45 | 0.0031679 | 0.00079394 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_301-9_0_4_load_85 | 46 | 0.0031218 | 0.00078241 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_301-9_0_4_load_39 | 47 | 0.0076281 | 0.0019118 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_301-9_0_4_load_40 | 48 | 0.001888 | 0.00047317 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_301-9_0_4_load_43 | 51 | 0.0052981 | 0.0013278 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_301-9_0_4_load_48 | 52 | 0.092171 | 0.0231 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_301-9_0_4_load_64 | 53 | 0.0047205 | 0.0011831 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_301-9_0_4_load_45 | 54 | 0.0028379 | 0.00071126 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_301-9_0_4_load_46 | 55 | 0.0036191 | 0.00090702 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_301-9_0_4_load_49 | 56 | 0.0056585 | 0.0014182 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_301-9_0_4_load_50 | 57 | 0.0061973 | 0.0015532 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_301-9_0_4_load_52 | 59 | 0.0015548 | 0.00038966 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_301-9_0_4_load_54 | 60 | 0.0060005 | 0.0015039 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_301-9_0_4_load_66 | 61 | 0.0039268 | 0.00098414 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_301-9_0_4_load_86 | 62 | 0.0031007 | 0.00077712 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_301-9_0_4_load_59 | 63 | 0.004681 | 0.0011732 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_301-9_0_4_load_58 | 65 | 0.0014743 | 0.0003695 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_301-9_0_4_load_60 | 66 | 0.0043213 | 0.001083 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_301-9_0_4_load_61 | 67 | 0.0014956 | 0.00037482 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_301-9_0_4_load_68 | 68 | 0.0027549 | 0.00069044 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_301-9_0_4_load_67 | 69 | 0.0025149 | 0.00063029 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_301-9_0_4_load_84 | 70 | 0.0042744 | 0.0010713 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_301-9_0_4_load_69 | 71 | 0.0044835 | 0.0011237 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_301-9_0_4_load_71 | 72 | 0.004508 | 0.0011298 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_301-9_0_4_load_72 | 73 | 0.0005216 | 0.00013073 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_301-9_0_4_load_75 | 75 | 0.00035218 | 8.8266e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_301-9_0_4_load_76 | 76 | 0.0083547 | 0.0020939 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_301-9_0_4_line_0 |  | 0 | 1 | 0.014314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_301-9_0_4_line_1 |  | 1 | 2 | 0.012118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_301-9_0_4_line_2 |  | 2 | 3 | 0.018723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_301-9_0_4_line_3 |  | 3 | 8 | 0.015267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_301-9_0_4_line_4 |  | 3 | 9 | 0.038737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_301-9_0_4_line_5 |  | 3 | 7 | 0.038259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_301-9_0_4_line_6 |  | 4 | 5 | 0.017019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_301-9_0_4_line_7 |  | 4 | 6 | 0.0092425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_301-9_0_4_line_8 |  | 5 | 10 | 0.026381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_301-9_0_4_line_9 |  | 6 | 7 | 0.017481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_301-9_0_4_line_10 |  | 8 | 11 | 0.020666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_301-9_0_4_line_11 |  | 10 | 71 | 0.014473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_301-9_0_4_line_12 |  | 11 | 65 | 0.0054147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_301-9_0_4_line_13 |  | 12 | 13 | 0.061712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_301-9_0_4_line_14 |  | 12 | 14 | 0.00225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_301-9_0_4_line_15 |  | 13 | 15 | 0.00428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_301-9_0_4_line_16 |  | 15 | 18 | 0.014874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_301-9_0_4_line_17 |  | 16 | 17 | 0.01345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_301-9_0_4_line_18 |  | 17 | 30 | 0.012018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_301-9_0_4_line_19 |  | 18 | 64 | 0.022492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_301-9_0_4_line_20 |  | 19 | 20 | 0.036872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_301-9_0_4_line_21 |  | 19 | 21 | 0.0047531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_301-9_0_4_line_22 |  | 20 | 22 | 0.0187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_301-9_0_4_line_23 |  | 21 | 23 | 0.059151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_301-9_0_4_line_24 |  | 23 | 24 | 0.010517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_301-9_0_4_line_25 |  | 23 | 25 | 0.035436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_301-9_0_4_line_26 |  | 24 | 75 | 0.074457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_301-9_0_4_line_27 |  | 26 | 27 | 0.0072277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_301-9_0_4_line_28 |  | 26 | 28 | 0.035167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_301-9_0_4_line_29 |  | 27 | 29 | 0.01321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_301-9_0_4_line_30 |  | 28 | 30 | 0.0099539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_301-9_0_4_line_31 |  | 28 | 31 | 0.01934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_301-9_0_4_line_32 |  | 29 | 32 | 0.014596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_301-9_0_4_line_33 |  | 29 | 33 | 0.011277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_301-9_0_4_line_34 |  | 31 | 34 | 0.0011998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_301-9_0_4_line_35 |  | 32 | 36 | 0.018002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_301-9_0_4_line_36 |  | 33 | 68 | 0.023519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_301-9_0_4_line_37 |  | 34 | 54 | 0.020852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_301-9_0_4_line_38 |  | 35 | 36 | 0.0083141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_301-9_0_4_line_39 |  | 35 | 37 | 0.018798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_301-9_0_4_line_40 |  | 37 | 38 | 0.011523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_301-9_0_4_line_41 |  | 38 | 39 | 0.021167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_301-9_0_4_line_42 |  | 39 | 62 | 0.020395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_301-9_0_4_line_43 |  | 40 | 41 | 0.014968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_301-9_0_4_line_44 |  | 40 | 42 | 0.0056628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_301-9_0_4_line_45 |  | 41 | 43 | 0.0058346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_301-9_0_4_line_46 |  | 42 | 44 | 0.0076726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_301-9_0_4_line_47 |  | 43 | 45 | 0.018318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_301-9_0_4_line_48 |  | 44 | 46 | 0.015387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_301-9_0_4_line_49 |  | 45 | 67 | 0.0049771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_301-9_0_4_line_50 |  | 46 | 50 | 0.018263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_301-9_0_4_line_51 |  | 47 | 48 | 0.019365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_301-9_0_4_line_52 |  | 47 | 49 | 0.023792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_301-9_0_4_line_53 |  | 48 | 50 | 0.053679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_301-9_0_4_line_54 |  | 49 | 51 | 0.037292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_301-9_0_4_line_55 |  | 50 | 52 | 0.0086779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_301-9_0_4_line_56 |  | 51 | 53 | 0.02004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_301-9_0_4_line_57 |  | 52 | 55 | 0.011857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_301-9_0_4_line_58 |  | 54 | 55 | 0.008072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_301-9_0_4_line_59 |  | 56 | 57 | 0.027086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_301-9_0_4_line_60 |  | 56 | 58 | 0.013941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_301-9_0_4_line_61 |  | 57 | 59 | 0.017124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_301-9_0_4_line_62 |  | 58 | 60 | 0.02367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_301-9_0_4_line_63 |  | 59 | 61 | 0.014504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_301-9_0_4_line_64 |  | 60 | 63 | 0.012038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_301-9_0_4_line_65 |  | 61 | 69 | 0.016266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_301-9_0_4_line_66 |  | 62 | 64 | 0.004733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_301-9_0_4_line_67 |  | 63 | 65 | 0.01194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_301-9_0_4_line_68 |  | 66 | 67 | 0.033629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_301-9_0_4_line_69 |  | 68 | 71 | 0.01032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_301-9_0_4_line_70 |  | 69 | 70 | 0.019189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_301-9_0_4_line_71 |  | 70 | 76 | 0.02649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_301-9_0_4_line_72 |  | 72 | 73 | 0.0016967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_301-9_0_4_line_73 |  | 72 | 74 | 0.016846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_301-9_0_4_line_74 |  | 74 | 75 | 0.015151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_301-9_0_4_line_75 |  | 74 | 76 | 0.0035331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_301-9_0_4_trafo_27 | 0.63 MVA 20/0.4 kV | 77 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2587599.8602 | 1210644.5681 | 2587599.219 | 1210630.2688
1 | 2587599.8602 | 1210644.5681 | 2587601.925 | 1210656.5092
2 | 2587605.828 | 1210674.817 | 2587602.5909 | 1210660.3601 | 2587601.925 | 1210656.5092
3 | 2587605.828 | 1210674.817 | 2587608.8151 | 1210689.7886
4 | 2587605.828 | 1210674.817 | 2587596.4626 | 1210676.8377 | 2587567.7933 | 1210682.1444
5 | 2587605.828 | 1210674.817 | 2587613.586 | 1210670.8986 | 2587617.9641 | 1210667.7766 | 2587637.0756 | 1210652.9461
6 | 2587658.0824 | 1210636.431 | 2587668.0606 | 1210650.2186
7 | 2587658.0824 | 1210636.431 | 2587652.8859 | 1210640.6775 | 2587650.8859 | 1210642.2295
8 | 2587668.0606 | 1210650.2186 | 2587683.5272 | 1210671.59
9 | 2587650.8859 | 1210642.2295 | 2587637.0756 | 1210652.9461
10 | 2587613.2345 | 1210709.9746 | 2587610.0517 | 1210695.9866 | 2587608.8151 | 1210689.7886
11 | 2587692.0125 | 1210683.3147 | 2587683.5272 | 1210671.59
12 | 2587614.4358 | 1210715.2544 | 2587613.2345 | 1210709.9746
13 | 2587711.4229 | 1210820.8228 | 2587719.3824 | 1210822.5517 | 2587750.0651 | 1210829.2142 | 2587769.6992 | 1210839.5087
14 | 2587771.6919 | 1210840.5536 | 2587769.6992 | 1210839.5087
15 | 2587708.6333 | 1210824.0749 | 2587711.4229 | 1210820.8228
16 | 2587708.6333 | 1210824.0749 | 2587696.5068 | 1210815.4616
17 | 2587733.041 | 1210792.9709 | 2587741.288 | 1210782.3458
18 | 2587741.288 | 1210782.3458 | 2587748.6567 | 1210772.8523
19 | 2587678.1701 | 1210802.4372 | 2587696.5068 | 1210815.4616
20 | 2587759.1152 | 1210989.4102 | 2587722.362 | 1210986.4503
21 | 2587717.6243 | 1210986.0687 | 2587722.362 | 1210986.4503
22 | 2587759.1152 | 1210989.4102 | 2587768.9007 | 1210990.1983 | 2587777.6505 | 1210991.7283
23 | 2587663.9968 | 1210991.4498 | 2587688.3972 | 1210995.6792 | 2587697.2195 | 1210984.877 | 2587717.6243 | 1210986.0687
24 | 2587663.9968 | 1210991.4498 | 2587660.4233 | 1210981.5587
25 | 2587663.9968 | 1210991.4498 | 2587677.2662 | 1211024.308
26 | 2587660.4233 | 1210981.5587 | 2587655.9338 | 1210969.1319 | 2587643.284 | 1210937.3072 | 2587639.6986 | 1210926.9533 | 2587636.7487 | 1210915.2419 | 2587635.786 | 1210911.3974
27 | 2587726.581 | 1210730.2841 | 2587731.0229 | 1210735.9858
28 | 2587752.6348 | 1210763.7279 | 2587731.0229 | 1210735.9858
29 | 2587718.4628 | 1210719.8631 | 2587726.581 | 1210730.2841
30 | 2587752.6348 | 1210763.7279 | 2587748.6567 | 1210772.8523 | 2587748.6567 | 1210772.8523
31 | 2587752.6348 | 1210763.7279 | 2587766.7269 | 1210750.4816
32 | 2587718.4628 | 1210719.8631 | 2587706.9954 | 1210728.894
33 | 2587718.4628 | 1210719.8631 | 2587711.8515 | 1210710.7278
34 | 2587766.7269 | 1210750.4816 | 2587767.6011 | 1210749.6598
35 | 2587692.8525 | 1210740.0318 | 2587706.9954 | 1210728.894
36 | 2587698.0629 | 1210691.675 | 2587711.8515 | 1210710.7278
37 | 2587782.7945 | 1210735.3782 | 2587767.6011 | 1210749.6598
38 | 2587692.8525 | 1210740.0318 | 2587689.5884 | 1210742.6023 | 2587686.8745 | 1210745.7544
39 | 2587674.9543 | 1210760.2544 | 2587676.4512 | 1210757.8604 | 2587686.8745 | 1210745.7544
40 | 2587674.9543 | 1210760.2544 | 2587668.8453 | 1210770.0244
41 | 2587657.6231 | 1210787.9719 | 2587668.8453 | 1210770.0244
42 | 2587657.6231 | 1210787.9719 | 2587674.3 | 1210799.7126
43 | 2587763.6405 | 1210668.4734 | 2587773.3042 | 1210679.904
44 | 2587776.9601 | 1210684.2284 | 2587773.3042 | 1210679.904
45 | 2587759.8735 | 1210664.0177 | 2587763.6405 | 1210668.4734
46 | 2587776.9601 | 1210684.2284 | 2587781.9137 | 1210690.0877
47 | 2587748.194 | 1210649.9106 | 2587750.6279 | 1210653.0816 | 2587759.8735 | 1210664.0177
48 | 2587781.9137 | 1210690.0877 | 2587791.8481 | 1210701.8385
49 | 2587745.1636 | 1210645.9624 | 2587748.194 | 1210649.9106
50 | 2587803.6387 | 1210715.7849 | 2587791.8481 | 1210701.8385
51 | 2587841.028 | 1210666.0846 | 2587826.7159 | 1210679.1297
52 | 2587858.6117 | 1210650.0577 | 2587841.028 | 1210666.0846
53 | 2587803.6387 | 1210715.7849 | 2587825.3161 | 1210699.787 | 2587822.5554 | 1210695.0233 | 2587817.7446 | 1210687.3067 | 2587826.7159 | 1210679.1297
54 | 2587858.6117 | 1210650.0577 | 2587849.1532 | 1210640.0826 | 2587832.957 | 1210622.9921
55 | 2587803.6387 | 1210715.7849 | 2587797.3157 | 1210721.7285
56 | 2587819.1723 | 1210608.4461 | 2587832.957 | 1210622.9921
57 | 2587788.6761 | 1210729.8496 | 2587797.3157 | 1210721.7285
58 | 2587782.7945 | 1210735.3782 | 2587788.6761 | 1210729.8496
59 | 2587619.1206 | 1210773.997 | 2587618.2091 | 1210784.9747 | 2587617.7068 | 1210801.0375
60 | 2587625.0071 | 1210761.7142 | 2587620.3093 | 1210768.2054 | 2587619.2542 | 1210772.3877 | 2587619.1206 | 1210773.997
61 | 2587618.0473 | 1210818.1346 | 2587617.4327 | 1210809.8012 | 2587617.7068 | 1210801.0375
62 | 2587625.0071 | 1210761.7142 | 2587619.7556 | 1210738.6343
63 | 2587619.1141 | 1210832.5993 | 2587618.0473 | 1210818.1346
64 | 2587617.0848 | 1210726.8965 | 2587619.7556 | 1210738.6343
65 | 2587619.1141 | 1210832.5993 | 2587621.1801 | 1210848.734
66 | 2587678.1701 | 1210802.4372 | 2587674.3 | 1210799.7126
67 | 2587614.4358 | 1210715.2544 | 2587617.0848 | 1210726.8965
68 | 2587745.1636 | 1210645.9624 | 2587737.6441 | 1210636.1657 | 2587726.5577 | 1210618.0022
69 | 2587692.0125 | 1210683.3147 | 2587698.0629 | 1210691.675
70 | 2587624.8787 | 1210867.5623 | 2587621.2076 | 1210848.9485 | 2587621.1801 | 1210848.734
71 | 2587624.8787 | 1210867.5623 | 2587631.114 | 1210893.3077
72 | 2587613.9096 | 1210901.0416 | 2587615.5628 | 1210900.6594
73 | 2587631.9457 | 1210896.7416 | 2587627.7079 | 1210897.851 | 2587615.5628 | 1210900.6594
74 | 2587631.9457 | 1210896.7416 | 2587634.1971 | 1210905.0526 | 2587635.786 | 1210911.3974
75 | 2587631.9457 | 1210896.7416 | 2587631.114 | 1210893.3077

## bus_geodata
| x | y | coords
0 | 2587599.219 | 1210630.2688
1 | 2587599.8602 | 1210644.5681
2 | 2587601.925 | 1210656.5092
3 | 2587605.828 | 1210674.817
4 | 2587658.0824 | 1210636.431
5 | 2587668.0606 | 1210650.2185
6 | 2587650.8859 | 1210642.2295
7 | 2587637.0756 | 1210652.9461
8 | 2587608.8151 | 1210689.7886
9 | 2587567.7933 | 1210682.1444
10 | 2587683.5272 | 1210671.59
11 | 2587613.2345 | 1210709.9746
12 | 2587769.6992 | 1210839.5087
13 | 2587711.4229 | 1210820.8228
14 | 2587771.6919 | 1210840.5536
15 | 2587708.6333 | 1210824.0749
16 | 2587733.041 | 1210792.9709
17 | 2587741.288 | 1210782.3458
18 | 2587696.5068 | 1210815.4616
19 | 2587722.362 | 1210986.4503
20 | 2587759.1152 | 1210989.4102
21 | 2587717.6243 | 1210986.0687
22 | 2587777.6505 | 1210991.7283
23 | 2587663.9968 | 1210991.4498
24 | 2587660.4233 | 1210981.5587
25 | 2587677.2662 | 1211024.308
26 | 2587731.0229 | 1210735.9858
27 | 2587726.581 | 1210730.2841
28 | 2587752.6348 | 1210763.7279
29 | 2587718.4628 | 1210719.8631
30 | 2587748.6567 | 1210772.8523
31 | 2587766.7269 | 1210750.4816
32 | 2587706.9954 | 1210728.894
33 | 2587711.8515 | 1210710.7278
34 | 2587767.6011 | 1210749.6598
35 | 2587686.8745 | 1210745.7544
36 | 2587692.8525 | 1210740.0318
37 | 2587674.9543 | 1210760.2544
38 | 2587668.8453 | 1210770.0244
39 | 2587657.6231 | 1210787.9719
40 | 2587773.3042 | 1210679.904
41 | 2587763.6405 | 1210668.4734
42 | 2587776.9601 | 1210684.2284
43 | 2587759.8735 | 1210664.0177
44 | 2587781.9137 | 1210690.0877
45 | 2587748.194 | 1210649.9106
46 | 2587791.8481 | 1210701.8385
47 | 2587841.028 | 1210666.0846
48 | 2587826.7159 | 1210679.1297
49 | 2587858.6117 | 1210650.0577
50 | 2587803.6387 | 1210715.7849
51 | 2587832.957 | 1210622.9921
52 | 2587797.3157 | 1210721.7285
53 | 2587819.1723 | 1210608.4461
54 | 2587782.7945 | 1210735.3782
55 | 2587788.6761 | 1210729.8496
56 | 2587619.1206 | 1210773.997
57 | 2587617.7068 | 1210801.0375
58 | 2587625.0071 | 1210761.7142
59 | 2587618.0473 | 1210818.1346
60 | 2587619.7556 | 1210738.6343
61 | 2587619.1141 | 1210832.5993
62 | 2587674.3 | 1210799.7126
63 | 2587617.0848 | 1210726.8965
64 | 2587678.1701 | 1210802.4372
65 | 2587614.4358 | 1210715.2544
66 | 2587726.5577 | 1210618.0022
67 | 2587745.1636 | 1210645.9624
68 | 2587698.0629 | 1210691.675
69 | 2587621.1801 | 1210848.734
70 | 2587624.8787 | 1210867.5623
71 | 2587692.0125 | 1210683.3147
72 | 2587615.5628 | 1210900.6594
73 | 2587613.9096 | 1210901.0416
74 | 2587631.9457 | 1210896.7416
75 | 2587635.786 | 1210911.3974
76 | 2587631.114 | 1210893.3077
77 | 2587752.6348 | 1210763.7279

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1