## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_307-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_307-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_307-1_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_307-1_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_307-1_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_307-1_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_307-1_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_307-1_0_2_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_307-1_0_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_307-1_0_2_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_307-1_0_2_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_307-1_0_2_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_307-1_0_2_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_307-1_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_307-1_0_2_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_307-1_0_2_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_307-1_0_2_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_307-1_0_2_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_307-1_0_2_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_307-1_0_2_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_307-1_0_2_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_307-1_0_2_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_307-1_0_2_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_307-1_0_2_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_307-1_0_2_node_153 | 0.4 | n |  | TRUE
25 | bus_LV_307-1_0_2_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_307-1_0_2_node_40 | 0.4 | n |  | TRUE
27 | bus_LV_307-1_0_2_node_152 | 0.4 | n |  | TRUE
28 | bus_LV_307-1_0_2_node_155 | 0.4 | n |  | TRUE
29 | bus_LV_307-1_0_2_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_307-1_0_2_node_45 | 0.4 | n |  | TRUE
31 | bus_LV_307-1_0_2_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_307-1_0_2_node_76 | 0.4 | n |  | TRUE
33 | bus_LV_307-1_0_2_node_77 | 0.4 | n |  | TRUE
34 | bus_LV_307-1_0_2_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_307-1_0_2_node_90 | 0.4 | n |  | TRUE
36 | bus_LV_307-1_0_2_node_99 | 0.4 | n |  | TRUE
37 | bus_LV_307-1_0_2_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_307-1_0_2_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_307-1_0_2_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_307-1_0_2_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_307-1_0_2_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_307-1_0_2_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_307-1_0_2_node_94 | 0.4 | n |  | TRUE
44 | bus_LV_307-1_0_2_node_95 | 0.4 | n |  | TRUE
45 | bus_LV_307-1_0_2_node_92 | 0.4 | n |  | TRUE
46 | bus_LV_307-1_0_2_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_307-1_0_2_node_31 | 0.4 | n |  | TRUE
48 | bus_LV_307-1_0_2_node_32 | 0.4 | n |  | TRUE
49 | bus_LV_307-1_0_2_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_307-1_0_2_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_307-1_0_2_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_307-1_0_2_node_69 | 0.4 | n |  | TRUE
53 | bus_LV_307-1_0_2_node_67 | 0.4 | n |  | TRUE
54 | bus_LV_307-1_0_2_node_107 | 0.4 | n |  | TRUE
55 | bus_LV_307-1_0_2_node_108 | 0.4 | n |  | TRUE
56 | bus_LV_307-1_0_2_node_106 | 0.4 | n |  | TRUE
57 | bus_LV_307-1_0_2_node_72 | 0.4 | n |  | TRUE
58 | bus_LV_307-1_0_2_node_73 | 0.4 | n |  | TRUE
59 | bus_LV_307-1_0_2_node_68 | 0.4 | n |  | TRUE
60 | bus_LV_307-1_0_2_node_60 | 0.4 | n |  | TRUE
61 | bus_LV_307-1_0_2_node_61 | 0.4 | n |  | TRUE
62 | bus_LV_307-1_0_2_node_62 | 0.4 | n |  | TRUE
63 | bus_LV_307-1_0_2_node_63 | 0.4 | n |  | TRUE
64 | bus_LV_307-1_0_2_node_64 | 0.4 | n |  | TRUE
65 | bus_LV_307-1_0_2_node_66 | 0.4 | n |  | TRUE
66 | bus_LV_307-1_0_2_node_96 | 0.4 | n |  | TRUE
67 | bus_LV_307-1_0_2_node_71 | 0.4 | n |  | TRUE
68 | bus_LV_307-1_0_2_node_110 | 0.4 | n |  | TRUE
69 | bus_LV_307-1_0_2_node_75 | 0.4 | n |  | TRUE
70 | bus_LV_307-1_0_2_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_307-1_0_2_node_74 | 0.4 | n |  | TRUE
72 | bus_LV_307-1_0_2_node_100 | 0.4 | n |  | TRUE
73 | bus_LV_307-1_0_2_node_111 | 0.4 | n |  | TRUE
74 | bus_LV_307-1_0_2_node_109 | 0.4 | n |  | TRUE
75 | bus_LV_307-1_0_2_node_154 | 0.4 | n |  | TRUE
76 | bus_LV_307-1_0_2_node_150 | 0.4 | n |  | TRUE
77 | bus_LV_307-1_0_2_node_112 | 0.4 | n |  | TRUE
78 | bus_LV_307-1_0_2_node_113 | 0.4 | n |  | TRUE
79 | bus_LV_307-1_0_2_node_114 | 0.4 | n |  | TRUE
80 | bus_LV_307-1_0_2_node_115 | 0.4 | n |  | TRUE
81 | bus_MV_405_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_307-1_0_2_load_0 | 0 | 0.0023259 | 0.00058293 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_307-1_0_2_load_1 | 1 | 0.0025702 | 0.00064416 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_307-1_0_2_load_3 | 3 | 0.0021707 | 0.00054403 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_307-1_0_2_load_4 | 4 | 0.0048467 | 0.0012147 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_307-1_0_2_load_5 | 5 | 0.0095113 | 0.0023838 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_307-1_0_2_load_6 | 6 | 0.0087081 | 0.0021825 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_307-1_0_2_load_7 | 7 | 0.002348 | 0.00058846 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_307-1_0_2_load_8 | 8 | 0.0061214 | 0.0015342 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_307-1_0_2_load_9 | 9 | 0.0025208 | 0.00063177 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_307-1_0_2_load_12 | 10 | 0.0022331 | 0.00055966 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_307-1_0_2_load_10 | 11 | 0.0069122 | 0.0017323 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_307-1_0_2_load_13 | 12 | 0.0074718 | 0.0018726 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_307-1_0_2_load_21 | 14 | 0.0044592 | 0.0011176 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_307-1_0_2_load_24 | 17 | 0.0010787 | 0.00027035 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_307-1_0_2_load_19 | 18 | 0.0034918 | 0.00087513 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_307-1_0_2_load_20 | 19 | 0.012646 | 0.0031695 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_307-1_0_2_load_14 | 20 | 0.0039678 | 0.00099441 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_307-1_0_2_load_153 | 24 | 0.0043307 | 0.0010854 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_307-1_0_2_load_152 | 27 | 0.0029319 | 0.00073481 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_307-1_0_2_load_155 | 28 | 0.0039432 | 0.00098826 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_307-1_0_2_load_38 | 29 | 0.0030435 | 0.00076278 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_307-1_0_2_load_36 | 31 | 0.0014492 | 0.0003632 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_307-1_0_2_load_77 | 33 | 0.0019712 | 0.00049402 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_307-1_0_2_load_41 | 34 | 0.00131 | 0.00032833 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_307-1_0_2_load_99 | 36 | 0.0032371 | 0.0008113 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_307-1_0_2_load_39 | 37 | 0.003983 | 0.00099824 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_307-1_0_2_load_25 | 38 | 0.004308 | 0.0010797 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_307-1_0_2_load_26 | 39 | 0.00094856 | 0.00023773 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_307-1_0_2_load_27 | 40 | 0.0051866 | 0.0012999 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_307-1_0_2_load_28 | 41 | 0.009038 | 0.0022651 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_307-1_0_2_load_94 | 43 | 0.0089279 | 0.0022375 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_307-1_0_2_load_95 | 44 | 0.0024941 | 0.00062507 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_307-1_0_2_load_92 | 45 | 0.0055237 | 0.0013844 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_307-1_0_2_load_30 | 46 | 0.0024198 | 0.00060646 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_307-1_0_2_load_31 | 47 | 0.0033928 | 0.00085032 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_307-1_0_2_load_32 | 48 | 0.0064899 | 0.0016265 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_307-1_0_2_load_33 | 49 | 0.0012633 | 0.00031661 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_307-1_0_2_load_67 | 53 | 0.0095788 | 0.0024007 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_307-1_0_2_load_106 | 56 | 0.005533 | 0.0013867 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_307-1_0_2_load_72 | 57 | 0.0041965 | 0.0010517 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_307-1_0_2_load_73 | 58 | 0.0019862 | 0.00049778 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_307-1_0_2_load_60 | 60 | 0.0021874 | 0.00054821 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_307-1_0_2_load_61 | 61 | 0.0010671 | 0.00026744 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_307-1_0_2_load_62 | 62 | 0.0018039 | 0.0004521 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_307-1_0_2_load_63 | 63 | 0.002634 | 0.00066013 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_307-1_0_2_load_64 | 64 | 0.00097411 | 0.00024414 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_307-1_0_2_load_75 | 69 | 0.0037753 | 0.00094618 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_307-1_0_2_load_74 | 71 | 0.0036755 | 0.00092116 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_307-1_0_2_load_100 | 72 | 0.0079147 | 0.0019836 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_307-1_0_2_load_111 | 73 | 0.0014695 | 0.00036828 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_307-1_0_2_load_109 | 74 | 0.0018446 | 0.00046231 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_307-1_0_2_load_154 | 75 | 0.0016051 | 0.00040228 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_307-1_0_2_load_150 | 76 | 0.0006704 | 0.00016802 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_307-1_0_2_load_112 | 77 | 0.0042799 | 0.0010726 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_307-1_0_2_load_113 | 78 | 0.001388 | 0.00034786 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_307-1_0_2_load_114 | 79 | 0.00093964 | 0.0002355 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_307-1_0_2_load_115 | 80 | 0.0012418 | 0.00031123 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_307-1_0_2_line_0 |  | 0 | 1 | 0.028164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_307-1_0_2_line_1 |  | 0 | 2 | 0.010197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_307-1_0_2_line_2 |  | 1 | 3 | 0.010706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_307-1_0_2_line_3 |  | 2 | 4 | 0.014661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_307-1_0_2_line_4 |  | 2 | 5 | 0.024423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_307-1_0_2_line_5 |  | 3 | 6 | 0.0042335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_307-1_0_2_line_6 |  | 4 | 7 | 0.021266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_307-1_0_2_line_7 |  | 5 | 8 | 0.0095651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_307-1_0_2_line_8 |  | 7 | 9 | 0.010516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_307-1_0_2_line_9 |  | 8 | 10 | 0.010622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_307-1_0_2_line_10 |  | 9 | 11 | 0.032472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_307-1_0_2_line_11 |  | 10 | 12 | 0.011828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_307-1_0_2_line_12 |  | 11 | 13 | 0.0024769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_307-1_0_2_line_13 |  | 12 | 18 | 0.018666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_307-1_0_2_line_14 |  | 13 | 14 | 0.0089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_307-1_0_2_line_15 |  | 13 | 15 | 0.029069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_307-1_0_2_line_16 |  | 15 | 16 | 0.014199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_307-1_0_2_line_17 |  | 15 | 17 | 0.0071915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_307-1_0_2_line_18 |  | 16 | 32 | 0.015779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_307-1_0_2_line_19 |  | 16 | 33 | 0.017531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_307-1_0_2_line_20 |  | 17 | 34 | 0.0013592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_307-1_0_2_line_21 |  | 18 | 19 | 0.003626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_307-1_0_2_line_22 |  | 19 | 30 | 0.021024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_307-1_0_2_line_23 |  | 20 | 21 | 0.022698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_307-1_0_2_line_24 |  | 21 | 22 | 0.060275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_307-1_0_2_line_25 |  | 22 | 27 | 0.005926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_307-1_0_2_line_26 |  | 22 | 23 | 0.079321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_307-1_0_2_line_27 |  | 23 | 24 | 0.022752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_307-1_0_2_line_28 |  | 23 | 25 | 0.02846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_307-1_0_2_line_29 |  | 23 | 26 | 0.055318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_307-1_0_2_line_30 |  | 25 | 28 | 0.006532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_307-1_0_2_line_31 |  | 26 | 29 | 0.023697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_307-1_0_2_line_32 |  | 29 | 37 | 0.0013486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_307-1_0_2_line_33 |  | 30 | 31 | 0.0013185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_307-1_0_2_line_34 |  | 31 | 50 | 0.018049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_307-1_0_2_line_35 |  | 32 | 35 | 0.035032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_307-1_0_2_line_36 |  | 32 | 36 | 0.022735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_307-1_0_2_line_37 |  | 34 | 37 | 0.031144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_307-1_0_2_line_38 |  | 35 | 45 | 0.033037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_307-1_0_2_line_39 |  | 36 | 72 | 0.021037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_307-1_0_2_line_40 |  | 38 | 39 | 0.019751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_307-1_0_2_line_41 |  | 38 | 40 | 0.019961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_307-1_0_2_line_42 |  | 39 | 41 | 0.011577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_307-1_0_2_line_43 |  | 41 | 42 | 0.018534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_307-1_0_2_line_44 |  | 42 | 43 | 0.0068539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_307-1_0_2_line_45 |  | 43 | 44 | 0.018402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_307-1_0_2_line_46 |  | 44 | 69 | 0.0089733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_307-1_0_2_line_47 |  | 46 | 47 | 0.0014578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_307-1_0_2_line_48 |  | 46 | 48 | 0.0083527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_307-1_0_2_line_49 |  | 47 | 49 | 0.0073487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_307-1_0_2_line_50 |  | 48 | 50 | 0.03879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_307-1_0_2_line_51 |  | 50 | 51 | 0.015213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_307-1_0_2_line_52 |  | 51 | 52 | 0.005294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_307-1_0_2_line_53 |  | 51 | 53 | 0.01552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_307-1_0_2_line_54 |  | 52 | 57 | 0.042993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_307-1_0_2_line_55 |  | 52 | 58 | 0.011372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_307-1_0_2_line_56 |  | 53 | 59 | 0.018255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_307-1_0_2_line_57 |  | 54 | 55 | 0.047316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_307-1_0_2_line_58 |  | 54 | 56 | 0.027984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_307-1_0_2_line_59 |  | 55 | 75 | 0.013918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_307-1_0_2_line_60 |  | 56 | 57 | 0.037371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_307-1_0_2_line_61 |  | 58 | 70 | 0.018018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_307-1_0_2_line_62 |  | 59 | 67 | 0.005682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_307-1_0_2_line_63 |  | 60 | 61 | 0.036468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_307-1_0_2_line_64 |  | 60 | 62 | 0.0019261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_307-1_0_2_line_65 |  | 61 | 63 | 0.020304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_307-1_0_2_line_66 |  | 62 | 64 | 0.01475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_307-1_0_2_line_67 |  | 64 | 65 | 0.017242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_307-1_0_2_line_68 |  | 65 | 66 | 0.022003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_307-1_0_2_line_69 |  | 65 | 67 | 0.006461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_307-1_0_2_line_70 |  | 66 | 68 | 0.020765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_307-1_0_2_line_71 |  | 67 | 69 | 0.034697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_307-1_0_2_line_72 |  | 68 | 73 | 0.034708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_307-1_0_2_line_73 |  | 68 | 74 | 0.073823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_307-1_0_2_line_74 |  | 70 | 71 | 0.0064357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_307-1_0_2_line_75 |  | 73 | 77 | 0.021479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_307-1_0_2_line_76 |  | 74 | 76 | 0.41381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_307-1_0_2_line_77 |  | 77 | 78 | 0.0091601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_307-1_0_2_line_78 |  | 78 | 79 | 0.0049288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_307-1_0_2_line_79 |  | 79 | 80 | 0.024543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_307-1_0_2_trafo_13 | 0.63 MVA 20/0.4 kV | 81 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2594351.9416 | 1206365.6042 | 2594325.5166 | 1206355.8606
1 | 2594361.509 | 1206369.1319 | 2594351.9416 | 1206365.6042
2 | 2594315.4714 | 1206352.1567 | 2594325.5166 | 1206355.8606
3 | 2594361.509 | 1206369.1319 | 2594375.9977 | 1206371.3749
4 | 2594361.509 | 1206369.1319 | 2594351.3602 | 1206391.3468
5 | 2594311.4993 | 1206350.6921 | 2594315.4714 | 1206352.1567
6 | 2594395.5383 | 1206379.7657 | 2594375.9977 | 1206371.3749 | 2594375.9977 | 1206371.3749
7 | 2594351.3602 | 1206391.3468 | 2594347.3855 | 1206400.0469
8 | 2594405.2012 | 1206383.915 | 2594395.5383 | 1206379.7657
9 | 2594347.3855 | 1206400.0469 | 2594344.6397 | 1206406.0572 | 2594342.5005 | 1206409.4534
10 | 2594405.2012 | 1206383.915 | 2594410.1481 | 1206386.0393 | 2594416.0574 | 1206386.7007 | 2594424.0333 | 1206385.4925 | 2594436.3192 | 1206389.9672
11 | 2594336.1965 | 1206419.4616 | 2594342.5005 | 1206409.4534
12 | 2594438.6465 | 1206390.8149 | 2594436.3192 | 1206389.9672
13 | 2594323.4913 | 1206433.135 | 2594324.0877 | 1206432.547 | 2594336.1965 | 1206419.4616 | 2594336.1965 | 1206419.4616
14 | 2594438.6465 | 1206390.8149 | 2594435.2247 | 1206399.0337
15 | 2594438.6465 | 1206390.8149 | 2594453.3753 | 1206397.7159 | 2594464.742 | 1206403.7529
16 | 2594458.3738 | 1206416.4437 | 2594463.0118 | 1206407.6234 | 2594464.742 | 1206403.7529
17 | 2594464.742 | 1206403.7529 | 2594467.4794 | 1206397.1028
18 | 2594452.3573 | 1206431.0351 | 2594458.3738 | 1206416.4437
19 | 2594458.3738 | 1206416.4437 | 2594474.9606 | 1206422.1183
20 | 2594467.9967 | 1206395.846 | 2594467.4794 | 1206397.1028
21 | 2594320.9092 | 1206435.6808 | 2594323.4913 | 1206433.135
22 | 2594305.938 | 1206450.441 | 2594320.9092 | 1206435.6808
23 | 2594363.1842 | 1206291.9881 | 2594354.9554 | 1206313.1421
24 | 2594363.1842 | 1206291.9881 | 2594391.8951 | 1206303.8005 | 2594380.978 | 1206330.9146
25 | 2594375.5081 | 1206328.5964 | 2594380.978 | 1206330.9146
26 | 2594380.978 | 1206330.9146 | 2594391.8951 | 1206303.8005 | 2594409.9326 | 1206311.2096 | 2594431.5303 | 1206320.094 | 2594438.2249 | 1206322.8448
27 | 2594438.2249 | 1206322.8448 | 2594428.9822 | 1206343.6427
28 | 2594422.9175 | 1206339.4906 | 2594431.5303 | 1206320.094 | 2594438.2249 | 1206322.8448
29 | 2594438.2249 | 1206322.8448 | 2594486.3269 | 1206342.6215 | 2594489.3851 | 1206343.8859
30 | 2594422.9175 | 1206339.4906 | 2594416.8544 | 1206337.0172
31 | 2594489.3851 | 1206343.8859 | 2594480.3649 | 1206365.7993
32 | 2594480.3649 | 1206365.7993 | 2594479.8515 | 1206367.0464
33 | 2594305.938 | 1206450.441 | 2594305.0009 | 1206451.3684
34 | 2594294.5542 | 1206466.0495 | 2594303.6665 | 1206452.6889 | 2594305.0009 | 1206451.3684
35 | 2594452.3573 | 1206431.0351 | 2594449.8156 | 1206437.1853 | 2594446.4849 | 1206445.2707 | 2594446.4177 | 1206454.6425 | 2594456.6688 | 1206455.0775
36 | 2594452.3573 | 1206431.0351 | 2594433.7932 | 1206417.9106
37 | 2594467.9967 | 1206395.846 | 2594479.8515 | 1206367.0464
38 | 2594456.6688 | 1206455.0775 | 2594452.0189 | 1206467.4109 | 2594433.4788 | 1206474.6657
39 | 2594416.6154 | 1206405.7662 | 2594433.7932 | 1206417.9106
40 | 2594428.5323 | 1206496.2281 | 2594421.7551 | 1206501.1246 | 2594415.1668 | 1206497.9402 | 2594413.4891 | 1206494.2294
41 | 2594444.7121 | 1206484.5383 | 2594428.5323 | 1206496.2281
42 | 2594413.4891 | 1206494.2294 | 2594408.7197 | 1206483.6802
43 | 2594401.0844 | 1206466.7921 | 2594408.7197 | 1206483.6802
44 | 2594401.0844 | 1206466.7921 | 2594394.8523 | 1206469.6449
45 | 2594378.1203 | 1206477.304 | 2594394.8523 | 1206469.6449
46 | 2594378.1203 | 1206477.304 | 2594369.9612 | 1206481.0389
47 | 2594254.4647 | 1206438.5757 | 2594255.6672 | 1206439.3998
48 | 2594262.5572 | 1206444.1216 | 2594255.6672 | 1206439.3998
49 | 2594254.4647 | 1206438.5757 | 2594248.4029 | 1206434.4215
50 | 2594294.5542 | 1206466.0495 | 2594262.5572 | 1206444.1216
51 | 2594294.5542 | 1206466.0495 | 2594304.6597 | 1206473.2103 | 2594307.0566 | 1206474.7644
52 | 2594303.5472 | 1206478.7366 | 2594307.0566 | 1206474.7644
53 | 2594307.0566 | 1206474.7644 | 2594319.8054 | 1206483.6154
54 | 2594303.5472 | 1206478.7366 | 2594261.2339 | 1206486.3506
55 | 2594303.5472 | 1206478.7366 | 2594301.3861 | 1206485.0422 | 2594301.1143 | 1206487.0213 | 2594301.3747 | 1206488.9221 | 2594301.5939 | 1206489.6811
56 | 2594334.8006 | 1206494.0259 | 2594319.8054 | 1206483.6154
57 | 2594187.268 | 1206500.6177 | 2594185.4033 | 1206498.8964 | 2594192.6502 | 1206491.1962 | 2594194.2451 | 1206489.1268 | 2594194.6769 | 1206487.481 | 2594194.8881 | 1206485.7243 | 2594194.335 | 1206480.1106 | 2594194.5613 | 1206478.2094 | 2594195.6288 | 1206473.4724 | 2594196.5477 | 1206472.1597 | 2594207.0628 | 1206462.7553
58 | 2594207.0628 | 1206462.7553 | 2594211.3455 | 1206464.1852 | 2594228.3056 | 1206480.4068
59 | 2594187.268 | 1206500.6177 | 2594197.4824 | 1206510.1017
60 | 2594228.3056 | 1206480.4068 | 2594238.8762 | 1206490.5171 | 2594246.9581 | 1206488.9194 | 2594261.2339 | 1206486.3506
61 | 2594309.8772 | 1206505.6452 | 2594302.0232 | 1206491.1671 | 2594301.5939 | 1206489.6811
62 | 2594339.4728 | 1206497.2788 | 2594334.8006 | 1206494.0259
63 | 2594363.245 | 1206523.5424 | 2594370.2169 | 1206528.9222 | 2594377.8258 | 1206533.7954 | 2594386.6971 | 1206538.7674 | 2594392.8061 | 1206541.6743 | 2594394.3834 | 1206542.2831
64 | 2594361.7201 | 1206522.3657 | 2594363.245 | 1206523.5424
65 | 2594413.3255 | 1206549.5937 | 2594394.3834 | 1206542.2831
66 | 2594350.0697 | 1206513.3215 | 2594353.5663 | 1206515.9533 | 2594357.2953 | 1206518.9513 | 2594361.7201 | 1206522.3657
67 | 2594336.3376 | 1206502.896 | 2594340.1426 | 1206505.8495 | 2594350.0697 | 1206513.3215
68 | 2594336.3376 | 1206502.896 | 2594331.2937 | 1206524.3126
69 | 2594336.3376 | 1206502.896 | 2594337.8476 | 1206499.5371 | 2594339.4728 | 1206497.2788
70 | 2594327.3668 | 1206544.6942 | 2594330.0366 | 1206529.6612 | 2594331.2937 | 1206524.3126
71 | 2594339.4728 | 1206497.2788 | 2594342.8845 | 1206494.5629 | 2594346.6992 | 1206491.8244 | 2594368.6432 | 1206481.6423 | 2594369.9612 | 1206481.0389
72 | 2594327.3668 | 1206544.6942 | 2594320.0762 | 1206546.6912 | 2594311.1134 | 1206549.368 | 2594293.7219 | 1206545.5985
73 | 2594327.3668 | 1206544.6942 | 2594315.0725 | 1206617.4861
74 | 2594309.8772 | 1206505.6452 | 2594313.6084 | 1206510.8889
75 | 2594293.7219 | 1206545.5985 | 2594283.2836 | 1206543.3361 | 2594272.8761 | 1206546.2144
76 | 2594315.0725 | 1206617.4861 | 2594076.7981 | 1206955.8079
77 | 2594272.8761 | 1206546.2144 | 2594272.8761 | 1206546.2144 | 2594272.7781 | 1206554.8526 | 2594272.8583 | 1206555.3678
78 | 2594273.6163 | 1206560.2379 | 2594272.8583 | 1206555.3678
79 | 2594273.6163 | 1206560.2379 | 2594276.1985 | 1206576.828 | 2594280.8356 | 1206583.0414

## bus_geodata
| x | y | coords
0 | 2594351.9416 | 1206365.6042
1 | 2594325.5166 | 1206355.8606
2 | 2594361.509 | 1206369.1319
3 | 2594315.4714 | 1206352.1567
4 | 2594375.9977 | 1206371.3749
5 | 2594351.3602 | 1206391.3468
6 | 2594311.4993 | 1206350.6921
7 | 2594395.5383 | 1206379.7657
8 | 2594347.3855 | 1206400.0469
9 | 2594405.2012 | 1206383.915
10 | 2594342.5005 | 1206409.4534
11 | 2594436.3192 | 1206389.9672
12 | 2594336.1965 | 1206419.4616
13 | 2594438.6465 | 1206390.8149
14 | 2594435.2247 | 1206399.0337
15 | 2594464.742 | 1206403.7529
16 | 2594458.3738 | 1206416.4437
17 | 2594467.4794 | 1206397.1028
18 | 2594323.4913 | 1206433.135
19 | 2594320.9092 | 1206435.6808
20 | 2594354.9554 | 1206313.1421
21 | 2594363.1842 | 1206291.9881
22 | 2594380.978 | 1206330.9146
23 | 2594438.2249 | 1206322.8448
24 | 2594428.9822 | 1206343.6427
25 | 2594422.9175 | 1206339.4906
26 | 2594489.3851 | 1206343.8859
27 | 2594375.5081 | 1206328.5964
28 | 2594416.8544 | 1206337.0172
29 | 2594480.3649 | 1206365.7993
30 | 2594305.9381 | 1206450.441
31 | 2594305.0009 | 1206451.3684
32 | 2594452.3573 | 1206431.0351
33 | 2594474.9606 | 1206422.1183
34 | 2594467.9967 | 1206395.846
35 | 2594456.6688 | 1206455.0775
36 | 2594433.7932 | 1206417.9106
37 | 2594479.8515 | 1206367.0464
38 | 2594428.5323 | 1206496.2281
39 | 2594413.4891 | 1206494.2294
40 | 2594444.7121 | 1206484.5383
41 | 2594408.7197 | 1206483.6802
42 | 2594401.0844 | 1206466.7921
43 | 2594394.8523 | 1206469.6449
44 | 2594378.1203 | 1206477.304
45 | 2594433.4788 | 1206474.6657
46 | 2594255.6672 | 1206439.3998
47 | 2594254.4647 | 1206438.5757
48 | 2594262.5572 | 1206444.1216
49 | 2594248.4029 | 1206434.4215
50 | 2594294.5542 | 1206466.0495
51 | 2594307.0566 | 1206474.7644
52 | 2594303.5472 | 1206478.7366
53 | 2594319.8054 | 1206483.6154
54 | 2594207.0628 | 1206462.7553
55 | 2594187.268 | 1206500.6177
56 | 2594228.3056 | 1206480.4067
57 | 2594261.2339 | 1206486.3506
58 | 2594301.5939 | 1206489.6811
59 | 2594334.8006 | 1206494.026
60 | 2594363.245 | 1206523.5424
61 | 2594394.3834 | 1206542.2831
62 | 2594361.7201 | 1206522.3657
63 | 2594413.3255 | 1206549.5937
64 | 2594350.0697 | 1206513.3215
65 | 2594336.3376 | 1206502.896
66 | 2594331.2937 | 1206524.3126
67 | 2594339.4728 | 1206497.2788
68 | 2594327.3668 | 1206544.6942
69 | 2594369.9612 | 1206481.0389
70 | 2594309.8772 | 1206505.6452
71 | 2594313.6084 | 1206510.8889
72 | 2594416.6154 | 1206405.7662
73 | 2594293.7219 | 1206545.5985
74 | 2594315.0725 | 1206617.4861
75 | 2594197.4824 | 1206510.1017
76 | 2594076.7981 | 1206955.8079
77 | 2594272.8761 | 1206546.2144
78 | 2594272.8583 | 1206555.3678
79 | 2594273.6163 | 1206560.2379
80 | 2594280.8356 | 1206583.0414
81 | 2594305.9381 | 1206450.441

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1