## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_311-3_2_2_node_257 | 0.4 | n |  | TRUE
1 | bus_LV_311-3_2_2_node_43 | 0.4 | n |  | TRUE
2 | bus_LV_311-3_2_2_node_264 | 0.4 | n |  | TRUE
3 | bus_LV_311-3_2_2_node_89 | 0.4 | n |  | TRUE
4 | bus_LV_311-3_2_2_node_265 | 0.4 | n |  | TRUE
5 | bus_LV_311-3_2_2_node_266 | 0.4 | n |  | TRUE
6 | bus_LV_311-3_2_2_node_42 | 0.4 | n |  | TRUE
7 | bus_LV_311-3_2_2_node_40 | 0.4 | n |  | TRUE
8 | bus_LV_311-3_2_2_node_45 | 0.4 | n |  | TRUE
9 | bus_LV_311-3_2_2_node_46 | 0.4 | n |  | TRUE
10 | bus_LV_311-3_2_2_node_47 | 0.4 | n |  | TRUE
11 | bus_LV_311-3_2_2_node_48 | 0.4 | n |  | TRUE
12 | bus_LV_311-3_2_2_node_49 | 0.4 | n |  | TRUE
13 | bus_LV_311-3_2_2_node_66 | 0.4 | n |  | TRUE
14 | bus_LV_311-3_2_2_node_51 | 0.4 | n |  | TRUE
15 | bus_LV_311-3_2_2_node_52 | 0.4 | n |  | TRUE
16 | bus_LV_311-3_2_2_node_53 | 0.4 | n |  | TRUE
17 | bus_LV_311-3_2_2_node_54 | 0.4 | n |  | TRUE
18 | bus_LV_311-3_2_2_node_55 | 0.4 | n |  | TRUE
19 | bus_LV_311-3_2_2_node_82 | 0.4 | n |  | TRUE
20 | bus_LV_311-3_2_2_node_78 | 0.4 | n |  | TRUE
21 | bus_LV_311-3_2_2_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_311-3_2_2_node_90 | 0.4 | n |  | TRUE
23 | bus_LV_311-3_2_2_node_87 | 0.4 | n |  | TRUE
24 | bus_LV_311-3_2_2_node_60 | 0.4 | n |  | TRUE
25 | bus_LV_311-3_2_2_node_61 | 0.4 | n |  | TRUE
26 | bus_LV_311-3_2_2_node_62 | 0.4 | n |  | TRUE
27 | bus_LV_311-3_2_2_node_63 | 0.4 | n |  | TRUE
28 | bus_LV_311-3_2_2_node_74 | 0.4 | n |  | TRUE
29 | bus_LV_311-3_2_2_node_85 | 0.4 | n |  | TRUE
30 | bus_LV_311-3_2_2_node_64 | 0.4 | n |  | TRUE
31 | bus_LV_311-3_2_2_node_65 | 0.4 | n |  | TRUE
32 | bus_LV_311-3_2_2_node_67 | 0.4 | n |  | TRUE
33 | bus_LV_311-3_2_2_node_68 | 0.4 | n |  | TRUE
34 | bus_LV_311-3_2_2_node_88 | 0.4 | n |  | TRUE
35 | bus_LV_311-3_2_2_node_72 | 0.4 | n |  | TRUE
36 | bus_LV_311-3_2_2_node_69 | 0.4 | n |  | TRUE
37 | bus_LV_311-3_2_2_node_70 | 0.4 | n |  | TRUE
38 | bus_LV_311-3_2_2_node_71 | 0.4 | n |  | TRUE
39 | bus_LV_311-3_2_2_node_73 | 0.4 | n |  | TRUE
40 | bus_LV_311-3_2_2_node_75 | 0.4 | n |  | TRUE
41 | bus_LV_311-3_2_2_node_76 | 0.4 | n |  | TRUE
42 | bus_LV_311-3_2_2_node_77 | 0.4 | n |  | TRUE
43 | bus_LV_311-3_2_2_node_80 | 0.4 | n |  | TRUE
44 | bus_LV_311-3_2_2_node_79 | 0.4 | n |  | TRUE
45 | bus_LV_311-3_2_2_node_81 | 0.4 | n |  | TRUE
46 | bus_LV_311-3_2_2_node_83 | 0.4 | n |  | TRUE
47 | bus_LV_311-3_2_2_node_84 | 0.4 | n |  | TRUE
48 | bus_LV_311-3_2_2_node_86 | 0.4 | n |  | TRUE
49 | bus_LV_311-3_2_2_node_91 | 0.4 | n |  | TRUE
50 | bus_LV_311-3_2_2_node_190 | 0.4 | n |  | TRUE
51 | bus_LV_311-3_2_2_node_191 | 0.4 | n |  | TRUE
52 | bus_LV_311-3_2_2_node_192 | 0.4 | n |  | TRUE
53 | bus_MV_385_1_node_222 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_311-3_2_2_load_257 | 0 | 0.0054067 | 0.001355 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_311-3_2_2_load_89 | 3 | 0.011774 | 0.0029508 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_311-3_2_2_load_265 | 4 | 0.01156 | 0.0028973 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_311-3_2_2_load_266 | 5 | 0.05506 | 0.013799 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_311-3_2_2_load_40 | 7 | 0.001086 | 0.00027218 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_311-3_2_2_load_45 | 8 | 0.0035936 | 0.00090064 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_311-3_2_2_load_46 | 9 | 0.0010646 | 0.00026682 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_311-3_2_2_load_48 | 11 | 0.0050104 | 0.0012557 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_311-3_2_2_load_49 | 12 | 0.0029532 | 0.00074014 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_311-3_2_2_load_51 | 14 | 0.0064044 | 0.0016051 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_311-3_2_2_load_52 | 15 | 0.00040325 | 0.00010106 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_311-3_2_2_load_54 | 17 | 0.0024384 | 0.00061113 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_311-3_2_2_load_55 | 18 | 0.0061759 | 0.0015478 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_311-3_2_2_load_82 | 19 | 0.0079224 | 0.0019855 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_311-3_2_2_load_78 | 20 | 0.012022 | 0.003013 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_311-3_2_2_load_87 | 23 | 0.00088322 | 0.00022136 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_311-3_2_2_load_60 | 24 | 0.0022498 | 0.00056385 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_311-3_2_2_load_62 | 26 | 0.00059913 | 0.00015016 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_311-3_2_2_load_63 | 27 | 0.0016782 | 0.00042059 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_311-3_2_2_load_74 | 28 | 0.00082871 | 0.00020769 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_311-3_2_2_load_85 | 29 | 0.001985 | 0.00049749 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_311-3_2_2_load_64 | 30 | 0.0041422 | 0.0010381 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_311-3_2_2_load_65 | 31 | 0.0030934 | 0.00077527 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_311-3_2_2_load_68 | 33 | 0.0077092 | 0.0019321 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_311-3_2_2_load_88 | 34 | 0.0071166 | 0.0017836 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_311-3_2_2_load_72 | 35 | 0.0095883 | 0.0024031 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_311-3_2_2_load_69 | 36 | 0.011876 | 0.0029765 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_311-3_2_2_load_70 | 37 | 0.0029935 | 0.00075024 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_311-3_2_2_load_73 | 39 | 0.0005925 | 0.0001485 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_311-3_2_2_load_75 | 40 | 0.00081219 | 0.00020355 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_311-3_2_2_load_76 | 41 | 0.0004081 | 0.00010228 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_311-3_2_2_load_77 | 42 | 0.0013177 | 0.00033025 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_311-3_2_2_load_80 | 43 | 0.00035848 | 8.9845e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_311-3_2_2_load_79 | 44 | 0.0009904 | 0.00024822 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_311-3_2_2_load_81 | 45 | 0.0019682 | 0.00049329 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_311-3_2_2_load_83 | 46 | 0.0010638 | 0.00026662 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_311-3_2_2_load_84 | 47 | 0.0022045 | 0.00055251 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_311-3_2_2_load_86 | 48 | 0.00088837 | 0.00022265 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_311-3_2_2_load_91 | 49 | 0.018356 | 0.0046004 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_311-3_2_2_load_190 | 50 | 0.0036101 | 0.00090477 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_311-3_2_2_load_191 | 51 | 0.007104 | 0.0017804 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_311-3_2_2_load_192 | 52 | 0.0070044 | 0.0017555 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_311-3_2_2_line_0 |  | 0 | 1 | 0.011873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_311-3_2_2_line_1 |  | 1 | 6 | 0.22194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_311-3_2_2_line_2 |  | 2 | 3 | 0.021764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_311-3_2_2_line_3 |  | 2 | 4 | 0.057843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_311-3_2_2_line_4 |  | 2 | 5 | 0.049546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_311-3_2_2_line_5 |  | 3 | 32 | 0.035479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_311-3_2_2_line_6 |  | 4 | 6 | 0.15264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_311-3_2_2_line_7 |  | 6 | 7 | 0.12752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_311-3_2_2_line_8 |  | 8 | 9 | 0.010287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_311-3_2_2_line_9 |  | 8 | 10 | 0.021612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_311-3_2_2_line_10 |  | 9 | 11 | 0.0084327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_311-3_2_2_line_11 |  | 10 | 12 | 0.030543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_311-3_2_2_line_12 |  | 12 | 13 | 0.083649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_311-3_2_2_line_13 |  | 13 | 33 | 0.035317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_311-3_2_2_line_14 |  | 13 | 30 | 0.017162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_311-3_2_2_line_15 |  | 14 | 15 | 0.016435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_311-3_2_2_line_16 |  | 14 | 16 | 0.087174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_311-3_2_2_line_17 |  | 15 | 17 | 0.0058867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_311-3_2_2_line_18 |  | 16 | 18 | 0.02695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_311-3_2_2_line_19 |  | 17 | 19 | 0.031991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_311-3_2_2_line_20 |  | 18 | 20 | 0.0045076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_311-3_2_2_line_21 |  | 19 | 45 | 0.0022876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_311-3_2_2_line_22 |  | 20 | 44 | 0.13568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_311-3_2_2_line_23 |  | 21 | 22 | 0.1724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_311-3_2_2_line_24 |  | 21 | 23 | 0.11676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_311-3_2_2_line_25 |  | 22 | 50 | 0.043347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_311-3_2_2_line_26 |  | 23 | 44 | 0.034223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_311-3_2_2_line_27 |  | 24 | 25 | 0.013942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_311-3_2_2_line_28 |  | 25 | 26 | 0.045591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_311-3_2_2_line_29 |  | 25 | 27 | 0.022555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_311-3_2_2_line_30 |  | 26 | 28 | 0.057895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_311-3_2_2_line_31 |  | 27 | 29 | 0.011927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_311-3_2_2_line_32 |  | 28 | 38 | 0.024038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_311-3_2_2_line_33 |  | 29 | 46 | 0.014287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_311-3_2_2_line_34 |  | 30 | 31 | 0.00068934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_311-3_2_2_line_35 |  | 31 | 32 | 0.027495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_311-3_2_2_line_36 |  | 32 | 34 | 0.015972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_311-3_2_2_line_37 |  | 33 | 35 | 0.020711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_311-3_2_2_line_38 |  | 34 | 49 | 0.014993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_311-3_2_2_line_39 |  | 35 | 37 | 0.024698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_311-3_2_2_line_40 |  | 36 | 37 | 0.017305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_311-3_2_2_line_41 |  | 36 | 38 | 0.0099025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_311-3_2_2_line_42 |  | 38 | 39 | 0.034107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_311-3_2_2_line_43 |  | 39 | 40 | 0.016532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_311-3_2_2_line_44 |  | 40 | 41 | 0.019576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_311-3_2_2_line_45 |  | 41 | 42 | 0.021047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_311-3_2_2_line_46 |  | 42 | 43 | 0.0069244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_311-3_2_2_line_47 |  | 43 | 45 | 0.00032172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_311-3_2_2_line_48 |  | 46 | 47 | 0.015736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_311-3_2_2_line_49 |  | 47 | 48 | 0.0059593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_311-3_2_2_line_50 |  | 50 | 51 | 0.031356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_311-3_2_2_line_51 |  | 51 | 52 | 0.046774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_311-3_2_2_trafo_266 | 0.63 MVA 20/0.4 kV | 53 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2595413.4688 | 1209104.588 | 2595416.1325 | 1209099.094 | 2595418.0054 | 1209093.6398
1 | 2595413.4688 | 1209104.588 | 2595416.5335 | 1209106.42 | 2595468.7778 | 1209198.5191 | 2595524.977 | 1209295.9632
2 | 2595629.7727 | 1209475.0053 | 2595611.3756 | 1209486.634
3 | 2595629.7727 | 1209475.0053 | 2595631.27 | 1209464.7763 | 2595612.0917 | 1209421.3
4 | 2595629.7727 | 1209475.0053 | 2595639.68 | 1209469.8507 | 2595647.8272 | 1209458.8719 | 2595657.392 | 1209442.8115 | 2595658.8165 | 1209436.9183
5 | 2595581.1064 | 1209505.0362 | 2595583.1192 | 1209503.2003 | 2595610.7728 | 1209487.015 | 2595611.3756 | 1209486.634
6 | 2595612.0917 | 1209421.3 | 2595524.977 | 1209295.9632
7 | 2595524.977 | 1209295.9632 | 2595470.0397 | 1209316.8613 | 2595459.8962 | 1209321.2938 | 2595449.958 | 1209325.8151 | 2595443.2875 | 1209329.5668 | 2595435.4552 | 1209334.8091 | 2595426.1501 | 1209342.1982 | 2595415.3122 | 1209352.7347 | 2595413.4679 | 1209354.6779
8 | 2595461.3412 | 1209576.4025 | 2595451.7309 | 1209572.7343
9 | 2595478.3216 | 1209589.1276 | 2595473.6738 | 1209584.0395 | 2595471.8331 | 1209582.1955 | 2595469.0268 | 1209579.8297 | 2595466.8292 | 1209578.4973 | 2595461.3412 | 1209576.4025
10 | 2595443.8526 | 1209569.7272 | 2595451.7309 | 1209572.7343
11 | 2595478.3216 | 1209589.1276 | 2595487.9614 | 1209582.5277 | 2595492.8235 | 1209579.7335 | 2595497.4049 | 1209577.6288 | 2595505.0438 | 1209574.6171
12 | 2595584.7197 | 1209549.4135 | 2595531.0647 | 1209564.6515 | 2595527.2958 | 1209565.8439 | 2595505.0438 | 1209574.6171
13 | 2595584.7197 | 1209549.4135 | 2595592.6983 | 1209546.984 | 2595618.2719 | 1209538.3974
14 | 2595584.7197 | 1209549.4135 | 2595582.6222 | 1209539.6875 | 2595581.5187 | 1209532.5597
15 | 2595823.8561 | 1209492.2981 | 2595839.7013 | 1209487.9334
16 | 2595923.7765 | 1209464.899 | 2595909.9689 | 1209468.5774 | 2595839.7013 | 1209487.9334
17 | 2595823.8561 | 1209492.2981 | 2595818.1808 | 1209493.8614
18 | 2595923.7765 | 1209464.899 | 2595921.6128 | 1209446.6571 | 2595921.9668 | 1209441.9765 | 2595922.8686 | 1209438.196
19 | 2595818.1808 | 1209493.8614 | 2595787.3387 | 1209502.3572
20 | 2595922.8686 | 1209438.196 | 2595922.8686 | 1209438.196 | 2595924.918 | 1209434.1813 | 2595924.918 | 1209434.1813
21 | 2595787.3387 | 1209502.3572 | 2595785.1333 | 1209502.9647
22 | 2595924.918 | 1209434.1813 | 2596001.5124 | 1209328.0142 | 2596005.0117 | 1209324.7814
23 | 2596121.691 | 1209058.6736 | 2596122.271 | 1209096.5719 | 2596119.7199 | 1209181.1202 | 2596119.7228 | 1209185.4337 | 2596119.7484 | 1209224.0439 | 2596120.3962 | 1209226.6449 | 2596122.6409 | 1209230.3233
24 | 2596122.6409 | 1209230.3233 | 2596084.2924 | 1209260.9324 | 2596030.1491 | 1209301.5579
25 | 2596121.691 | 1209058.6736 | 2596127.3543 | 1209048.064 | 2596131.4909 | 1209027.461 | 2596133.2622 | 1209017.308
26 | 2596005.0117 | 1209324.7814 | 2596030.1491 | 1209301.5579
27 | 2595740.7738 | 1209636.1794 | 2595744.7492 | 1209649.5431
28 | 2595740.7738 | 1209636.1794 | 2595728.0519 | 1209595.7997 | 2595726.5413 | 1209592.9172
29 | 2595740.7738 | 1209636.1794 | 2595759.5948 | 1209623.749
30 | 2595699.6681 | 1209541.6368 | 2595726.5413 | 1209592.9172
31 | 2595759.5948 | 1209623.749 | 2595769.5474 | 1209617.1757
32 | 2595688.4137 | 1209520.3981 | 2595689.9358 | 1209523.0652 | 2595699.6681 | 1209541.6368
33 | 2595781.4693 | 1209609.3018 | 2595781.4693 | 1209609.3018 | 2595769.5474 | 1209617.1757
34 | 2595581.4132 | 1209531.8785 | 2595581.5187 | 1209532.5597
35 | 2595581.1064 | 1209505.0362 | 2595579.5128 | 1209508.2836 | 2595578.9595 | 1209510.3407 | 2595578.75 | 1209514.6766 | 2595581.4132 | 1209531.8785
36 | 2595581.1064 | 1209505.0362 | 2595565.3247 | 1209507.4967
37 | 2595637.9057 | 1209531.8052 | 2595618.2719 | 1209538.3974
38 | 2595550.5105 | 1209509.8064 | 2595565.3247 | 1209507.4967
39 | 2595637.9057 | 1209531.8052 | 2595652.0656 | 1209527.0509 | 2595656.5414 | 1209525.858 | 2595661.5973 | 1209524.9919
40 | 2595678.6534 | 1209522.0701 | 2595661.5973 | 1209524.9919
41 | 2595688.4137 | 1209520.3981 | 2595678.6534 | 1209522.0701
42 | 2595688.4137 | 1209520.3981 | 2595719.5125 | 1209517.307 | 2595722.3384 | 1209516.9004
43 | 2595738.6755 | 1209514.383 | 2595733.3363 | 1209515.318 | 2595722.3384 | 1209516.9004
44 | 2595738.6755 | 1209514.383 | 2595744.1732 | 1209513.4202 | 2595757.8519 | 1209510.4642
45 | 2595757.8519 | 1209510.4642 | 2595757.8519 | 1209510.4642 | 2595773.0422 | 1209506.2954 | 2595778.1473 | 1209504.8891
46 | 2595784.8231 | 1209503.0502 | 2595778.1473 | 1209504.8891
47 | 2595785.1333 | 1209502.9647 | 2595784.8231 | 1209503.0502
48 | 2595781.4693 | 1209609.3018 | 2595795.0855 | 1209601.414
49 | 2595800.242 | 1209598.4268 | 2595795.0855 | 1209601.414
50 | 2596133.2622 | 1209017.308 | 2596138.6511 | 1208986.4186
51 | 2596137.0047 | 1208939.909 | 2596139.449 | 1208958.0841 | 2596140.0669 | 1208972.9252 | 2596139.3662 | 1208982.3197 | 2596138.6511 | 1208986.4186

## bus_geodata
| x | y | coords
0 | 2595418.0054 | 1209093.6398
1 | 2595413.4688 | 1209104.588
2 | 2595629.7727 | 1209475.0053
3 | 2595611.3756 | 1209486.634
4 | 2595612.0917 | 1209421.3
5 | 2595658.8165 | 1209436.9183
6 | 2595524.977 | 1209295.9632
7 | 2595413.4679 | 1209354.6779
8 | 2595461.3412 | 1209576.4025
9 | 2595451.7309 | 1209572.7343
10 | 2595478.3216 | 1209589.1276
11 | 2595443.8526 | 1209569.7272
12 | 2595505.0438 | 1209574.6171
13 | 2595584.7197 | 1209549.4135
14 | 2595839.7013 | 1209487.9334
15 | 2595823.8561 | 1209492.2981
16 | 2595923.7765 | 1209464.899
17 | 2595818.1808 | 1209493.8614
18 | 2595922.8686 | 1209438.196
19 | 2595787.3387 | 1209502.3572
20 | 2595924.918 | 1209434.1813
21 | 2596122.6409 | 1209230.3233
22 | 2596121.691 | 1209058.6736
23 | 2596030.1491 | 1209301.5579
24 | 2595744.7492 | 1209649.5431
25 | 2595740.7738 | 1209636.1794
26 | 2595726.5413 | 1209592.9172
27 | 2595759.5948 | 1209623.749
28 | 2595699.6681 | 1209541.6368
29 | 2595769.5474 | 1209617.1757
30 | 2595581.5187 | 1209532.5597
31 | 2595581.4132 | 1209531.8785
32 | 2595581.1064 | 1209505.0362
33 | 2595618.2719 | 1209538.3974
34 | 2595565.3247 | 1209507.4967
35 | 2595637.9057 | 1209531.8052
36 | 2595678.6534 | 1209522.0701
37 | 2595661.5973 | 1209524.9919
38 | 2595688.4137 | 1209520.3981
39 | 2595722.3384 | 1209516.9004
40 | 2595738.6755 | 1209514.383
41 | 2595757.8519 | 1209510.4642
42 | 2595778.1473 | 1209504.8891
43 | 2595784.8231 | 1209503.0502
44 | 2596005.0117 | 1209324.7814
45 | 2595785.1333 | 1209502.9647
46 | 2595781.4693 | 1209609.3018
47 | 2595795.0855 | 1209601.414
48 | 2595800.242 | 1209598.4268
49 | 2595550.5105 | 1209509.8064
50 | 2596133.2622 | 1209017.308
51 | 2596138.6511 | 1208986.4186
52 | 2596137.0047 | 1208939.909
53 | 2595629.7727 | 1209475.0053

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1