## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_354-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_354-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_354-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_354-9_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_354-9_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_354-9_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_354-9_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_354-9_0_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_354-9_0_4_node_88 | 0.4 | n |  | TRUE
9 | bus_LV_354-9_0_4_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_354-9_0_4_node_89 | 0.4 | n |  | TRUE
11 | bus_LV_354-9_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_354-9_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_354-9_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_354-9_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_354-9_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_354-9_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_354-9_0_4_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_354-9_0_4_node_99 | 0.4 | n |  | TRUE
19 | bus_LV_354-9_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_354-9_0_4_node_87 | 0.4 | n |  | TRUE
21 | bus_LV_354-9_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_354-9_0_4_node_90 | 0.4 | n |  | TRUE
23 | bus_LV_354-9_0_4_node_81 | 0.4 | n |  | TRUE
24 | bus_LV_354-9_0_4_node_50 | 0.4 | n |  | TRUE
25 | bus_LV_354-9_0_4_node_49 | 0.4 | n |  | TRUE
26 | bus_LV_354-9_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_354-9_0_4_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_354-9_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_354-9_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_354-9_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_354-9_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_354-9_0_4_node_42 | 0.4 | n |  | TRUE
33 | bus_LV_354-9_0_4_node_92 | 0.4 | n |  | TRUE
34 | bus_LV_354-9_0_4_node_59 | 0.4 | n |  | TRUE
35 | bus_LV_354-9_0_4_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_354-9_0_4_node_91 | 0.4 | n |  | TRUE
37 | bus_LV_354-9_0_4_node_54 | 0.4 | n |  | TRUE
38 | bus_LV_354-9_0_4_node_53 | 0.4 | n |  | TRUE
39 | bus_LV_354-9_0_4_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_354-9_0_4_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_354-9_0_4_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_354-9_0_4_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_354-9_0_4_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_354-9_0_4_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_354-9_0_4_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_354-9_0_4_node_71 | 0.4 | n |  | TRUE
47 | bus_LV_354-9_0_4_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_354-9_0_4_node_58 | 0.4 | n |  | TRUE
49 | bus_LV_354-9_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_354-9_0_4_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_354-9_0_4_node_72 | 0.4 | n |  | TRUE
52 | bus_LV_354-9_0_4_node_29 | 0.4 | n |  | TRUE
53 | bus_LV_354-9_0_4_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_354-9_0_4_node_32 | 0.4 | n |  | TRUE
55 | bus_LV_354-9_0_4_node_75 | 0.4 | n |  | TRUE
56 | bus_LV_354-9_0_4_node_74 | 0.4 | n |  | TRUE
57 | bus_LV_354-9_0_4_node_73 | 0.4 | n |  | TRUE
58 | bus_LV_354-9_0_4_node_95 | 0.4 | n |  | TRUE
59 | bus_LV_354-9_0_4_node_35 | 0.4 | n |  | TRUE
60 | bus_LV_354-9_0_4_node_37 | 0.4 | n |  | TRUE
61 | bus_LV_354-9_0_4_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_354-9_0_4_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_354-9_0_4_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_354-9_0_4_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_354-9_0_4_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_354-9_0_4_node_60 | 0.4 | n |  | TRUE
67 | bus_LV_354-9_0_4_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_354-9_0_4_node_45 | 0.4 | n |  | TRUE
69 | bus_LV_354-9_0_4_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_354-9_0_4_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_354-9_0_4_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_354-9_0_4_node_96 | 0.4 | n |  | TRUE
73 | bus_LV_354-9_0_4_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_354-9_0_4_node_51 | 0.4 | n |  | TRUE
75 | bus_LV_354-9_0_4_node_55 | 0.4 | n |  | TRUE
76 | bus_LV_354-9_0_4_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_354-9_0_4_node_57 | 0.4 | n |  | TRUE
78 | bus_LV_354-9_0_4_node_98 | 0.4 | n |  | TRUE
79 | bus_LV_354-9_0_4_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_354-9_0_4_node_94 | 0.4 | n |  | TRUE
81 | bus_LV_354-9_0_4_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_354-9_0_4_node_61 | 0.4 | n |  | TRUE
83 | bus_LV_354-9_0_4_node_93 | 0.4 | n |  | TRUE
84 | bus_LV_354-9_0_4_node_66 | 0.4 | n |  | TRUE
85 | bus_LV_354-9_0_4_node_67 | 0.4 | n |  | TRUE
86 | bus_LV_354-9_0_4_node_68 | 0.4 | n |  | TRUE
87 | bus_LV_354-9_0_4_node_69 | 0.4 | n |  | TRUE
88 | bus_LV_354-9_0_4_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_354-9_0_4_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_354-9_0_4_node_77 | 0.4 | n |  | TRUE
91 | bus_LV_354-9_0_4_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_354-9_0_4_node_79 | 0.4 | n |  | TRUE
93 | bus_LV_354-9_0_4_node_80 | 0.4 | n |  | TRUE
94 | bus_LV_354-9_0_4_node_97 | 0.4 | n |  | TRUE
95 | bus_LV_354-9_0_4_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_354-9_0_4_node_85 | 0.4 | n |  | TRUE
97 | bus_LV_354-9_0_4_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_354-9_0_4_node_82 | 0.4 | n |  | TRUE
99 | bus_MV_415_0_node_157 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_354-9_0_4_load_0 | 0 | 0.0053427 | 0.001339 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_354-9_0_4_load_1 | 1 | 0.0028404 | 0.00071188 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_354-9_0_4_load_3 | 3 | 0.0039045 | 0.00097856 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_354-9_0_4_load_4 | 4 | 0.0031919 | 0.00079996 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_354-9_0_4_load_5 | 5 | 0.013045 | 0.0032695 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_354-9_0_4_load_6 | 6 | 0.0019873 | 0.00049805 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_354-9_0_4_load_13 | 7 | 0.0022255 | 0.00055776 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_354-9_0_4_load_88 | 8 | 0.0054055 | 0.0013547 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_354-9_0_4_load_14 | 9 | 0.0016456 | 0.00041243 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_354-9_0_4_load_89 | 10 | 0.0049902 | 0.0012507 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_354-9_0_4_load_7 | 11 | 0.012742 | 0.0031935 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_354-9_0_4_load_8 | 12 | 0.010962 | 0.0027473 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_354-9_0_4_load_10 | 14 | 0.0019253 | 0.00048253 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_354-9_0_4_load_11 | 15 | 0.0027645 | 0.00069285 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_354-9_0_4_load_12 | 16 | 0.011328 | 0.002839 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_354-9_0_4_load_33 | 17 | 0.0025157 | 0.0006305 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_354-9_0_4_load_99 | 18 | 0.0077806 | 0.00195 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_354-9_0_4_load_15 | 19 | 0.001359 | 0.0003406 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_354-9_0_4_load_16 | 21 | 0.0041824 | 0.0010482 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_354-9_0_4_load_90 | 22 | 0.002966 | 0.00074334 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_354-9_0_4_load_50 | 24 | 0.0023627 | 0.00059214 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_354-9_0_4_load_49 | 25 | 0.0014299 | 0.00035836 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_354-9_0_4_load_21 | 26 | 0.0016731 | 0.00041932 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_354-9_0_4_load_22 | 27 | 0.001277 | 0.00032006 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_354-9_0_4_load_17 | 28 | 0.0084209 | 0.0021105 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_354-9_0_4_load_19 | 30 | 0.0013829 | 0.00034658 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_354-9_0_4_load_20 | 31 | 0.0016615 | 0.00041641 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_354-9_0_4_load_92 | 33 | 0.0013909 | 0.00034859 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_354-9_0_4_load_59 | 34 | 0.0030349 | 0.00076062 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_354-9_0_4_load_41 | 35 | 0.0079534 | 0.0019933 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_354-9_0_4_load_91 | 36 | 0.00074495 | 0.0001867 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_354-9_0_4_load_54 | 37 | 0.00080759 | 0.0002024 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_354-9_0_4_load_53 | 38 | 0.0035877 | 0.00089916 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_354-9_0_4_load_23 | 39 | 0.013994 | 0.0035072 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_354-9_0_4_load_24 | 40 | 0.0039274 | 0.00098431 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_354-9_0_4_load_27 | 43 | 0.01423 | 0.0035663 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_354-9_0_4_load_28 | 44 | 0.0043237 | 0.0010836 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_354-9_0_4_load_71 | 46 | 0.0162 | 0.0040601 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_354-9_0_4_load_30 | 47 | 0.0088007 | 0.0022057 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_354-9_0_4_load_58 | 48 | 0.004608 | 0.0011549 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_354-9_0_4_load_39 | 49 | 0.01001 | 0.0025087 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_354-9_0_4_load_34 | 50 | 0.020076 | 0.0050316 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_354-9_0_4_load_29 | 52 | 0.040042 | 0.010035 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_354-9_0_4_load_31 | 53 | 0.00051615 | 0.00012936 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_354-9_0_4_load_74 | 56 | 0.0093913 | 0.0023537 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_354-9_0_4_load_73 | 57 | 0.0031057 | 0.00077837 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_354-9_0_4_load_95 | 58 | 0.0023167 | 0.00058061 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_354-9_0_4_load_38 | 61 | 0.0088526 | 0.0022187 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_354-9_0_4_load_43 | 62 | 0.010733 | 0.0026899 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_354-9_0_4_load_40 | 63 | 0.0075375 | 0.0018891 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_354-9_0_4_load_63 | 64 | 0.0036913 | 0.00092513 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_354-9_0_4_load_62 | 65 | 0.011966 | 0.002999 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_354-9_0_4_load_60 | 66 | 0.0024362 | 0.00061056 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_354-9_0_4_load_44 | 67 | 0.0020245 | 0.00050739 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_354-9_0_4_load_46 | 69 | 0.0034364 | 0.00086124 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_354-9_0_4_load_47 | 70 | 0.0011776 | 0.00029513 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_354-9_0_4_load_96 | 72 | 0.0097957 | 0.002455 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_354-9_0_4_load_51 | 74 | 0.0026015 | 0.00065199 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_354-9_0_4_load_57 | 77 | 0.0007913 | 0.00019832 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_354-9_0_4_load_98 | 78 | 0.046873 | 0.011748 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_354-9_0_4_load_94 | 80 | 0.0028867 | 0.00072348 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_354-9_0_4_load_65 | 81 | 0.0030084 | 0.00075396 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_354-9_0_4_load_61 | 82 | 0.030289 | 0.0075913 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_354-9_0_4_load_93 | 83 | 0.0041153 | 0.0010314 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_354-9_0_4_load_66 | 84 | 0.0017343 | 0.00043465 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_354-9_0_4_load_67 | 85 | 0.0031826 | 0.00079764 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_354-9_0_4_load_68 | 86 | 0.002653 | 0.00066491 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_354-9_0_4_load_69 | 87 | 0.003383 | 0.00084787 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_354-9_0_4_load_70 | 88 | 0.0010072 | 0.00025242 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_354-9_0_4_load_76 | 89 | 0.0040139 | 0.001006 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_354-9_0_4_load_78 | 91 | 0.0042314 | 0.0010605 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_354-9_0_4_load_79 | 92 | 0.0035903 | 0.00089981 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_354-9_0_4_load_97 | 94 | 0.018801 | 0.0047119 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_354-9_0_4_load_85 | 96 | 0.0014101 | 0.0003534 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_354-9_0_4_load_84 | 97 | 0.041712 | 0.010454 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_354-9_0_4_load_82 | 98 | 0.009334 | 0.0023393 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 48 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_354-9_0_4_line_0 |  | 0 | 1 | 0.01711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_354-9_0_4_line_1 |  | 0 | 2 | 0.017898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_354-9_0_4_line_2 |  | 1 | 3 | 0.0035201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_354-9_0_4_line_3 |  | 2 | 4 | 0.025893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_354-9_0_4_line_4 |  | 2 | 5 | 0.0028779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_354-9_0_4_line_5 |  | 3 | 6 | 0.0015759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_354-9_0_4_line_6 |  | 4 | 7 | 0.0072933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_354-9_0_4_line_7 |  | 5 | 8 | 0.021737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_354-9_0_4_line_8 |  | 7 | 9 | 0.0046415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_354-9_0_4_line_9 |  | 8 | 10 | 0.010571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_354-9_0_4_line_10 |  | 9 | 24 | 0.00042468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_354-9_0_4_line_11 |  | 10 | 62 | 0.015678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_354-9_0_4_line_12 |  | 11 | 12 | 0.06412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_354-9_0_4_line_13 |  | 11 | 13 | 0.013653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_354-9_0_4_line_14 |  | 12 | 14 | 0.024432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_354-9_0_4_line_15 |  | 13 | 15 | 0.035362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_354-9_0_4_line_16 |  | 13 | 16 | 0.014992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_354-9_0_4_line_17 |  | 14 | 17 | 0.0061367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_354-9_0_4_line_18 |  | 14 | 18 | 0.054267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_354-9_0_4_line_19 |  | 15 | 19 | 0.029552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_354-9_0_4_line_20 |  | 16 | 20 | 0.016301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_354-9_0_4_line_21 |  | 19 | 21 | 0.013382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_354-9_0_4_line_22 |  | 20 | 22 | 0.025528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_354-9_0_4_line_23 |  | 20 | 23 | 0.011921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_354-9_0_4_line_24 |  | 21 | 26 | 0.0092776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_354-9_0_4_line_25 |  | 23 | 96 | 0.017797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_354-9_0_4_line_26 |  | 23 | 93 | 0.038762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_354-9_0_4_line_27 |  | 24 | 25 | 0.002706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_354-9_0_4_line_28 |  | 25 | 70 | 0.00012833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_354-9_0_4_line_29 |  | 26 | 27 | 0.0025975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_354-9_0_4_line_30 |  | 27 | 37 | 0.0016181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_354-9_0_4_line_31 |  | 28 | 29 | 0.021918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_354-9_0_4_line_32 |  | 29 | 30 | 0.020319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_354-9_0_4_line_33 |  | 29 | 31 | 0.021689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_354-9_0_4_line_34 |  | 30 | 32 | 0.039145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_354-9_0_4_line_35 |  | 31 | 33 | 0.0083237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_354-9_0_4_line_36 |  | 32 | 34 | 0.016559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_354-9_0_4_line_37 |  | 32 | 35 | 0.015234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_354-9_0_4_line_38 |  | 33 | 36 | 0.010765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_354-9_0_4_line_39 |  | 34 | 66 | 0.0071348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_354-9_0_4_line_40 |  | 35 | 63 | 0.018815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_354-9_0_4_line_41 |  | 36 | 88 | 0.0092624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_354-9_0_4_line_42 |  | 37 | 38 | 0.027586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_354-9_0_4_line_43 |  | 38 | 75 | 0.023368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_354-9_0_4_line_44 |  | 39 | 40 | 0.012703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_354-9_0_4_line_45 |  | 39 | 41 | 0.0034861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_354-9_0_4_line_46 |  | 40 | 42 | 0.01268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_354-9_0_4_line_47 |  | 41 | 43 | 0.0048613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_354-9_0_4_line_48 |  | 41 | 44 | 0.038067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_354-9_0_4_line_49 |  | 42 | 45 | 0.026195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_354-9_0_4_line_50 |  | 42 | 46 | 0.019884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_354-9_0_4_line_51 |  | 43 | 47 | 0.08787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_354-9_0_4_line_52 |  | 44 | 48 | 0.0066054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_354-9_0_4_line_53 |  | 45 | 49 | 0.012284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_354-9_0_4_line_54 |  | 45 | 50 | 0.021637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_354-9_0_4_line_55 |  | 46 | 51 | 0.021026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_354-9_0_4_line_56 |  | 47 | 52 | 0.0010771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_354-9_0_4_line_57 |  | 49 | 64 | 0.033253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_354-9_0_4_line_58 |  | 51 | 61 | 0.013809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_354-9_0_4_line_59 |  | 52 | 53 | 0.026952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_354-9_0_4_line_60 |  | 53 | 54 | 0.014293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_354-9_0_4_line_61 |  | 54 | 55 | 0.00211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_354-9_0_4_line_62 |  | 54 | 56 | 0.028379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_354-9_0_4_line_63 |  | 55 | 58 | 0.018694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_354-9_0_4_line_64 |  | 56 | 57 | 0.039005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_354-9_0_4_line_65 |  | 59 | 60 | 0.018726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_354-9_0_4_line_66 |  | 59 | 61 | 0.021442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_354-9_0_4_line_67 |  | 60 | 62 | 0.0078532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_354-9_0_4_line_68 |  | 60 | 63 | 0.015672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_354-9_0_4_line_69 |  | 64 | 65 | 0.00066991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_354-9_0_4_line_70 |  | 65 | 79 | 0.046102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_354-9_0_4_line_71 |  | 66 | 82 | 0.0024728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_354-9_0_4_line_72 |  | 67 | 68 | 0.015973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_354-9_0_4_line_73 |  | 67 | 69 | 0.0080188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_354-9_0_4_line_74 |  | 68 | 70 | 0.020341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_354-9_0_4_line_75 |  | 68 | 71 | 0.017087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_354-9_0_4_line_76 |  | 71 | 72 | 0.013225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_354-9_0_4_line_77 |  | 71 | 73 | 0.058175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_354-9_0_4_line_78 |  | 73 | 74 | 0.021394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_354-9_0_4_line_79 |  | 75 | 76 | 0.003223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_354-9_0_4_line_80 |  | 75 | 77 | 0.015543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_354-9_0_4_line_81 |  | 76 | 78 | 0.04425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_354-9_0_4_line_82 |  | 76 | 79 | 0.044724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_354-9_0_4_line_83 |  | 77 | 80 | 0.0077701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_354-9_0_4_line_84 |  | 79 | 81 | 0.0066834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_354-9_0_4_line_85 |  | 81 | 83 | 0.014965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_354-9_0_4_line_86 |  | 84 | 85 | 0.012654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_354-9_0_4_line_87 |  | 84 | 86 | 0.011879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_354-9_0_4_line_88 |  | 85 | 87 | 0.02481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_354-9_0_4_line_89 |  | 86 | 88 | 0.023784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_354-9_0_4_line_90 |  | 89 | 90 | 0.015877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_354-9_0_4_line_91 |  | 89 | 91 | 0.0038139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_354-9_0_4_line_92 |  | 90 | 92 | 0.015233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_354-9_0_4_line_93 |  | 90 | 93 | 0.010243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_354-9_0_4_line_94 |  | 93 | 94 | 0.011595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_354-9_0_4_line_95 |  | 93 | 95 | 0.049532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_354-9_0_4_line_96 |  | 95 | 97 | 0.01086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_354-9_0_4_line_97 |  | 95 | 98 | 0.011029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_354-9_0_4_trafo_58 | 0.63 MVA 20/0.4 kV | 99 | 48 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2598363.3675 | 1205497.8016 | 2598362.5075 | 1205499.6239 | 2598359.238 | 1205502.682 | 2598355.7706 | 1205505.3289 | 2598353.9386 | 1205508.3755 | 2598353.2332 | 1205510.9832
1 | 2598368.1911 | 1205480.6007 | 2598365.5627 | 1205491.4963 | 2598364.1342 | 1205496.1771 | 2598363.3675 | 1205497.8016
2 | 2598353.2332 | 1205510.9832 | 2598352.314 | 1205514.3812
3 | 2598368.1911 | 1205480.6007 | 2598388.0431 | 1205485.5978 | 2598393.2482 | 1205487.1147
4 | 2598368.1911 | 1205480.6007 | 2598365.3862 | 1205479.9568
5 | 2598351.9025 | 1205515.9025 | 2598352.314 | 1205514.3812
6 | 2598400.2503 | 1205489.1553 | 2598393.2482 | 1205487.1147
7 | 2598365.3862 | 1205479.9568 | 2598344.2008 | 1205475.0928
8 | 2598400.2503 | 1205489.1553 | 2598404.7064 | 1205490.4539
9 | 2598344.2008 | 1205475.0928 | 2598342.9464 | 1205474.8048 | 2598333.8694 | 1205472.8542
10 | 2598405.1141 | 1205490.5727 | 2598404.7064 | 1205490.4539
11 | 2598333.8694 | 1205472.8542 | 2598318.5418 | 1205469.5604
12 | 2597978.3924 | 1205364.4344 | 2597979.0701 | 1205364.1944 | 2597988.251 | 1205366.4258 | 2597993.1496 | 1205367.847 | 2597995.1874 | 1205366.2232 | 2597997.8325 | 1205361.1418 | 2597999.4662 | 1205356.8611 | 2597999.6699 | 1205351.9806 | 2597996.4052 | 1205346.7011 | 2597990.6908 | 1205339.7882 | 2597984.5433 | 1205333.976 | 2597984.6626 | 1205327.239 | 2597984.8127 | 1205326.5791
13 | 2597973.6286 | 1205376.2474 | 2597975.1931 | 1205369.6877 | 2597976.2107 | 1205365.2071 | 2597978.3924 | 1205364.4344
14 | 2597996.969 | 1205306.2938 | 2597991.5934 | 1205310.9721 | 2597986.6978 | 1205318.2889 | 2597984.8127 | 1205326.5791
15 | 2597973.6286 | 1205376.2474 | 2597987.8441 | 1205377.1317 | 2598003.406 | 1205378.8606 | 2598008.7896 | 1205379.7805
16 | 2597973.6286 | 1205376.2474 | 2597965.4522 | 1205375.5832 | 2597958.7169 | 1205374.7373
17 | 2597996.969 | 1205306.2938 | 2598001.5981 | 1205302.2651
18 | 2597996.969 | 1205306.2938 | 2597955.9611 | 1205270.7516
19 | 2598037.7408 | 1205385.644 | 2598022.7562 | 1205382.1668 | 2598008.7896 | 1205379.7805
20 | 2597942.816 | 1205371.2555 | 2597954.5071 | 1205374.2086 | 2597958.7169 | 1205374.7373
21 | 2598050.7096 | 1205388.9345 | 2598043.4226 | 1205386.9624 | 2598037.7408 | 1205385.644
22 | 2597942.816 | 1205371.2555 | 2597951.4351 | 1205347.2263
23 | 2597942.816 | 1205371.2555 | 2597931.239 | 1205368.2803
24 | 2598050.7096 | 1205388.9345 | 2598059.6651 | 1205391.358
25 | 2597931.239 | 1205368.2803 | 2597922.9553 | 1205365.4929 | 2597914.8643 | 1205361.4238
26 | 2597931.239 | 1205368.2803 | 2597926.6791 | 1205378.2652 | 2597921.4546 | 1205401.0684 | 2597920.6956 | 1205405.3932
27 | 2598405.1141 | 1205490.5727 | 2598407.7121 | 1205491.3298
28 | 2598407.8353 | 1205491.3657 | 2598407.7121 | 1205491.3298
29 | 2598059.6651 | 1205391.358 | 2598062.1724 | 1205392.0366
30 | 2598062.1724 | 1205392.0366 | 2598062.1724 | 1205392.0366 | 2598063.7049 | 1205392.556
31 | 2598341.3328 | 1205365.8681 | 2598340.5246 | 1205343.9653
32 | 2598341.3328 | 1205365.8681 | 2598341.5602 | 1205386.1854
33 | 2598341.3328 | 1205365.8681 | 2598362.5732 | 1205370.2554
34 | 2598333.0289 | 1205423.4019 | 2598338.7756 | 1205412.4832 | 2598341.3215 | 1205405.7121 | 2598341.595 | 1205404.6003 | 2598341.7544 | 1205403.533 | 2598341.5602 | 1205386.1854
35 | 2598362.5732 | 1205370.2554 | 2598370.7248 | 1205371.9391
36 | 2598333.0289 | 1205423.4019 | 2598336.9156 | 1205424.179 | 2598343.7079 | 1205425.5444 | 2598349.2644 | 1205426.6586
37 | 2598333.0289 | 1205423.4019 | 2598326.2374 | 1205437.0388
38 | 2598370.7248 | 1205371.9391 | 2598372.1303 | 1205372.2294 | 2598381.0419 | 1205374.9923
39 | 2598349.2644 | 1205426.6586 | 2598356.2599 | 1205428.0614
40 | 2598317.85 | 1205453.8813 | 2598323.5046 | 1205442.5262 | 2598326.2374 | 1205437.0388
41 | 2598389.8889 | 1205377.7351 | 2598381.0419 | 1205374.9923
42 | 2598089.8313 | 1205401.4102 | 2598063.7049 | 1205392.556
43 | 2598112.0334 | 1205408.6957 | 2598098.4177 | 1205404.3201 | 2598089.8313 | 1205401.4102
44 | 2598224.9365 | 1205486.5776 | 2598232.4264 | 1205476.3171
45 | 2598222.8811 | 1205489.3933 | 2598224.9365 | 1205486.5776
46 | 2598239.9028 | 1205466.0753 | 2598232.4264 | 1205476.3171
47 | 2598222.8811 | 1205489.3933 | 2598224.1146 | 1205494.0954
48 | 2598222.8811 | 1205489.3933 | 2598220.0984 | 1205492.707 | 2598219.2545 | 1205493.4855 | 2598218.1062 | 1205493.9306 | 2598216.8741 | 1205494.0199 | 2598215.6495 | 1205493.809 | 2598214.4705 | 1205493.3647 | 2598191.2893 | 1205478.3444
49 | 2598239.9028 | 1205466.0753 | 2598240.3662 | 1205464.0741 | 2598240.1753 | 1205461.6395 | 2598239.9844 | 1205459.2048 | 2598240.4552 | 1205456.6811 | 2598247.3792 | 1205441.4929
50 | 2598239.9028 | 1205466.0753 | 2598255.4845 | 1205478.4283
51 | 2598224.1146 | 1205494.0954 | 2598203.8338 | 1205579.5932
52 | 2598185.7459 | 1205474.7525 | 2598191.2893 | 1205478.3444
53 | 2598247.3792 | 1205441.4929 | 2598238.9889 | 1205437.2821 | 2598237.2394 | 1205436.4711 | 2598236.3687 | 1205436.0492
54 | 2598247.3792 | 1205441.4929 | 2598266.7708 | 1205451.0902
55 | 2598271.9606 | 1205491.4905 | 2598255.4845 | 1205478.4283
56 | 2598203.2248 | 1205580.4817 | 2598203.8338 | 1205579.5932
57 | 2598236.3687 | 1205436.0492 | 2598229.2142 | 1205432.5825 | 2598223.0072 | 1205430.0164 | 2598214.8454 | 1205427.2174 | 2598207.5585 | 1205425.2519 | 2598205.2263 | 1205424.6415
58 | 2598271.9606 | 1205491.4905 | 2598279.5254 | 1205482.1943 | 2598280.6096 | 1205480.728
59 | 2598203.2248 | 1205580.4817 | 2598200.8773 | 1205583.9072 | 2598195.7693 | 1205592.9027 | 2598190.2366 | 1205604.0615
60 | 2598183.6461 | 1205616.7417 | 2598187.2794 | 1205610.0258 | 2598190.2366 | 1205604.0615
61 | 2598182.5439 | 1205618.543 | 2598183.6461 | 1205616.7417
62 | 2598183.6461 | 1205616.7417 | 2598196.0899 | 1205620.8956 | 2598209.0572 | 1205620.8915 | 2598211.272 | 1205621.4837
63 | 2598182.5439 | 1205618.543 | 2598175.9251 | 1205612.2306 | 2598171.4454 | 1205611.8985 | 2598167.5068 | 1205615.0681
64 | 2598248.4541 | 1205633.2054 | 2598238.6298 | 1205629.8539 | 2598223.8433 | 1205624.8447 | 2598211.272 | 1205621.4837
65 | 2598292.7382 | 1205463.0576 | 2598300.8998 | 1205465.6011 | 2598310.8639 | 1205467.9105
66 | 2598292.7382 | 1205463.0576 | 2598286.0788 | 1205473.3319 | 2598280.6096 | 1205480.728
67 | 2598310.8639 | 1205467.9105 | 2598318.5418 | 1205469.5604
68 | 2598310.8639 | 1205467.9105 | 2598317.85 | 1205453.8813
69 | 2598204.5783 | 1205424.4718 | 2598205.2263 | 1205424.6415
70 | 2598159.0698 | 1205417.3741 | 2598192.2016 | 1205421.6881 | 2598200.1348 | 1205423.3088 | 2598204.5783 | 1205424.4718
71 | 2598358.6311 | 1205428.753 | 2598356.8284 | 1205428.1754 | 2598356.2599 | 1205428.0614
72 | 2598427.1621 | 1205497.7046 | 2598431.9176 | 1205482.4564
73 | 2598434.305 | 1205474.8013 | 2598431.9176 | 1205482.4564
74 | 2598427.1621 | 1205497.7046 | 2598409.7665 | 1205491.9285 | 2598407.8353 | 1205491.3657
75 | 2598443.3483 | 1205503.3144 | 2598432.2431 | 1205499.4597 | 2598427.1621 | 1205497.7046
76 | 2598443.3483 | 1205503.3144 | 2598439.2143 | 1205515.8779
77 | 2598497.1789 | 1205525.6788 | 2598478.3528 | 1205517.0124 | 2598457.0245 | 1205508.369 | 2598443.3483 | 1205503.3144
78 | 2598497.1789 | 1205525.6788 | 2598487.4188 | 1205544.7168
79 | 2598112.0334 | 1205408.6957 | 2598115.076 | 1205409.7842
80 | 2598112.0334 | 1205408.6957 | 2598118.4123 | 1205401.801 | 2598119.9331 | 1205400.8 | 2598123.6253 | 1205398.5394
81 | 2598096.7977 | 1205450.0789 | 2598111.8836 | 1205415.7107 | 2598115.076 | 1205409.7842
82 | 2598115.076 | 1205409.7842 | 2598127.3146 | 1205412.893 | 2598134.1374 | 1205414.3138 | 2598141.1426 | 1205415.4677 | 2598159.0698 | 1205417.3741
83 | 2598130.252 | 1205394.482 | 2598123.6253 | 1205398.5394
84 | 2598159.0698 | 1205417.3741 | 2598160.445 | 1205412.8823 | 2598161.5397 | 1205411.2255
85 | 2598174.5887 | 1205403.9062 | 2598164.186 | 1205409.6016 | 2598161.5397 | 1205411.2255
86 | 2598422.7438 | 1205391.3835 | 2598433.8489 | 1205397.4493
87 | 2598422.7438 | 1205391.3835 | 2598413.7073 | 1205386.4477 | 2598412.2254 | 1205385.8914
88 | 2598433.8489 | 1205397.4493 | 2598440.4378 | 1205401.0483 | 2598454.975 | 1205410.4307
89 | 2598412.2254 | 1205385.8914 | 2598393.375 | 1205378.8159 | 2598389.8889 | 1205377.7351
90 | 2597915.636 | 1205400.4479 | 2597908.9077 | 1205414.8284
91 | 2597907.2914 | 1205418.2829 | 2597908.9077 | 1205414.8284
92 | 2597915.636 | 1205400.4479 | 2597901.7932 | 1205394.0891
93 | 2597915.636 | 1205400.4479 | 2597921.4546 | 1205401.0684 | 2597920.6956 | 1205405.3932
94 | 2597932.0898 | 1205407.7126 | 2597920.6956 | 1205405.3932
95 | 2597910.4074 | 1205453.8345 | 2597916.0116 | 1205429.4747 | 2597920.6956 | 1205405.3932
96 | 2597921.0941 | 1205455.9318 | 2597910.4074 | 1205453.8345
97 | 2597910.4074 | 1205453.8345 | 2597908.6761 | 1205461.3503 | 2597907.5209 | 1205464.4593

## bus_geodata
| x | y | coords
0 | 2598363.3675 | 1205497.8016
1 | 2598353.2332 | 1205510.9832
2 | 2598368.1911 | 1205480.6007
3 | 2598352.314 | 1205514.3812
4 | 2598393.2482 | 1205487.1147
5 | 2598365.3862 | 1205479.9568
6 | 2598351.9025 | 1205515.9025
7 | 2598400.2503 | 1205489.1553
8 | 2598344.2008 | 1205475.0928
9 | 2598404.7064 | 1205490.4539
10 | 2598333.8694 | 1205472.8542
11 | 2597978.3924 | 1205364.4344
12 | 2597984.8127 | 1205326.5791
13 | 2597973.6286 | 1205376.2474
14 | 2597996.969 | 1205306.2938
15 | 2598008.7896 | 1205379.7805
16 | 2597958.7169 | 1205374.7373
17 | 2598001.5981 | 1205302.2651
18 | 2597955.9611 | 1205270.7516
19 | 2598037.7408 | 1205385.644
20 | 2597942.816 | 1205371.2555
21 | 2598050.7096 | 1205388.9345
22 | 2597951.4351 | 1205347.2263
23 | 2597931.239 | 1205368.2803
24 | 2598405.1141 | 1205490.5727
25 | 2598407.7121 | 1205491.3298
26 | 2598059.6651 | 1205391.358
27 | 2598062.1724 | 1205392.0366
28 | 2598340.5246 | 1205343.9653
29 | 2598341.3328 | 1205365.8681
30 | 2598341.5602 | 1205386.1854
31 | 2598362.5732 | 1205370.2554
32 | 2598333.0289 | 1205423.4019
33 | 2598370.7248 | 1205371.9391
34 | 2598349.2644 | 1205426.6586
35 | 2598326.2374 | 1205437.0388
36 | 2598381.0419 | 1205374.9923
37 | 2598063.7049 | 1205392.556
38 | 2598089.8313 | 1205401.4102
39 | 2598224.9365 | 1205486.5776
40 | 2598232.4264 | 1205476.3171
41 | 2598222.8811 | 1205489.3933
42 | 2598239.9028 | 1205466.0753
43 | 2598224.1146 | 1205494.0954
44 | 2598191.2893 | 1205478.3444
45 | 2598247.3792 | 1205441.4929
46 | 2598255.4845 | 1205478.4283
47 | 2598203.8338 | 1205579.5932
48 | 2598185.7459 | 1205474.7525
49 | 2598236.3687 | 1205436.0492
50 | 2598266.7708 | 1205451.0902
51 | 2598271.9606 | 1205491.4905
52 | 2598203.2248 | 1205580.4817
53 | 2598190.2366 | 1205604.0615
54 | 2598183.6461 | 1205616.7417
55 | 2598182.5439 | 1205618.543
56 | 2598211.272 | 1205621.4837
57 | 2598248.4541 | 1205633.2054
58 | 2598167.5068 | 1205615.0682
59 | 2598292.7382 | 1205463.0576
60 | 2598310.8639 | 1205467.9105
61 | 2598280.6096 | 1205480.728
62 | 2598318.5418 | 1205469.5604
63 | 2598317.85 | 1205453.8813
64 | 2598205.2263 | 1205424.6415
65 | 2598204.5783 | 1205424.4718
66 | 2598356.2599 | 1205428.0614
67 | 2598431.9176 | 1205482.4564
68 | 2598427.1621 | 1205497.7046
69 | 2598434.305 | 1205474.8013
70 | 2598407.8353 | 1205491.3657
71 | 2598443.3483 | 1205503.3144
72 | 2598439.2143 | 1205515.8779
73 | 2598497.1789 | 1205525.6788
74 | 2598487.4188 | 1205544.7168
75 | 2598112.0334 | 1205408.6957
76 | 2598115.076 | 1205409.7842
77 | 2598123.6253 | 1205398.5394
78 | 2598096.7977 | 1205450.0789
79 | 2598159.0698 | 1205417.3741
80 | 2598130.252 | 1205394.482
81 | 2598161.5397 | 1205411.2255
82 | 2598358.6311 | 1205428.753
83 | 2598174.5887 | 1205403.9062
84 | 2598422.7438 | 1205391.3835
85 | 2598433.8489 | 1205397.4493
86 | 2598412.2254 | 1205385.8914
87 | 2598454.975 | 1205410.4307
88 | 2598389.8889 | 1205377.7351
89 | 2597908.9077 | 1205414.8284
90 | 2597915.636 | 1205400.4479
91 | 2597907.2914 | 1205418.2829
92 | 2597901.7932 | 1205394.0891
93 | 2597920.6956 | 1205405.3932
94 | 2597932.0898 | 1205407.7126
95 | 2597910.4074 | 1205453.8345
96 | 2597914.8643 | 1205361.4238
97 | 2597921.0941 | 1205455.9318
98 | 2597907.5209 | 1205464.4593
99 | 2598222.8811 | 1205489.3933

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1