## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4024-6_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4024-6_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4024-6_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4024-6_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4024-6_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4024-6_0_2_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_4024-6_0_2_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_4024-6_0_2_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_4024-6_0_2_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_4024-6_0_2_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_4024-6_0_2_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_4024-6_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_4024-6_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_4024-6_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_4024-6_0_2_node_99 | 0.4 | n |  | TRUE
15 | bus_LV_4024-6_0_2_node_70 | 0.4 | n |  | TRUE
16 | bus_LV_4024-6_0_2_node_100 | 0.4 | n |  | TRUE
17 | bus_LV_4024-6_0_2_node_97 | 0.4 | n |  | TRUE
18 | bus_LV_4024-6_0_2_node_68 | 0.4 | n |  | TRUE
19 | bus_LV_4024-6_0_2_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_4024-6_0_2_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_4024-6_0_2_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_4024-6_0_2_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_4024-6_0_2_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_4024-6_0_2_node_65 | 0.4 | n |  | TRUE
25 | bus_LV_4024-6_0_2_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_4024-6_0_2_node_64 | 0.4 | n |  | TRUE
27 | bus_LV_4024-6_0_2_node_47 | 0.4 | n |  | TRUE
28 | bus_LV_4024-6_0_2_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_4024-6_0_2_node_78 | 0.4 | n |  | TRUE
30 | bus_LV_4024-6_0_2_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_4024-6_0_2_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_4024-6_0_2_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_4024-6_0_2_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_4024-6_0_2_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_4024-6_0_2_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_4024-6_0_2_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_4024-6_0_2_node_72 | 0.4 | n |  | TRUE
38 | bus_LV_4024-6_0_2_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_4024-6_0_2_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_4024-6_0_2_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_4024-6_0_2_node_71 | 0.4 | n |  | TRUE
42 | bus_LV_4024-6_0_2_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_4024-6_0_2_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_4024-6_0_2_node_21 | 0.4 | n |  | TRUE
45 | bus_LV_4024-6_0_2_node_22 | 0.4 | n |  | TRUE
46 | bus_LV_4024-6_0_2_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_4024-6_0_2_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_4024-6_0_2_node_61 | 0.4 | n |  | TRUE
49 | bus_LV_4024-6_0_2_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_4024-6_0_2_node_79 | 0.4 | n |  | TRUE
51 | bus_LV_4024-6_0_2_node_76 | 0.4 | n |  | TRUE
52 | bus_LV_4024-6_0_2_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_4024-6_0_2_node_63 | 0.4 | n |  | TRUE
54 | bus_LV_4024-6_0_2_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_4024-6_0_2_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_4024-6_0_2_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_4024-6_0_2_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_4024-6_0_2_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_4024-6_0_2_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_4024-6_0_2_node_95 | 0.4 | n |  | TRUE
61 | bus_LV_4024-6_0_2_node_75 | 0.4 | n |  | TRUE
62 | bus_LV_4024-6_0_2_node_96 | 0.4 | n |  | TRUE
63 | bus_LV_4024-6_0_2_node_90 | 0.4 | n |  | TRUE
64 | bus_LV_4024-6_0_2_node_58 | 0.4 | n |  | TRUE
65 | bus_LV_4024-6_0_2_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_4024-6_0_2_node_42 | 0.4 | n |  | TRUE
67 | bus_LV_4024-6_0_2_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_4024-6_0_2_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_4024-6_0_2_node_80 | 0.4 | n |  | TRUE
70 | bus_LV_4024-6_0_2_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_4024-6_0_2_node_82 | 0.4 | n |  | TRUE
72 | bus_LV_4024-6_0_2_node_86 | 0.4 | n |  | TRUE
73 | bus_LV_4024-6_0_2_node_87 | 0.4 | n |  | TRUE
74 | bus_LV_4024-6_0_2_node_85 | 0.4 | n |  | TRUE
75 | bus_LV_4024-6_0_2_node_81 | 0.4 | n |  | TRUE
76 | bus_LV_4024-6_0_2_node_49 | 0.4 | n |  | TRUE
77 | bus_LV_4024-6_0_2_node_50 | 0.4 | n |  | TRUE
78 | bus_LV_4024-6_0_2_node_51 | 0.4 | n |  | TRUE
79 | bus_LV_4024-6_0_2_node_52 | 0.4 | n |  | TRUE
80 | bus_LV_4024-6_0_2_node_54 | 0.4 | n |  | TRUE
81 | bus_LV_4024-6_0_2_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_4024-6_0_2_node_92 | 0.4 | n |  | TRUE
83 | bus_LV_4024-6_0_2_node_57 | 0.4 | n |  | TRUE
84 | bus_LV_4024-6_0_2_node_91 | 0.4 | n |  | TRUE
85 | bus_LV_4024-6_0_2_node_55 | 0.4 | n |  | TRUE
86 | bus_LV_4024-6_0_2_node_59 | 0.4 | n |  | TRUE
87 | bus_LV_4024-6_0_2_node_101 | 0.4 | n |  | TRUE
88 | bus_LV_4024-6_0_2_node_66 | 0.4 | n |  | TRUE
89 | bus_LV_4024-6_0_2_node_67 | 0.4 | n |  | TRUE
90 | bus_LV_4024-6_0_2_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_4024-6_0_2_node_98 | 0.4 | n |  | TRUE
92 | bus_LV_4024-6_0_2_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_4024-6_0_2_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_4024-6_0_2_node_77 | 0.4 | n |  | TRUE
95 | bus_LV_4024-6_0_2_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_4024-6_0_2_node_93 | 0.4 | n |  | TRUE
97 | bus_LV_4024-6_0_2_node_94 | 0.4 | n |  | TRUE
98 | bus_LV_4024-6_0_2_node_88 | 0.4 | n |  | TRUE
99 | bus_MV_421_0_node_15 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4024-6_0_2_load_0 | 0 | 0.0047316 | 0.0011858 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4024-6_0_2_load_1 | 1 | 0.0031011 | 0.00077721 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4024-6_0_2_load_2 | 2 | 0.0049165 | 0.0012322 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4024-6_0_2_load_3 | 3 | 0.0019196 | 0.00048111 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4024-6_0_2_load_4 | 4 | 0.007156 | 0.0017935 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4024-6_0_2_load_29 | 6 | 0.0085481 | 0.0021424 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4024-6_0_2_load_25 | 7 | 0.0025462 | 0.00063813 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4024-6_0_2_load_26 | 8 | 0.0024026 | 0.00060214 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4024-6_0_2_load_30 | 9 | 0.0070717 | 0.0017723 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4024-6_0_2_load_5 | 10 | 0.0031573 | 0.0007913 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4024-6_0_2_load_6 | 11 | 0.0024245 | 0.00060763 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4024-6_0_2_load_7 | 12 | 0.0056732 | 0.0014218 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4024-6_0_2_load_99 | 14 | 0.0020181 | 0.00050578 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4024-6_0_2_load_100 | 16 | 0.0020428 | 0.00051196 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4024-6_0_2_load_97 | 17 | 0.0026529 | 0.00066488 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4024-6_0_2_load_9 | 19 | 0.0041023 | 0.0010281 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4024-6_0_2_load_10 | 20 | 0.0029199 | 0.0007318 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4024-6_0_2_load_11 | 21 | 0.002613 | 0.00065487 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4024-6_0_2_load_12 | 22 | 0.0021738 | 0.00054479 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4024-6_0_2_load_13 | 23 | 0.0050058 | 0.0012546 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4024-6_0_2_load_65 | 24 | 0.0021735 | 0.00054473 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4024-6_0_2_load_34 | 25 | 0.0054668 | 0.0013701 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4024-6_0_2_load_64 | 26 | 0.0033303 | 0.00083464 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4024-6_0_2_load_47 | 27 | 0.0021258 | 0.00053277 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4024-6_0_2_load_15 | 30 | 0.0029189 | 0.00073155 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4024-6_0_2_load_16 | 31 | 0.0010972 | 0.00027498 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4024-6_0_2_load_18 | 33 | 0.0040324 | 0.0010106 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4024-6_0_2_load_20 | 35 | 0.0039771 | 0.00099675 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4024-6_0_2_load_32 | 36 | 0.001146 | 0.00028722 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4024-6_0_2_load_72 | 37 | 0.0022063 | 0.00055296 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4024-6_0_2_load_27 | 38 | 0.0015067 | 0.0003776 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4024-6_0_2_load_40 | 39 | 0.0025297 | 0.000634 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4024-6_0_2_load_31 | 40 | 0.0020362 | 0.00051031 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4024-6_0_2_load_71 | 41 | 0.00088222 | 0.0002211 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4024-6_0_2_load_28 | 42 | 0.0013423 | 0.0003364 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4024-6_0_2_load_41 | 43 | 0.0067364 | 0.0016883 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4024-6_0_2_load_21 | 44 | 0.0022477 | 0.00056333 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4024-6_0_2_load_22 | 45 | 0.0021522 | 0.0005394 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4024-6_0_2_load_23 | 46 | 0.0021726 | 0.00054452 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4024-6_0_2_load_61 | 48 | 0.0033359 | 0.00083604 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4024-6_0_2_load_43 | 49 | 0.0039091 | 0.00097971 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4024-6_0_2_load_79 | 50 | 0.0049103 | 0.0012306 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4024-6_0_2_load_76 | 51 | 0.0033361 | 0.00083611 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4024-6_0_2_load_62 | 52 | 0.0041037 | 0.0010285 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4024-6_0_2_load_63 | 53 | 0.0047793 | 0.0011978 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4024-6_0_2_load_48 | 54 | 0.0026145 | 0.00065525 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4024-6_0_2_load_35 | 55 | 0.002415 | 0.00060525 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4024-6_0_2_load_36 | 56 | 0.0045948 | 0.0011516 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4024-6_0_2_load_38 | 58 | 0.0017228 | 0.00043177 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4024-6_0_2_load_39 | 59 | 0.0027269 | 0.00068342 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4024-6_0_2_load_95 | 60 | 0.005833 | 0.0014619 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4024-6_0_2_load_96 | 62 | 0.0017877 | 0.00044804 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4024-6_0_2_load_90 | 63 | 0.0027276 | 0.00068359 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4024-6_0_2_load_56 | 65 | 0.0021733 | 0.00054469 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4024-6_0_2_load_42 | 66 | 0.0033475 | 0.00083896 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4024-6_0_2_load_44 | 67 | 0.0042288 | 0.0010598 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4024-6_0_2_load_80 | 69 | 0.0054546 | 0.001367 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4024-6_0_2_load_53 | 70 | 0.0033369 | 0.0008363 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4024-6_0_2_load_87 | 73 | 0.0037398 | 0.00093727 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4024-6_0_2_load_85 | 74 | 0.0037398 | 0.00093729 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4024-6_0_2_load_81 | 75 | 0.0032724 | 0.00082015 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4024-6_0_2_load_49 | 76 | 0.0021746 | 0.00054501 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4024-6_0_2_load_50 | 77 | 0.0021739 | 0.00054484 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4024-6_0_2_load_52 | 79 | 0.0043466 | 0.0010894 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4024-6_0_2_load_60 | 81 | 0.0024453 | 0.00061285 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4024-6_0_2_load_92 | 82 | 0.0031579 | 0.00079143 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4024-6_0_2_load_91 | 84 | 0.0031596 | 0.00079186 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4024-6_0_2_load_55 | 85 | 0.0021726 | 0.00054451 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4024-6_0_2_load_101 | 87 | 0.0087619 | 0.002196 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4024-6_0_2_load_66 | 88 | 0.006702 | 0.0016797 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4024-6_0_2_load_67 | 89 | 0.003738 | 0.00093683 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4024-6_0_2_load_98 | 91 | 0.0023936 | 0.0005999 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4024-6_0_2_load_73 | 92 | 0.00088195 | 0.00022104 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4024-6_0_2_load_77 | 94 | 0.0056152 | 0.0014073 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4024-6_0_2_load_83 | 95 | 0.0076114 | 0.0019076 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4024-6_0_2_load_93 | 96 | 0.0031566 | 0.00079113 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4024-6_0_2_load_94 | 97 | 0.0040413 | 0.0010128 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4024-6_0_2_load_88 | 98 | 0.0037052 | 0.00092861 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4024-6_0_2_line_0 |  | 0 | 1 | 0.0046594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4024-6_0_2_line_1 |  | 0 | 2 | 0.011466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4024-6_0_2_line_2 |  | 1 | 3 | 0.015604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4024-6_0_2_line_3 |  | 2 | 4 | 0.016009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4024-6_0_2_line_4 |  | 3 | 5 | 0.025025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4024-6_0_2_line_5 |  | 4 | 6 | 0.015942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4024-6_0_2_line_6 |  | 5 | 7 | 0.016377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4024-6_0_2_line_7 |  | 5 | 8 | 0.014869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4024-6_0_2_line_8 |  | 6 | 9 | 0.015804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4024-6_0_2_line_9 |  | 7 | 28 | 0.0055132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4024-6_0_2_line_10 |  | 8 | 29 | 0.026666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4024-6_0_2_line_11 |  | 9 | 52 | 0.0021217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4024-6_0_2_line_12 |  | 10 | 11 | 0.0048511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4024-6_0_2_line_13 |  | 10 | 12 | 0.0098768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4024-6_0_2_line_14 |  | 11 | 13 | 0.015195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4024-6_0_2_line_15 |  | 13 | 14 | 0.027077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4024-6_0_2_line_16 |  | 13 | 15 | 0.007489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4024-6_0_2_line_17 |  | 14 | 16 | 0.0081292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4024-6_0_2_line_18 |  | 15 | 17 | 0.031585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4024-6_0_2_line_19 |  | 15 | 18 | 0.045949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4024-6_0_2_line_20 |  | 16 | 86 | 0.018661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4024-6_0_2_line_21 |  | 17 | 91 | 0.0018888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4024-6_0_2_line_22 |  | 18 | 88 | 0.028867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4024-6_0_2_line_23 |  | 19 | 20 | 0.027385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4024-6_0_2_line_24 |  | 19 | 21 | 0.0025039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4024-6_0_2_line_25 |  | 20 | 22 | 0.00087131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4024-6_0_2_line_26 |  | 21 | 23 | 0.0013604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4024-6_0_2_line_27 |  | 22 | 24 | 0.0036119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4024-6_0_2_line_28 |  | 23 | 25 | 0.022708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4024-6_0_2_line_29 |  | 24 | 26 | 0.024975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4024-6_0_2_line_30 |  | 25 | 27 | 0.0035292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4024-6_0_2_line_31 |  | 26 | 64 | 0.0090697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4024-6_0_2_line_32 |  | 27 | 54 | 0.020647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4024-6_0_2_line_33 |  | 28 | 47 | 0.045338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_4024-6_0_2_line_34 |  | 28 | 46 | 0.014196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_4024-6_0_2_line_35 |  | 29 | 50 | 0.01675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4024-6_0_2_line_36 |  | 29 | 51 | 0.019654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4024-6_0_2_line_37 |  | 30 | 31 | 0.0088603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4024-6_0_2_line_38 |  | 30 | 32 | 0.034088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4024-6_0_2_line_39 |  | 31 | 33 | 0.028716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4024-6_0_2_line_40 |  | 32 | 34 | 0.025798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4024-6_0_2_line_41 |  | 32 | 35 | 0.012864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4024-6_0_2_line_42 |  | 33 | 36 | 0.015823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4024-6_0_2_line_43 |  | 33 | 37 | 0.019529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4024-6_0_2_line_44 |  | 34 | 38 | 0.011387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4024-6_0_2_line_45 |  | 35 | 39 | 0.02511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4024-6_0_2_line_46 |  | 36 | 40 | 0.0071391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4024-6_0_2_line_47 |  | 37 | 41 | 0.024406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4024-6_0_2_line_48 |  | 38 | 42 | 0.041337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4024-6_0_2_line_49 |  | 39 | 43 | 0.0018657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4024-6_0_2_line_50 |  | 41 | 92 | 0.0030794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4024-6_0_2_line_51 |  | 43 | 64 | 0.022923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4024-6_0_2_line_52 |  | 44 | 45 | 0.019098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_4024-6_0_2_line_53 |  | 44 | 46 | 0.0067621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_4024-6_0_2_line_54 |  | 47 | 48 | 0.014487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_4024-6_0_2_line_55 |  | 47 | 49 | 0.0023869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4024-6_0_2_line_56 |  | 48 | 70 | 0.006319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4024-6_0_2_line_57 |  | 49 | 66 | 0.022921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4024-6_0_2_line_58 |  | 50 | 95 | 0.027115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4024-6_0_2_line_59 |  | 51 | 94 | 0.01999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4024-6_0_2_line_60 |  | 52 | 53 | 0.025193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4024-6_0_2_line_61 |  | 53 | 61 | 0.010428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4024-6_0_2_line_62 |  | 55 | 56 | 0.0016333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4024-6_0_2_line_63 |  | 55 | 57 | 0.013171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4024-6_0_2_line_64 |  | 56 | 58 | 0.01508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4024-6_0_2_line_65 |  | 57 | 59 | 0.0025926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4024-6_0_2_line_66 |  | 58 | 60 | 0.022264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4024-6_0_2_line_67 |  | 59 | 61 | 0.016198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4024-6_0_2_line_68 |  | 60 | 62 | 0.0034505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4024-6_0_2_line_69 |  | 61 | 63 | 0.037755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4024-6_0_2_line_70 |  | 63 | 93 | 0.013072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4024-6_0_2_line_71 |  | 64 | 65 | 0.019204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4024-6_0_2_line_72 |  | 65 | 85 | 0.023465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4024-6_0_2_line_73 |  | 66 | 67 | 0.022281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4024-6_0_2_line_74 |  | 67 | 68 | 0.015325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4024-6_0_2_line_75 |  | 68 | 69 | 0.013889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4024-6_0_2_line_76 |  | 69 | 75 | 0.029349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4024-6_0_2_line_77 |  | 70 | 78 | 0.022914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4024-6_0_2_line_78 |  | 71 | 72 | 0.025009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4024-6_0_2_line_79 |  | 71 | 73 | 0.013546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4024-6_0_2_line_80 |  | 71 | 74 | 0.017169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4024-6_0_2_line_81 |  | 72 | 96 | 0.010208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4024-6_0_2_line_82 |  | 72 | 84 | 0.011406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4024-6_0_2_line_83 |  | 73 | 97 | 0.0014994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4024-6_0_2_line_84 |  | 75 | 90 | 0.035476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4024-6_0_2_line_85 |  | 76 | 77 | 0.00014935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4024-6_0_2_line_86 |  | 76 | 78 | 0.014366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4024-6_0_2_line_87 |  | 77 | 79 | 0.017755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4024-6_0_2_line_88 |  | 78 | 80 | 0.008763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4024-6_0_2_line_89 |  | 80 | 81 | 0.017247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4024-6_0_2_line_90 |  | 80 | 82 | 0.019234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4024-6_0_2_line_91 |  | 81 | 83 | 0.012873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4024-6_0_2_line_92 |  | 82 | 84 | 0.022075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4024-6_0_2_line_93 |  | 83 | 86 | 0.007449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4024-6_0_2_line_94 |  | 83 | 85 | 0.012818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4024-6_0_2_line_95 |  | 86 | 87 | 0.040251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4024-6_0_2_line_96 |  | 89 | 90 | 0.027451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4024-6_0_2_line_97 |  | 93 | 98 | 0.014451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4024-6_0_2_trafo_22 | 0.63 MVA 20/0.4 kV | 99 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2660932.4866 | 1257274.9232 | 2660930.009 | 1257278.8694
1 | 2660932.4866 | 1257274.9232 | 2660932.8138 | 1257274.4021 | 2660935.9204 | 1257264.0053
2 | 2660930.009 | 1257278.8694 | 2660921.7119 | 1257292.0846
3 | 2660935.9204 | 1257264.0053 | 2660940.5036 | 1257248.6668
4 | 2660908.4052 | 1257313.279 | 2660921.7119 | 1257292.0846
5 | 2660945.0676 | 1257233.3923 | 2660940.5036 | 1257248.6668
6 | 2660908.4052 | 1257313.279 | 2660899.6962 | 1257327.1481
7 | 2660908.4052 | 1257313.279 | 2660897.4737 | 1257303.1991
8 | 2660949.5923 | 1257218.2494 | 2660945.0676 | 1257233.3923
9 | 2660897.5558 | 1257332.2255 | 2660899.574 | 1257327.3427 | 2660899.6962 | 1257327.1481
10 | 2660877.8701 | 1257285.1225 | 2660897.4737 | 1257303.1991
11 | 2660949.5923 | 1257218.2494 | 2660950.1998 | 1257216.2165
12 | 2660969.8317 | 1257463.5703 | 2660965.0349 | 1257464.2942
13 | 2660979.5979 | 1257462.0964 | 2660969.8317 | 1257463.5703
14 | 2660950.0098 | 1257466.5617 | 2660965.0349 | 1257464.2942
15 | 2660950.0098 | 1257466.5617 | 2660948.7111 | 1257447.7015 | 2660949.2856 | 1257439.5492
16 | 2660950.0098 | 1257466.5617 | 2660950.3578 | 1257471.5689 | 2660950.2797 | 1257474.0366
17 | 2660949.2856 | 1257439.5492 | 2660949.8571 | 1257431.4401
18 | 2660950.2797 | 1257474.0366 | 2660927.1827 | 1257467.6054 | 2660927.8105 | 1257460.0223
19 | 2660950.2797 | 1257474.0366 | 2660949.6846 | 1257493.7446 | 2660948.5995 | 1257512.7138 | 2660948.4648 | 1257519.9398
20 | 2660954.1164 | 1257413.3879 | 2660950.2741 | 1257425.5238 | 2660949.8571 | 1257431.4401
21 | 2660927.9663 | 1257458.14 | 2660927.8105 | 1257460.0223
22 | 2660948.4648 | 1257519.9398 | 2660919.6647 | 1257517.979
23 | 2661015.9637 | 1257300.6139 | 2661001.3888 | 1257323.7978
24 | 2661017.2963 | 1257298.4941 | 2661015.9637 | 1257300.6139
25 | 2661001.3888 | 1257323.7978 | 2661000.925 | 1257324.5355
26 | 2661017.2963 | 1257298.4941 | 2661018.0203 | 1257297.3424
27 | 2661000.925 | 1257324.5355 | 2660999.0027 | 1257327.5933
28 | 2661030.1063 | 1257278.1176 | 2661018.0203 | 1257297.3424
29 | 2660987.3856 | 1257349.6785 | 2660996.1304 | 1257332.1621 | 2660999.0027 | 1257327.5933
30 | 2661030.1063 | 1257278.1176 | 2661030.1063 | 1257278.1176 | 2661032.5462 | 1257275.5677
31 | 2660983.3344 | 1257357.7932 | 2660987.3856 | 1257349.6785
32 | 2661032.5462 | 1257275.5677 | 2661043.4228 | 1257264.2004 | 2661047.2252 | 1257261.0869
33 | 2660880.2419 | 1257374.1443 | 2660897.5558 | 1257332.2255
34 | 2660897.5558 | 1257332.2255 | 2660911.2113 | 1257336.1058
35 | 2660877.8701 | 1257285.1225 | 2660865.3698 | 1257273.9735
36 | 2660877.8701 | 1257285.1225 | 2660867.759 | 1257296.0709 | 2660863.1239 | 1257297.1159
37 | 2661065.4109 | 1257354.5306 | 2661059.5854 | 1257361.2065
38 | 2661037.1732 | 1257386.891 | 2661059.5854 | 1257361.2065
39 | 2661084.2913 | 1257332.8935 | 2661065.4109 | 1257354.5306
40 | 2661051.3688 | 1257408.3416 | 2661041.593 | 1257395.5428 | 2661037.1732 | 1257386.891
41 | 2661037.1732 | 1257386.891 | 2661027.4718 | 1257378.4435
42 | 2661084.2913 | 1257332.8935 | 2661094.6973 | 1257320.9736
43 | 2661084.2913 | 1257332.8935 | 2661087.705 | 1257336.0198 | 2661090.309 | 1257337.9592 | 2661101.1841 | 1257342.1456
44 | 2661051.3688 | 1257408.3416 | 2661061.5331 | 1257403.2094 | 2661061.5331 | 1257403.2094
45 | 2661027.4718 | 1257378.4435 | 2661013.2144 | 1257366.0291 | 2661007.232 | 1257364.3801
46 | 2661099.3623 | 1257315.5705 | 2661098.8275 | 1257316.2425 | 2661094.6973 | 1257320.9736
47 | 2661123.9609 | 1257350.9134 | 2661101.1841 | 1257342.1456
48 | 2661102.7513 | 1257404.615 | 2661085.2001 | 1257402.6419 | 2661069.2199 | 1257402.8884 | 2661061.5331 | 1257403.2094
49 | 2661007.232 | 1257364.3801 | 2661005.4333 | 1257363.8843
50 | 2661123.9609 | 1257350.9134 | 2661126.8347 | 1257352.0197
51 | 2660983.3344 | 1257357.7932 | 2661005.4333 | 1257363.8843
52 | 2660932.4582 | 1257336.5698 | 2660930.9294 | 1257341.7089 | 2660917.7159 | 1257337.9541
53 | 2660911.2113 | 1257336.1058 | 2660917.7159 | 1257337.9541
54 | 2660880.2419 | 1257374.1443 | 2660893.5885 | 1257379.7788
55 | 2660880.2419 | 1257374.1443 | 2660879.2635 | 1257376.3214
56 | 2660893.5885 | 1257379.7788 | 2660899.4099 | 1257382.2364
57 | 2660870.0526 | 1257397.2927 | 2660870.3335 | 1257396.1916 | 2660879.2635 | 1257376.3214
58 | 2660865.3698 | 1257273.9735 | 2660854.1845 | 1257263.9972 | 2660845.1338 | 1257255.926
59 | 2660863.1239 | 1257297.1159 | 2660853.845 | 1257299.208 | 2660844.0036 | 1257295.6095
60 | 2660950.1998 | 1257216.2165 | 2660957.4123 | 1257192.0784
61 | 2660960.3972 | 1257182.0862 | 2660958.5697 | 1257188.2051 | 2660957.4123 | 1257192.0784
62 | 2660980.5159 | 1257177.9658 | 2660981.5251 | 1257179.2499
63 | 2660972.3773 | 1257167.6102 | 2660980.5159 | 1257177.9658
64 | 2660990.8431 | 1257191.1062 | 2660981.5251 | 1257179.2499
65 | 2660972.3773 | 1257167.6102 | 2660970.7243 | 1257169.6076
66 | 2660990.8431 | 1257191.1062 | 2661013.1053 | 1257190.8353
67 | 2660960.3972 | 1257182.0862 | 2660970.7243 | 1257169.6076
68 | 2661015.7671 | 1257193.0309 | 2661013.1053 | 1257190.8353
69 | 2660960.3972 | 1257182.0862 | 2660938.1956 | 1257151.5488
70 | 2660930.0971 | 1257141.3118 | 2660933.348 | 1257144.8811 | 2660938.1956 | 1257151.5488
71 | 2660983.3344 | 1257357.7932 | 2660973.9991 | 1257374.5754
72 | 2660962.5923 | 1257395.0818 | 2660973.9991 | 1257374.5754
73 | 2660870.0526 | 1257397.2927 | 2660864.5445 | 1257418.882
74 | 2660860.7559 | 1257433.7313 | 2660864.5445 | 1257418.882
75 | 2660860.7559 | 1257433.7313 | 2660857.3432 | 1257447.1947
76 | 2660857.3432 | 1257447.1947 | 2660850.132 | 1257475.6435
77 | 2660920.5201 | 1257391.1485 | 2660899.4099 | 1257382.2364
78 | 2660912.1917 | 1257444.2899 | 2660887.9013 | 1257438.0468
79 | 2660887.9013 | 1257438.0468 | 2660884.9209 | 1257451.2606
80 | 2660887.9013 | 1257438.0468 | 2660892.04 | 1257421.3844
81 | 2660910.0155 | 1257454.2636 | 2660912.1917 | 1257444.2899
82 | 2660912.1917 | 1257444.2899 | 2660914.6138 | 1257433.1443
83 | 2660884.591 | 1257452.7233 | 2660884.9209 | 1257451.2606
84 | 2660841.4152 | 1257510.0319 | 2660850.132 | 1257475.6435
85 | 2660926.3008 | 1257377.8344 | 2660926.2413 | 1257377.9714
86 | 2660920.5201 | 1257391.1485 | 2660926.2413 | 1257377.9714
87 | 2660933.3718 | 1257361.5483 | 2660926.3008 | 1257377.8344
88 | 2660928.6133 | 1257394.5675 | 2660920.5201 | 1257391.1485
89 | 2660928.6133 | 1257394.5675 | 2660944.5016 | 1257401.2762
90 | 2660928.6133 | 1257394.5675 | 2660920.3161 | 1257411.9204
91 | 2660956.3611 | 1257406.2837 | 2660944.5016 | 1257401.2762
92 | 2660914.6138 | 1257433.1443 | 2660918.3179 | 1257416.0993 | 2660920.3161 | 1257411.9204
93 | 2660956.3611 | 1257406.2837 | 2660954.1164 | 1257413.3879
94 | 2660956.3611 | 1257406.2837 | 2660962.5923 | 1257395.0818
95 | 2660954.1164 | 1257413.3879 | 2660992.8072 | 1257424.8835
96 | 2660841.4152 | 1257510.0319 | 2660863.9485 | 1257512.6098 | 2660868.6714 | 1257513.2854
97 | 2660930.0971 | 1257141.3118 | 2660919.7262 | 1257151.3754

## bus_geodata
| x | y | coords
0 | 2660932.4866 | 1257274.9232
1 | 2660930.009 | 1257278.8694
2 | 2660935.9204 | 1257264.0053
3 | 2660921.7119 | 1257292.0846
4 | 2660940.5036 | 1257248.6668
5 | 2660908.4052 | 1257313.279
6 | 2660945.0676 | 1257233.3923
7 | 2660899.6962 | 1257327.1481
8 | 2660897.4737 | 1257303.1991
9 | 2660949.5923 | 1257218.2494
10 | 2660969.8317 | 1257463.5703
11 | 2660965.0349 | 1257464.2942
12 | 2660979.5979 | 1257462.0964
13 | 2660950.0098 | 1257466.5617
14 | 2660949.2856 | 1257439.5492
15 | 2660950.2797 | 1257474.0366
16 | 2660949.8571 | 1257431.4401
17 | 2660927.8105 | 1257460.0223
18 | 2660948.4648 | 1257519.9398
19 | 2661015.9637 | 1257300.6139
20 | 2661001.3888 | 1257323.7978
21 | 2661017.2963 | 1257298.4941
22 | 2661000.925 | 1257324.5355
23 | 2661018.0203 | 1257297.3424
24 | 2660999.0027 | 1257327.5933
25 | 2661030.1063 | 1257278.1176
26 | 2660987.3856 | 1257349.6785
27 | 2661032.5462 | 1257275.5677
28 | 2660897.5558 | 1257332.2255
29 | 2660877.8701 | 1257285.1225
30 | 2661059.5854 | 1257361.2065
31 | 2661065.4109 | 1257354.5306
32 | 2661037.1732 | 1257386.891
33 | 2661084.2913 | 1257332.8935
34 | 2661051.3688 | 1257408.3416
35 | 2661027.4718 | 1257378.4435
36 | 2661094.6973 | 1257320.9736
37 | 2661101.1841 | 1257342.1456
38 | 2661061.5331 | 1257403.2094
39 | 2661007.232 | 1257364.3801
40 | 2661099.3623 | 1257315.5705
41 | 2661123.9609 | 1257350.9134
42 | 2661102.7513 | 1257404.615
43 | 2661005.4333 | 1257363.8843
44 | 2660917.7159 | 1257337.9541
45 | 2660932.4582 | 1257336.5698
46 | 2660911.2113 | 1257336.1058
47 | 2660880.2419 | 1257374.1443
48 | 2660893.5885 | 1257379.7788
49 | 2660879.2635 | 1257376.3214
50 | 2660865.3698 | 1257273.9735
51 | 2660863.1239 | 1257297.1159
52 | 2660950.1998 | 1257216.2165
53 | 2660957.4123 | 1257192.0784
54 | 2661047.2252 | 1257261.0869
55 | 2660980.5159 | 1257177.9658
56 | 2660981.5251 | 1257179.2499
57 | 2660972.3773 | 1257167.6102
58 | 2660990.8431 | 1257191.1062
59 | 2660970.7243 | 1257169.6076
60 | 2661013.1053 | 1257190.8353
61 | 2660960.3972 | 1257182.0862
62 | 2661015.7671 | 1257193.0309
63 | 2660938.1956 | 1257151.5488
64 | 2660983.3344 | 1257357.7932
65 | 2660973.9991 | 1257374.5754
66 | 2660870.0526 | 1257397.2927
67 | 2660864.5445 | 1257418.882
68 | 2660860.7559 | 1257433.7313
69 | 2660857.3432 | 1257447.1947
70 | 2660899.4099 | 1257382.2364
71 | 2660887.9013 | 1257438.0468
72 | 2660912.1917 | 1257444.2899
73 | 2660884.9209 | 1257451.2606
74 | 2660892.04 | 1257421.3844
75 | 2660850.132 | 1257475.6435
76 | 2660926.2413 | 1257377.9714
77 | 2660926.3008 | 1257377.8344
78 | 2660920.5201 | 1257391.1485
79 | 2660933.3718 | 1257361.5483
80 | 2660928.6133 | 1257394.5675
81 | 2660944.5016 | 1257401.2762
82 | 2660920.3161 | 1257411.9204
83 | 2660956.3611 | 1257406.2837
84 | 2660914.6138 | 1257433.1443
85 | 2660962.5923 | 1257395.0818
86 | 2660954.1164 | 1257413.3879
87 | 2660992.8072 | 1257424.8835
88 | 2660919.6647 | 1257517.979
89 | 2660868.6714 | 1257513.2854
90 | 2660841.4152 | 1257510.0319
91 | 2660927.9663 | 1257458.14
92 | 2661126.8347 | 1257352.0197
93 | 2660930.0971 | 1257141.3118
94 | 2660844.0036 | 1257295.6095
95 | 2660845.1338 | 1257255.926
96 | 2660910.0155 | 1257454.2636
97 | 2660884.591 | 1257452.7233
98 | 2660919.7262 | 1257151.3754
99 | 2660933.3663 | 1257333.5169

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1