## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4032-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4032-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4032-6_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_4032-6_0_4_node_31 | 0.4 | n |  | TRUE
4 | bus_LV_4032-6_0_4_node_33 | 0.4 | n |  | TRUE
5 | bus_LV_4032-6_0_4_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_4032-6_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_4032-6_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_4032-6_0_4_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_4032-6_0_4_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_4032-6_0_4_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_4032-6_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_4032-6_0_4_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_4032-6_0_4_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_4032-6_0_4_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_4032-6_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_4032-6_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_4032-6_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_4032-6_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_4032-6_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_4032-6_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_4032-6_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_4032-6_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_4032-6_0_4_node_34 | 0.4 | n |  | TRUE
24 | bus_LV_4032-6_0_4_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_4032-6_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_4032-6_0_4_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_4032-6_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_4032-6_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_4032-6_0_4_node_42 | 0.4 | n |  | TRUE
30 | bus_LV_4032-6_0_4_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_4032-6_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_4032-6_0_4_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_4032-6_0_4_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_4032-6_0_4_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_4032-6_0_4_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_4032-6_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_4032-6_0_4_node_43 | 0.4 | n |  | TRUE
38 | bus_LV_4032-6_0_4_node_41 | 0.4 | n |  | TRUE
39 | bus_LV_4032-6_0_4_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_4032-6_0_4_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_4032-6_0_4_node_58 | 0.4 | n |  | TRUE
42 | bus_LV_4032-6_0_4_node_62 | 0.4 | n |  | TRUE
43 | bus_LV_4032-6_0_4_node_55 | 0.4 | n |  | TRUE
44 | bus_LV_4032-6_0_4_node_57 | 0.4 | n |  | TRUE
45 | bus_LV_4032-6_0_4_node_60 | 0.4 | n |  | TRUE
46 | bus_LV_4032-6_0_4_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_4032-6_0_4_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_4032-6_0_4_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_4032-6_0_4_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_4032-6_0_4_node_63 | 0.4 | n |  | TRUE
51 | bus_LV_4032-6_0_4_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_4032-6_0_4_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_4032-6_0_4_node_50 | 0.4 | n |  | TRUE
54 | bus_LV_4032-6_0_4_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_4032-6_0_4_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_4032-6_0_4_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_4032-6_0_4_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_4032-6_0_4_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_4032-6_0_4_node_59 | 0.4 | n |  | TRUE
60 | bus_LV_4032-6_0_4_node_61 | 0.4 | n |  | TRUE
61 | bus_MV_423_1_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4032-6_0_4_load_0 | 0 | 0.002663 | 0.00066741 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4032-6_0_4_load_1 | 1 | 0.0025691 | 0.00064389 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4032-6_0_4_load_3 | 2 | 0.002065 | 0.00051755 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4032-6_0_4_load_31 | 3 | 0.0091629 | 0.0022964 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4032-6_0_4_load_29 | 5 | 0.00056424 | 0.00014141 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4032-6_0_4_load_6 | 6 | 0.0011507 | 0.00028839 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4032-6_0_4_load_5 | 7 | 0.0020649 | 0.00051752 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4032-6_0_4_load_28 | 10 | 0.001154 | 0.00028923 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4032-6_0_4_load_7 | 11 | 0.0044698 | 0.0011202 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4032-6_0_4_load_26 | 12 | 0.0047665 | 0.0011946 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4032-6_0_4_load_35 | 13 | 0.0027798 | 0.00069668 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4032-6_0_4_load_19 | 14 | 0.0027806 | 0.00069689 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4032-6_0_4_load_8 | 15 | 0.00058354 | 0.00014625 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4032-6_0_4_load_14 | 16 | 0.00058777 | 0.00014731 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4032-6_0_4_load_15 | 17 | 0.00068864 | 0.00017259 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4032-6_0_4_load_9 | 18 | 0.0026965 | 0.0006758 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4032-6_0_4_load_10 | 19 | 0.0041371 | 0.0010368 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4032-6_0_4_load_11 | 20 | 0.011942 | 0.0029928 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4032-6_0_4_load_12 | 21 | 0.00049942 | 0.00012517 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4032-6_0_4_load_34 | 23 | 0.0033351 | 0.00083587 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4032-6_0_4_load_17 | 25 | 0.0037962 | 0.00095143 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4032-6_0_4_load_42 | 29 | 0.011472 | 0.0028753 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4032-6_0_4_load_40 | 30 | 0.015598 | 0.0039091 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4032-6_0_4_load_39 | 32 | 0.044841 | 0.011238 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4032-6_0_4_load_36 | 33 | 0.0023203 | 0.00058152 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4032-6_0_4_load_16 | 34 | 0.00078627 | 0.00019706 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4032-6_0_4_load_24 | 35 | 0.0023954 | 0.00060033 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4032-6_0_4_load_25 | 36 | 0.0030954 | 0.00077578 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4032-6_0_4_load_43 | 37 | 0.0057605 | 0.0014437 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4032-6_0_4_load_41 | 38 | 0.097626 | 0.024467 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4032-6_0_4_load_62 | 42 | 0.0023625 | 0.0005921 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4032-6_0_4_load_55 | 43 | 0.0024885 | 0.00062367 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4032-6_0_4_load_57 | 44 | 0.0015068 | 0.00037764 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4032-6_0_4_load_60 | 45 | 0.055473 | 0.013903 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4032-6_0_4_load_44 | 46 | 0.013293 | 0.0033316 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4032-6_0_4_load_45 | 47 | 0.062293 | 0.015612 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4032-6_0_4_load_46 | 48 | 0.062057 | 0.015553 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4032-6_0_4_load_47 | 49 | 0.013371 | 0.003351 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4032-6_0_4_load_63 | 50 | 0.038454 | 0.0096375 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4032-6_0_4_load_48 | 51 | 0.0017977 | 0.00045054 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4032-6_0_4_load_49 | 52 | 0.0021929 | 0.00054959 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4032-6_0_4_load_50 | 53 | 0.008363 | 0.002096 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4032-6_0_4_load_51 | 54 | 0.00063714 | 0.00015968 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4032-6_0_4_load_53 | 56 | 0.001358 | 0.00034034 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4032-6_0_4_load_54 | 57 | 0.0092833 | 0.0023266 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4032-6_0_4_load_56 | 58 | 0.0011821 | 0.00029626 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4032-6_0_4_load_59 | 59 | 0.012858 | 0.0032224 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4032-6_0_4_load_61 | 60 | 0.0046199 | 0.0011579 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 38 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4032-6_0_4_line_0 |  | 0 | 1 | 0.020862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4032-6_0_4_line_1 |  | 1 | 2 | 0.024192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4032-6_0_4_line_2 |  | 2 | 7 | 0.020019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4032-6_0_4_line_3 |  | 3 | 4 | 0.025232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4032-6_0_4_line_4 |  | 3 | 5 | 0.018783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4032-6_0_4_line_5 |  | 3 | 6 | 0.065727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4032-6_0_4_line_6 |  | 4 | 8 | 0.013089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4032-6_0_4_line_7 |  | 5 | 10 | 0.018653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4032-6_0_4_line_8 |  | 6 | 11 | 0.033128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4032-6_0_4_line_9 |  | 7 | 9 | 0.075336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4032-6_0_4_line_10 |  | 8 | 26 | 0.044549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4032-6_0_4_line_11 |  | 9 | 12 | 0.0021833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4032-6_0_4_line_12 |  | 11 | 15 | 0.0096993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4032-6_0_4_line_13 |  | 12 | 36 | 0.0033738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4032-6_0_4_line_14 |  | 13 | 14 | 0.0077835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4032-6_0_4_line_15 |  | 14 | 22 | 0.044781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4032-6_0_4_line_16 |  | 15 | 16 | 0.0084296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4032-6_0_4_line_17 |  | 16 | 17 | 0.005935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4032-6_0_4_line_18 |  | 17 | 34 | 0.0096651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4032-6_0_4_line_19 |  | 18 | 19 | 0.014366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4032-6_0_4_line_20 |  | 18 | 20 | 0.03088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4032-6_0_4_line_21 |  | 19 | 21 | 0.012829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4032-6_0_4_line_22 |  | 20 | 22 | 0.02374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4032-6_0_4_line_23 |  | 21 | 23 | 0.014047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4032-6_0_4_line_24 |  | 22 | 24 | 0.018948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4032-6_0_4_line_25 |  | 22 | 25 | 0.014321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4032-6_0_4_line_26 |  | 23 | 26 | 0.064774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4032-6_0_4_line_27 |  | 24 | 32 | 0.014141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_4032-6_0_4_line_28 |  | 24 | 28 | 0.041725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_4032-6_0_4_line_29 |  | 27 | 28 | 0.055389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_4032-6_0_4_line_30 |  | 27 | 29 | 0.014456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_4032-6_0_4_line_31 |  | 28 | 30 | 0.010445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_4032-6_0_4_line_32 |  | 29 | 37 | 0.010738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_4032-6_0_4_line_33 |  | 30 | 38 | 0.0054957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_4032-6_0_4_line_34 |  | 31 | 32 | 0.03736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4032-6_0_4_line_35 |  | 31 | 33 | 0.025162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4032-6_0_4_line_36 |  | 33 | 39 | 0.0033431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4032-6_0_4_line_37 |  | 34 | 35 | 0.011298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4032-6_0_4_line_38 |  | 35 | 36 | 0.011117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4032-6_0_4_line_39 |  | 37 | 46 | 0.012242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_4032-6_0_4_line_40 |  | 39 | 40 | 0.023715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4032-6_0_4_line_41 |  | 40 | 41 | 0.015558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4032-6_0_4_line_42 |  | 40 | 42 | 0.026317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4032-6_0_4_line_43 |  | 41 | 43 | 0.014054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4032-6_0_4_line_44 |  | 41 | 44 | 0.016281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4032-6_0_4_line_45 |  | 42 | 45 | 0.071211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4032-6_0_4_line_46 |  | 43 | 55 | 0.016036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4032-6_0_4_line_47 |  | 44 | 59 | 0.0098753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4032-6_0_4_line_48 |  | 45 | 60 | 0.019072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4032-6_0_4_line_49 |  | 46 | 47 | 0.0082481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_4032-6_0_4_line_50 |  | 47 | 48 | 0.010972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4032-6_0_4_line_51 |  | 48 | 49 | 0.020093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4032-6_0_4_line_52 |  | 49 | 50 | 0.014957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4032-6_0_4_line_53 |  | 51 | 52 | 0.027318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4032-6_0_4_line_54 |  | 51 | 53 | 0.0069632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4032-6_0_4_line_55 |  | 52 | 54 | 0.0025556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4032-6_0_4_line_56 |  | 53 | 55 | 0.020749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4032-6_0_4_line_57 |  | 54 | 56 | 0.0132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4032-6_0_4_line_58 |  | 55 | 57 | 0.0078805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4032-6_0_4_line_59 |  | 56 | 58 | 0.00065973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4032-6_0_4_trafo_41 | 0.63 MVA 20/0.4 kV | 61 | 38 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2659905.7321 | 1251365.7963 | 2659884.9888 | 1251363.5741
1 | 2659884.9888 | 1251363.5741 | 2659872.6817 | 1251362.2556 | 2659860.9422 | 1251360.922
2 | 2659860.9422 | 1251360.922 | 2659841.0516 | 1251358.6625
3 | 2659891.793 | 1251492.8957 | 2659890.9064 | 1251485.7818 | 2659872.8444 | 1251485.5774
4 | 2659854.0627 | 1251485.3649 | 2659854.0627 | 1251485.3649 | 2659872.8444 | 1251485.5774
5 | 2659872.8444 | 1251485.5774 | 2659884.8812 | 1251420.9615
6 | 2659891.793 | 1251492.8957 | 2659890.8983 | 1251501.5149 | 2659887.3765 | 1251504.2034
7 | 2659854.4741 | 1251504.0132 | 2659854.0627 | 1251485.3649
8 | 2659851.8087 | 1251419.346 | 2659867.1331 | 1251420.6071 | 2659884.8812 | 1251420.9615
9 | 2659794.86 | 1251396.9834 | 2659801.3433 | 1251379.8034 | 2659811.9558 | 1251354.3704 | 2659834.4353 | 1251357.9109 | 2659841.0516 | 1251358.6625
10 | 2659887.3765 | 1251504.2034 | 2659870.2051 | 1251545.3255
11 | 2659794.86 | 1251396.9834 | 2659796.8156 | 1251397.954
12 | 2659851.8087 | 1251419.346 | 2659844.1842 | 1251418.7185 | 2659842.2075 | 1251418.1789
13 | 2659799.8377 | 1251399.4539 | 2659796.8156 | 1251397.954
14 | 2659738.8485 | 1251433.6606 | 2659738.5731 | 1251441.4393
15 | 2659722.2528 | 1251482.8116 | 2659738.404 | 1251446.2153 | 2659738.5731 | 1251441.4393
16 | 2659834.0754 | 1251415.959 | 2659842.2075 | 1251418.1789
17 | 2659834.0754 | 1251415.959 | 2659834.0754 | 1251415.959 | 2659828.6495 | 1251413.554
18 | 2659819.9161 | 1251409.4191 | 2659824.8856 | 1251411.8856 | 2659828.6495 | 1251413.554
19 | 2659772.243 | 1251504.8053 | 2659785.4774 | 1251510.3933
20 | 2659743.8501 | 1251492.6671 | 2659748.2407 | 1251494.6706 | 2659772.243 | 1251504.8053
21 | 2659797.3021 | 1251515.37 | 2659792.8085 | 1251513.4887 | 2659785.4774 | 1251510.3933
22 | 2659722.2528 | 1251482.8116 | 2659743.8501 | 1251492.6671
23 | 2659810.2594 | 1251520.7948 | 2659797.3021 | 1251515.37
24 | 2659710.33 | 1251487.795 | 2659711.8996 | 1251483.3299 | 2659720.2523 | 1251487.339 | 2659722.2528 | 1251482.8116
25 | 2659722.2528 | 1251482.8116 | 2659709.3014 | 1251476.6993
26 | 2659870.2051 | 1251545.3255 | 2659845.5775 | 1251535.5811 | 2659810.2594 | 1251520.7948
27 | 2659710.33 | 1251487.795 | 2659705.6457 | 1251501.1374
28 | 2659748.7933 | 1251504.2385 | 2659710.33 | 1251487.795
29 | 2659799.875 | 1251526.0132 | 2659748.7933 | 1251504.2385
30 | 2659799.875 | 1251526.0132 | 2659797.0943 | 1251540.1997
31 | 2659748.7933 | 1251504.2385 | 2659744.9801 | 1251513.962
32 | 2659797.0943 | 1251540.1997 | 2659795.0289 | 1251550.7372
33 | 2659744.9801 | 1251513.962 | 2659742.9736 | 1251519.0784
34 | 2659680.4349 | 1251508.6419 | 2659700.329 | 1251516.2809 | 2659705.6457 | 1251501.1374
35 | 2659680.4349 | 1251508.6419 | 2659674.7846 | 1251533.1613
36 | 2659674.0339 | 1251536.4191 | 2659674.7846 | 1251533.1613
37 | 2659819.9161 | 1251409.4191 | 2659809.7957 | 1251404.3962
38 | 2659799.8377 | 1251399.4539 | 2659809.7957 | 1251404.3962
39 | 2659795.0289 | 1251550.7372 | 2659795.0289 | 1251550.7372 | 2659792.2796 | 1251553.9228 | 2659784.4064 | 1251555.5223
40 | 2659669.0605 | 1251559.6075 | 2659674.0339 | 1251536.4191
41 | 2659664.5329 | 1251574.4946 | 2659669.0605 | 1251559.6075
42 | 2659669.0605 | 1251559.6075 | 2659693.7847 | 1251568.6237
43 | 2659664.5329 | 1251574.4946 | 2659660.3896 | 1251587.9239
44 | 2659664.5329 | 1251574.4946 | 2659648.8576 | 1251570.0942
45 | 2659729.0943 | 1251607.5553 | 2659735.9631 | 1251601.455 | 2659738.3658 | 1251593.7183 | 2659736.5075 | 1251587.1394 | 2659731.837 | 1251582.5002 | 2659693.7847 | 1251568.6237
46 | 2659655.6618 | 1251603.2477 | 2659660.3896 | 1251587.9239
47 | 2659639.3499 | 1251567.4251 | 2659648.8576 | 1251570.0942
48 | 2659729.0943 | 1251607.5553 | 2659725.8494 | 1251610.4372 | 2659723.7526 | 1251617.7879 | 2659725.0478 | 1251624.7566
49 | 2659776.3728 | 1251554.3182 | 2659779.2134 | 1251554.0578 | 2659784.4064 | 1251555.5223 | 2659784.4064 | 1251555.5223
50 | 2659776.3728 | 1251554.3182 | 2659776.3728 | 1251554.3182 | 2659773.6453 | 1251556.092 | 2659771.9099 | 1251563.6128
51 | 2659771.9099 | 1251563.6128 | 2659767.3922 | 1251583.1911
52 | 2659764.0292 | 1251597.7652 | 2659767.3922 | 1251583.1911
53 | 2659629.8598 | 1251593.1383 | 2659620.884 | 1251589.6216 | 2659604.3575 | 1251583.3473
54 | 2659629.8598 | 1251593.1383 | 2659636.3431 | 1251595.6785
55 | 2659604.3575 | 1251583.3473 | 2659601.9683 | 1251582.4402
56 | 2659655.6618 | 1251603.2477 | 2659636.3431 | 1251595.6785
57 | 2659589.6275 | 1251577.755 | 2659601.9683 | 1251582.4402
58 | 2659655.6618 | 1251603.2477 | 2659653.2009 | 1251610.7341
59 | 2659589.0107 | 1251577.5209 | 2659589.6275 | 1251577.755

## bus_geodata
| x | y | coords
0 | 2659905.7321 | 1251365.7963
1 | 2659884.9888 | 1251363.5741
2 | 2659860.9422 | 1251360.922
3 | 2659872.8444 | 1251485.5774
4 | 2659891.793 | 1251492.8957
5 | 2659854.0627 | 1251485.3649
6 | 2659884.8812 | 1251420.9615
7 | 2659841.0516 | 1251358.6625
8 | 2659887.3765 | 1251504.2034
9 | 2659794.86 | 1251396.9834
10 | 2659854.4741 | 1251504.0132
11 | 2659851.8087 | 1251419.346
12 | 2659796.8156 | 1251397.954
13 | 2659738.8485 | 1251433.6606
14 | 2659738.5731 | 1251441.4393
15 | 2659842.2075 | 1251418.1789
16 | 2659834.0754 | 1251415.959
17 | 2659828.6495 | 1251413.554
18 | 2659772.243 | 1251504.8053
19 | 2659785.4774 | 1251510.3933
20 | 2659743.8501 | 1251492.6671
21 | 2659797.3021 | 1251515.37
22 | 2659722.2528 | 1251482.8116
23 | 2659810.2594 | 1251520.7948
24 | 2659710.33 | 1251487.795
25 | 2659709.3014 | 1251476.6993
26 | 2659870.2051 | 1251545.3255
27 | 2659799.875 | 1251526.0132
28 | 2659748.7933 | 1251504.2384
29 | 2659797.0943 | 1251540.1997
30 | 2659744.9801 | 1251513.962
31 | 2659680.4349 | 1251508.6419
32 | 2659705.6457 | 1251501.1374
33 | 2659674.7846 | 1251533.1613
34 | 2659819.916 | 1251409.4191
35 | 2659809.7957 | 1251404.3962
36 | 2659799.8377 | 1251399.4539
37 | 2659795.0289 | 1251550.7372
38 | 2659742.9736 | 1251519.0784
39 | 2659674.0339 | 1251536.4191
40 | 2659669.0605 | 1251559.6075
41 | 2659664.5329 | 1251574.4946
42 | 2659693.7847 | 1251568.6237
43 | 2659660.3896 | 1251587.9239
44 | 2659648.8576 | 1251570.0942
45 | 2659729.0943 | 1251607.5553
46 | 2659784.4064 | 1251555.5223
47 | 2659776.3728 | 1251554.3182
48 | 2659771.9099 | 1251563.6128
49 | 2659767.3922 | 1251583.1911
50 | 2659764.0292 | 1251597.7652
51 | 2659629.8598 | 1251593.1383
52 | 2659604.3575 | 1251583.3473
53 | 2659636.3431 | 1251595.6785
54 | 2659601.9683 | 1251582.4402
55 | 2659655.6618 | 1251603.2477
56 | 2659589.6275 | 1251577.755
57 | 2659653.2009 | 1251610.7341
58 | 2659589.0107 | 1251577.5209
59 | 2659639.3499 | 1251567.4251
60 | 2659725.0478 | 1251624.7566
61 | 2659748.7933 | 1251504.2384

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1