## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4092-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4092-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4092-2_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4092-2_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4092-2_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_4092-2_0_3_node_61 | 0.4 | n |  | TRUE
6 | bus_LV_4092-2_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_4092-2_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_4092-2_0_3_node_131 | 0.4 | n |  | TRUE
9 | bus_LV_4092-2_0_3_node_132 | 0.4 | n |  | TRUE
10 | bus_LV_4092-2_0_3_node_134 | 0.4 | n |  | TRUE
11 | bus_LV_4092-2_0_3_node_135 | 0.4 | n |  | TRUE
12 | bus_LV_4092-2_0_3_node_141 | 0.4 | n |  | TRUE
13 | bus_LV_4092-2_0_3_node_139 | 0.4 | n |  | TRUE
14 | bus_LV_4092-2_0_3_node_140 | 0.4 | n |  | TRUE
15 | bus_LV_4092-2_0_3_node_136 | 0.4 | n |  | TRUE
16 | bus_LV_4092-2_0_3_node_137 | 0.4 | n |  | TRUE
17 | bus_LV_4092-2_0_3_node_142 | 0.4 | n |  | TRUE
18 | bus_LV_4092-2_0_3_node_138 | 0.4 | n |  | TRUE
19 | bus_LV_4092-2_0_3_node_60 | 0.4 | n |  | TRUE
20 | bus_LV_4092-2_0_3_node_144 | 0.4 | n |  | TRUE
21 | bus_LV_4092-2_0_3_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_4092-2_0_3_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_4092-2_0_3_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_4092-2_0_3_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_4092-2_0_3_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_4092-2_0_3_node_118 | 0.4 | n |  | TRUE
27 | bus_LV_4092-2_0_3_node_107 | 0.4 | n |  | TRUE
28 | bus_LV_4092-2_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_4092-2_0_3_node_87 | 0.4 | n |  | TRUE
30 | bus_LV_4092-2_0_3_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_4092-2_0_3_node_59 | 0.4 | n |  | TRUE
32 | bus_LV_4092-2_0_3_node_158 | 0.4 | n |  | TRUE
33 | bus_LV_4092-2_0_3_node_49 | 0.4 | n |  | TRUE
34 | bus_LV_4092-2_0_3_node_50 | 0.4 | n |  | TRUE
35 | bus_LV_4092-2_0_3_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_4092-2_0_3_node_52 | 0.4 | n |  | TRUE
37 | bus_LV_4092-2_0_3_node_84 | 0.4 | n |  | TRUE
38 | bus_LV_4092-2_0_3_node_53 | 0.4 | n |  | TRUE
39 | bus_LV_4092-2_0_3_node_125 | 0.4 | n |  | TRUE
40 | bus_LV_4092-2_0_3_node_126 | 0.4 | n |  | TRUE
41 | bus_LV_4092-2_0_3_node_85 | 0.4 | n |  | TRUE
42 | bus_LV_4092-2_0_3_node_86 | 0.4 | n |  | TRUE
43 | bus_LV_4092-2_0_3_node_121 | 0.4 | n |  | TRUE
44 | bus_LV_4092-2_0_3_node_113 | 0.4 | n |  | TRUE
45 | bus_LV_4092-2_0_3_node_112 | 0.4 | n |  | TRUE
46 | bus_LV_4092-2_0_3_node_115 | 0.4 | n |  | TRUE
47 | bus_LV_4092-2_0_3_node_116 | 0.4 | n |  | TRUE
48 | bus_LV_4092-2_0_3_node_117 | 0.4 | n |  | TRUE
49 | bus_LV_4092-2_0_3_node_122 | 0.4 | n |  | TRUE
50 | bus_MV_423_0_node_144 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4092-2_0_3_load_0 | 0 | 0.0069799 | 0.0017493 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4092-2_0_3_load_3 | 3 | 0.0087332 | 0.0021888 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4092-2_0_3_load_5 | 4 | 0.0018765 | 0.0004703 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4092-2_0_3_load_4 | 6 | 0.0047149 | 0.0011817 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4092-2_0_3_load_6 | 7 | 0.0019297 | 0.00048363 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4092-2_0_3_load_131 | 8 | 0.007393 | 0.0018529 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4092-2_0_3_load_139 | 13 | 0.00065084 | 0.00016312 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4092-2_0_3_load_140 | 14 | 0.00074396 | 0.00018645 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4092-2_0_3_load_142 | 17 | 0.00086657 | 0.00021718 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4092-2_0_3_load_138 | 18 | 0.0006221 | 0.00015591 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4092-2_0_3_load_144 | 20 | 0.0081478 | 0.002042 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4092-2_0_3_load_23 | 21 | 0.0031285 | 0.00078408 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4092-2_0_3_load_24 | 23 | 0.0021133 | 0.00052964 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4092-2_0_3_load_27 | 25 | 0.0028849 | 0.00072303 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4092-2_0_3_load_118 | 26 | 0.0024476 | 0.00061343 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4092-2_0_3_load_107 | 27 | 0.0056296 | 0.0014109 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4092-2_0_3_load_59 | 31 | 0.0017463 | 0.00043766 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4092-2_0_3_load_158 | 32 | 0.014456 | 0.0036231 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4092-2_0_3_load_49 | 33 | 0.0044781 | 0.0011223 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4092-2_0_3_load_50 | 34 | 0.0057463 | 0.0014402 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4092-2_0_3_load_52 | 36 | 0.086313 | 0.021632 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4092-2_0_3_load_53 | 38 | 0.0012942 | 0.00032436 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4092-2_0_3_load_126 | 40 | 0.001178 | 0.00029523 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4092-2_0_3_load_121 | 43 | 0.043674 | 0.010946 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4092-2_0_3_load_113 | 44 | 0.00091047 | 0.00022818 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4092-2_0_3_load_112 | 45 | 0.008722 | 0.0021859 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4092-2_0_3_load_115 | 46 | 0.049416 | 0.012385 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4092-2_0_3_load_116 | 47 | 0.019282 | 0.0048326 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4092-2_0_3_load_122 | 49 | 0.018686 | 0.0046831 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4092-2_0_3_line_0 |  | 0 | 1 | 0.12347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4092-2_0_3_line_1 |  | 1 | 2 | 0.015311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4092-2_0_3_line_2 |  | 1 | 3 | 0.080001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4092-2_0_3_line_3 |  | 2 | 4 | 0.18031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4092-2_0_3_line_4 |  | 2 | 5 | 0.18805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4092-2_0_3_line_5 |  | 4 | 6 | 0.062645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4092-2_0_3_line_6 |  | 5 | 40 | 0.087189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4092-2_0_3_line_7 |  | 6 | 7 | 0.017911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4092-2_0_3_line_8 |  | 8 | 9 | 0.027968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4092-2_0_3_line_9 |  | 9 | 10 | 0.014448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4092-2_0_3_line_10 |  | 9 | 11 | 0.023217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4092-2_0_3_line_11 |  | 10 | 12 | 0.019553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4092-2_0_3_line_12 |  | 10 | 13 | 0.024866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4092-2_0_3_line_13 |  | 11 | 14 | 0.015842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4092-2_0_3_line_14 |  | 12 | 20 | 0.074764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4092-2_0_3_line_15 |  | 13 | 16 | 0.0043197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4092-2_0_3_line_16 |  | 14 | 19 | 0.15581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4092-2_0_3_line_17 |  | 15 | 16 | 0.045553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4092-2_0_3_line_18 |  | 15 | 17 | 0.056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4092-2_0_3_line_19 |  | 16 | 18 | 0.011469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4092-2_0_3_line_20 |  | 19 | 30 | 0.078233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4092-2_0_3_line_21 |  | 21 | 22 | 0.069212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4092-2_0_3_line_22 |  | 22 | 25 | 0.1158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4092-2_0_3_line_23 |  | 23 | 24 | 0.0061435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4092-2_0_3_line_24 |  | 24 | 26 | 0.068014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4092-2_0_3_line_25 |  | 25 | 27 | 0.072477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4092-2_0_3_line_26 |  | 26 | 41 | 0.031433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4092-2_0_3_line_27 |  | 27 | 28 | 0.052194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4092-2_0_3_line_28 |  | 28 | 29 | 0.074169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4092-2_0_3_line_29 |  | 28 | 30 | 0.20838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4092-2_0_3_line_30 |  | 29 | 32 | 0.043684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4092-2_0_3_line_31 |  | 29 | 42 | 0.12082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4092-2_0_3_line_32 |  | 30 | 31 | 0.12511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4092-2_0_3_line_33 |  | 33 | 34 | 0.0075612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4092-2_0_3_line_34 |  | 33 | 35 | 0.094134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4092-2_0_3_line_35 |  | 35 | 36 | 0.063516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4092-2_0_3_line_36 |  | 36 | 37 | 0.088562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4092-2_0_3_line_37 |  | 37 | 41 | 0.009504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4092-2_0_3_line_38 |  | 37 | 42 | 0.12751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4092-2_0_3_line_39 |  | 38 | 39 | 0.024966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4092-2_0_3_line_40 |  | 39 | 40 | 0.032154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4092-2_0_3_line_41 |  | 39 | 44 | 0.091396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4092-2_0_3_line_42 |  | 41 | 43 | 0.063474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4092-2_0_3_line_43 |  | 42 | 44 | 0.017282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4092-2_0_3_line_44 |  | 42 | 45 | 0.19077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4092-2_0_3_line_45 |  | 43 | 49 | 0.062375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4092-2_0_3_line_46 |  | 46 | 47 | 0.051211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4092-2_0_3_line_47 |  | 47 | 48 | 0.026509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4092-2_0_3_line_48 |  | 48 | 49 | 0.030184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4092-2_0_3_trafo_84 | 0.63 MVA 20/0.4 kV | 50 | 37 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2658929.4793 | 1253031.9976 | 2658931.022 | 1253012.6994 | 2658929.5714 | 1253003.0226 | 2658923.6569 | 1252997.5711 | 2658883.1146 | 1252983.814 | 2658875.9784 | 1252985.1218 | 2658872.2235 | 1252993.9352 | 2658866.0431 | 1253019.8405
1 | 2658944.6852 | 1253034.1392 | 2658929.4793 | 1253031.9976
2 | 2658929.4793 | 1253031.9976 | 2658931.022 | 1253012.6994 | 2658929.5714 | 1253003.0226 | 2658923.6569 | 1252997.5711 | 2658883.1146 | 1252983.814
3 | 2658944.6852 | 1253034.1392 | 2658959.009 | 1252914.164 | 2658960.7563 | 1252882.6704 | 2658958.5811 | 1252854.818
4 | 2658911.9116 | 1253218.7321 | 2658924.6241 | 1253178.7081 | 2658932.7606 | 1253138.2717 | 2658934.5375 | 1253122.734 | 2658944.6852 | 1253034.1392
5 | 2658948.7462 | 1252792.9628 | 2658954.7633 | 1252826.727 | 2658958.5811 | 1252854.818 | 2658958.5811 | 1252854.818
6 | 2658911.9116 | 1253218.7321 | 2658897.2037 | 1253264.4404 | 2658890.4259 | 1253303.0221
7 | 2658944.5647 | 1252775.5674 | 2658947.5378 | 1252786.1822 | 2658948.7462 | 1252792.9628
8 | 2658808.9067 | 1252908.8579 | 2658820.188 | 1252883.2664
9 | 2658795.4762 | 1252903.432 | 2658808.9067 | 1252908.8579
10 | 2658830.4842 | 1252917.5893 | 2658808.9067 | 1252908.8579
11 | 2658795.4762 | 1252903.432 | 2658785.6516 | 1252908.7382 | 2658782.9842 | 1252916.7174
12 | 2658795.4762 | 1252903.432 | 2658772.6612 | 1252893.5428
13 | 2658830.4842 | 1252917.5893 | 2658826.0489 | 1252932.7975
14 | 2658782.9842 | 1252916.7174 | 2658758.28 | 1252940.9672 | 2658747.6065 | 1252979.6696
15 | 2658768.6979 | 1252891.8249 | 2658772.6612 | 1252893.5428
16 | 2658774.007 | 1253079.1981 | 2658779.0889 | 1253068.1852 | 2658801.9005 | 1253017.9206 | 2658815.7823 | 1252968.001 | 2658826.0489 | 1252932.7975
17 | 2658730.5469 | 1252883.3519 | 2658747.7667 | 1252877.2627 | 2658749.8011 | 1252883.6429 | 2658768.6979 | 1252891.8249
18 | 2658730.5469 | 1252883.3519 | 2658724.3407 | 1252903.4934 | 2658721.0587 | 1252917.9044 | 2658720.87 | 1252938.0472
19 | 2658768.6979 | 1252891.8249 | 2658773.0702 | 1252881.2221
20 | 2658774.007 | 1253079.1981 | 2658760.0108 | 1253109.5251 | 2658738.0498 | 1253148.6572
21 | 2658488.1917 | 1253514.866 | 2658494.3797 | 1253518.5853 | 2658524.1242 | 1253524.5053 | 2658555.364 | 1253529.676
22 | 2658488.1917 | 1253514.866 | 2658491.5827 | 1253509.9516 | 2658524.5278 | 1253461.5205 | 2658543.8287 | 1253435.5262 | 2658555.0756 | 1253420.3611
23 | 2658724.1513 | 1253551.9255 | 2658723.1481 | 1253557.9865
24 | 2658724.1513 | 1253551.9255 | 2658734.46 | 1253498.4456 | 2658736.4884 | 1253485.0483
25 | 2658598.2491 | 1253362.1467 | 2658555.0756 | 1253420.3611
26 | 2658741.1938 | 1253453.9699 | 2658736.4884 | 1253485.0483
27 | 2658629.3404 | 1253320.2237 | 2658598.2491 | 1253362.1467
28 | 2658629.3404 | 1253320.2237 | 2658644.1922 | 1253326.0636 | 2658667.8861 | 1253330.4679 | 2658685.1247 | 1253333.7631 | 2658684.0794 | 1253341.0246 | 2658682.6687 | 1253350.1392
29 | 2658629.3404 | 1253320.2237 | 2658624.8795 | 1253316.577 | 2658630.8237 | 1253309.1083 | 2658694.4911 | 1253217.0071 | 2658725.1914 | 1253171.5681 | 2658738.0498 | 1253148.6572
30 | 2658682.6687 | 1253350.1392 | 2658663.0812 | 1253347.0765 | 2658659.3613 | 1253370.7007
31 | 2658682.6687 | 1253350.1392 | 2658710.7012 | 1253354.5311 | 2658711.946 | 1253346.1708 | 2658713.1852 | 1253339.1448 | 2658759.757 | 1253348.0571 | 2658788.8604 | 1253352.4933
32 | 2658738.0498 | 1253148.6572 | 2658749.5714 | 1253154.0307 | 2658761.0551 | 1253157.1356 | 2658858.353 | 1253182.3
33 | 2658868.2593 | 1253568.845 | 2658867.1512 | 1253576.3246
34 | 2658885.6429 | 1253477.798 | 2658881.7836 | 1253497.151 | 2658879.0104 | 1253499.0804 | 2658879.7327 | 1253505.3587 | 2658876.2497 | 1253538.4696 | 2658868.2593 | 1253568.845
35 | 2658885.6429 | 1253477.798 | 2658860.0775 | 1253473.4965 | 2658861.0121 | 1253466.7677 | 2658830.7404 | 1253461.0993
36 | 2658743.6917 | 1253444.7993 | 2658830.7404 | 1253461.0993
37 | 2658741.1938 | 1253453.9699 | 2658743.6917 | 1253444.7993
38 | 2658743.6917 | 1253444.7993 | 2658752.9876 | 1253390.7756 | 2658759.757 | 1253348.0571 | 2658788.8604 | 1253352.4933
39 | 2658883.3945 | 1253334.3746 | 2658892.7753 | 1253338.7264 | 2658898.8262 | 1253345.6025 | 2658900.9899 | 1253350.621
40 | 2658883.3945 | 1253334.3746 | 2658888.2458 | 1253315.4317 | 2658890.4259 | 1253303.0221
41 | 2658883.3945 | 1253334.3746 | 2658879.809 | 1253345.1466 | 2658863.8219 | 1253359.4311 | 2658850.3445 | 1253361.8546 | 2658805.946 | 1253355.0947
42 | 2658741.1938 | 1253453.9699 | 2658678.5743 | 1253443.5869
43 | 2658788.8604 | 1253352.4933 | 2658805.946 | 1253355.0947
44 | 2658788.8604 | 1253352.4933 | 2658816.3801 | 1253220.8515 | 2658810.6208 | 1253206.6288 | 2658771.6902 | 1253193.9646
45 | 2658678.5743 | 1253443.5869 | 2658649.6176 | 1253438.7856 | 2658644.759 | 1253438.7375 | 2658640.6887 | 1253439.0863 | 2658636.4566 | 1253442.0576 | 2658634.5808 | 1253445.5749 | 2658632.0116 | 1253460.2737
46 | 2658651.5234 | 1253539.9746 | 2658621.9919 | 1253535.1134 | 2658619.5212 | 1253534.6998 | 2658622.4585 | 1253516.1542
47 | 2658626.8146 | 1253490.0071 | 2658624.9859 | 1253500.1962 | 2658622.4585 | 1253516.1542
48 | 2658626.8146 | 1253490.0071 | 2658632.0116 | 1253460.2737

## bus_geodata
| x | y | coords
0 | 2658866.0431 | 1253019.8405
1 | 2658929.4793 | 1253031.9976
2 | 2658944.6852 | 1253034.1392
3 | 2658883.1146 | 1252983.814
4 | 2658958.5811 | 1252854.818
5 | 2658911.9116 | 1253218.7321
6 | 2658948.7462 | 1252792.9628
7 | 2658944.5647 | 1252775.5674
8 | 2658820.188 | 1252883.2664
9 | 2658808.9067 | 1252908.8579
10 | 2658795.4762 | 1252903.432
11 | 2658830.4842 | 1252917.5893
12 | 2658782.9842 | 1252916.7174
13 | 2658772.6612 | 1252893.5428
14 | 2658826.0489 | 1252932.7975
15 | 2658730.5469 | 1252883.3519
16 | 2658768.6979 | 1252891.8249
17 | 2658720.87 | 1252938.0472
18 | 2658773.0702 | 1252881.2221
19 | 2658774.007 | 1253079.1981
20 | 2658747.6065 | 1252979.6696
21 | 2658555.364 | 1253529.676
22 | 2658488.1917 | 1253514.866
23 | 2658723.1481 | 1253557.9865
24 | 2658724.1513 | 1253551.9255
25 | 2658555.0756 | 1253420.3611
26 | 2658736.4884 | 1253485.0483
27 | 2658598.2491 | 1253362.1467
28 | 2658629.3404 | 1253320.2237
29 | 2658682.6687 | 1253350.1392
30 | 2658738.0498 | 1253148.6572
31 | 2658858.353 | 1253182.3
32 | 2658659.3613 | 1253370.7007
33 | 2658868.2593 | 1253568.845
34 | 2658867.1512 | 1253576.3246
35 | 2658885.6429 | 1253477.798
36 | 2658830.7404 | 1253461.0993
37 | 2658743.6917 | 1253444.7993
38 | 2658900.9899 | 1253350.621
39 | 2658883.3945 | 1253334.3746
40 | 2658890.4259 | 1253303.0221
41 | 2658741.1938 | 1253453.9699
42 | 2658788.8604 | 1253352.4933
43 | 2658678.5743 | 1253443.5869
44 | 2658805.946 | 1253355.0947
45 | 2658771.6902 | 1253193.9646
46 | 2658651.5234 | 1253539.9746
47 | 2658622.4585 | 1253516.1542
48 | 2658626.8146 | 1253490.0071
49 | 2658632.0116 | 1253460.2737
50 | 2658741.1938 | 1253453.9699

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1