## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4107-1_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4107-1_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4107-1_0_7_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_4107-1_0_7_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_4107-1_0_7_node_80 | 0.4 | n |  | TRUE
5 | bus_LV_4107-1_0_7_node_44 | 0.4 | n |  | TRUE
6 | bus_LV_4107-1_0_7_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_4107-1_0_7_node_86 | 0.4 | n |  | TRUE
8 | bus_LV_4107-1_0_7_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_4107-1_0_7_node_47 | 0.4 | n |  | TRUE
10 | bus_LV_4107-1_0_7_node_82 | 0.4 | n |  | TRUE
11 | bus_LV_4107-1_0_7_node_43 | 0.4 | n |  | TRUE
12 | bus_LV_4107-1_0_7_node_87 | 0.4 | n |  | TRUE
13 | bus_LV_4107-1_0_7_node_48 | 0.4 | n |  | TRUE
14 | bus_LV_4107-1_0_7_node_78 | 0.4 | n |  | TRUE
15 | bus_LV_4107-1_0_7_node_93 | 0.4 | n |  | TRUE
16 | bus_LV_4107-1_0_7_node_76 | 0.4 | n |  | TRUE
17 | bus_LV_4107-1_0_7_node_94 | 0.4 | n |  | TRUE
18 | bus_LV_4107-1_0_7_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_4107-1_0_7_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_4107-1_0_7_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_4107-1_0_7_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_4107-1_0_7_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_4107-1_0_7_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_4107-1_0_7_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_4107-1_0_7_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_4107-1_0_7_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_4107-1_0_7_node_51 | 0.4 | n |  | TRUE
28 | bus_LV_4107-1_0_7_node_50 | 0.4 | n |  | TRUE
29 | bus_LV_4107-1_0_7_node_99 | 0.4 | n |  | TRUE
30 | bus_LV_4107-1_0_7_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_4107-1_0_7_node_64 | 0.4 | n |  | TRUE
32 | bus_LV_4107-1_0_7_node_83 | 0.4 | n |  | TRUE
33 | bus_LV_4107-1_0_7_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_4107-1_0_7_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_4107-1_0_7_node_65 | 0.4 | n |  | TRUE
36 | bus_LV_4107-1_0_7_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_4107-1_0_7_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_4107-1_0_7_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_4107-1_0_7_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_4107-1_0_7_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_4107-1_0_7_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_4107-1_0_7_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_4107-1_0_7_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_4107-1_0_7_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_4107-1_0_7_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_4107-1_0_7_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_4107-1_0_7_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_4107-1_0_7_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_4107-1_0_7_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_4107-1_0_7_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_4107-1_0_7_node_49 | 0.4 | n |  | TRUE
52 | bus_LV_4107-1_0_7_node_32 | 0.4 | n |  | TRUE
53 | bus_LV_4107-1_0_7_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_4107-1_0_7_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_4107-1_0_7_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_4107-1_0_7_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_4107-1_0_7_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_4107-1_0_7_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_4107-1_0_7_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_4107-1_0_7_node_81 | 0.4 | n |  | TRUE
61 | bus_LV_4107-1_0_7_node_75 | 0.4 | n |  | TRUE
62 | bus_LV_4107-1_0_7_node_71 | 0.4 | n |  | TRUE
63 | bus_LV_4107-1_0_7_node_42 | 0.4 | n |  | TRUE
64 | bus_LV_4107-1_0_7_node_85 | 0.4 | n |  | TRUE
65 | bus_LV_4107-1_0_7_node_72 | 0.4 | n |  | TRUE
66 | bus_LV_4107-1_0_7_node_73 | 0.4 | n |  | TRUE
67 | bus_LV_4107-1_0_7_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_4107-1_0_7_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_4107-1_0_7_node_54 | 0.4 | n |  | TRUE
70 | bus_LV_4107-1_0_7_node_55 | 0.4 | n |  | TRUE
71 | bus_LV_4107-1_0_7_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_4107-1_0_7_node_56 | 0.4 | n |  | TRUE
73 | bus_LV_4107-1_0_7_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_4107-1_0_7_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_4107-1_0_7_node_62 | 0.4 | n |  | TRUE
76 | bus_LV_4107-1_0_7_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_4107-1_0_7_node_59 | 0.4 | n |  | TRUE
78 | bus_LV_4107-1_0_7_node_66 | 0.4 | n |  | TRUE
79 | bus_LV_4107-1_0_7_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_4107-1_0_7_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_4107-1_0_7_node_69 | 0.4 | n |  | TRUE
82 | bus_LV_4107-1_0_7_node_68 | 0.4 | n |  | TRUE
83 | bus_LV_4107-1_0_7_node_77 | 0.4 | n |  | TRUE
84 | bus_LV_4107-1_0_7_node_79 | 0.4 | n |  | TRUE
85 | bus_LV_4107-1_0_7_node_92 | 0.4 | n |  | TRUE
86 | bus_LV_4107-1_0_7_node_91 | 0.4 | n |  | TRUE
87 | bus_LV_4107-1_0_7_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_4107-1_0_7_node_84 | 0.4 | n |  | TRUE
89 | bus_LV_4107-1_0_7_node_98 | 0.4 | n |  | TRUE
90 | bus_LV_4107-1_0_7_node_89 | 0.4 | n |  | TRUE
91 | bus_LV_4107-1_0_7_node_90 | 0.4 | n |  | TRUE
92 | bus_LV_4107-1_0_7_node_88 | 0.4 | n |  | TRUE
93 | bus_LV_4107-1_0_7_node_97 | 0.4 | n |  | TRUE
94 | bus_LV_4107-1_0_7_node_95 | 0.4 | n |  | TRUE
95 | bus_MV_421_0_node_153 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4107-1_0_7_load_0 | 0 | 0.0024688 | 0.00061873 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4107-1_0_7_load_1 | 1 | 0.0075383 | 0.0018893 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4107-1_0_7_load_44 | 5 | 0.0079845 | 0.0020011 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4107-1_0_7_load_86 | 7 | 0.0025794 | 0.00064646 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4107-1_0_7_load_7 | 8 | 0.0043222 | 0.0010832 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4107-1_0_7_load_47 | 9 | 0.0027688 | 0.00069392 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4107-1_0_7_load_82 | 10 | 0.016951 | 0.0042484 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4107-1_0_7_load_43 | 11 | 0.0079845 | 0.0020011 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4107-1_0_7_load_87 | 12 | 0.0036758 | 0.00092123 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4107-1_0_7_load_48 | 13 | 0.0052545 | 0.0013169 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4107-1_0_7_load_93 | 15 | 0.0041504 | 0.0010402 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4107-1_0_7_load_76 | 16 | 0.0081169 | 0.0020343 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4107-1_0_7_load_94 | 17 | 0.0031276 | 0.00078385 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4107-1_0_7_load_9 | 18 | 0.016486 | 0.0041319 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4107-1_0_7_load_10 | 19 | 0.04308 | 0.010797 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4107-1_0_7_load_11 | 20 | 0.0015005 | 0.00037607 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4107-1_0_7_load_14 | 23 | 0.046756 | 0.011718 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4107-1_0_7_load_15 | 24 | 0.0048675 | 0.0012199 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4107-1_0_7_load_16 | 25 | 0.0046659 | 0.0011694 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4107-1_0_7_load_51 | 27 | 0.00050039 | 0.00012541 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4107-1_0_7_load_50 | 28 | 0.0073309 | 0.0018373 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4107-1_0_7_load_99 | 29 | 0.0059413 | 0.001489 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4107-1_0_7_load_29 | 30 | 0.0039581 | 0.00099198 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4107-1_0_7_load_83 | 32 | 0.0013226 | 0.00033148 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4107-1_0_7_load_27 | 34 | 0.002098 | 0.0005258 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4107-1_0_7_load_65 | 35 | 0.0032017 | 0.00080243 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4107-1_0_7_load_18 | 36 | 0.0025 | 0.00062655 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4107-1_0_7_load_19 | 37 | 0.0057848 | 0.0014498 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4107-1_0_7_load_21 | 38 | 0.007936 | 0.001989 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4107-1_0_7_load_20 | 39 | 0.0076019 | 0.0019052 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4107-1_0_7_load_24 | 42 | 0.0044837 | 0.0011237 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4107-1_0_7_load_25 | 43 | 0.0010754 | 0.00026951 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4107-1_0_7_load_38 | 46 | 0.063302 | 0.015865 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4107-1_0_7_load_26 | 47 | 0.0025715 | 0.00064448 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4107-1_0_7_load_28 | 48 | 0.03385 | 0.0084835 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4107-1_0_7_load_30 | 49 | 0.0050832 | 0.001274 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4107-1_0_7_load_31 | 50 | 0.0053028 | 0.001329 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4107-1_0_7_load_49 | 51 | 0.0027092 | 0.00067899 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4107-1_0_7_load_32 | 52 | 0.0053798 | 0.0013483 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4107-1_0_7_load_33 | 53 | 0.0085634 | 0.0021462 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4107-1_0_7_load_40 | 56 | 0.012075 | 0.0030263 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4107-1_0_7_load_46 | 59 | 0.005005 | 0.0012544 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4107-1_0_7_load_81 | 60 | 0.064925 | 0.016272 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4107-1_0_7_load_75 | 61 | 0.0019568 | 0.00049041 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4107-1_0_7_load_42 | 63 | 0.0036466 | 0.00091392 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4107-1_0_7_load_85 | 64 | 0.0022265 | 0.00055802 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4107-1_0_7_load_72 | 65 | 0.0091601 | 0.0022957 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4107-1_0_7_load_52 | 67 | 0.0077037 | 0.0019307 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4107-1_0_7_load_53 | 68 | 0.0057687 | 0.0014458 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4107-1_0_7_load_55 | 70 | 0.015135 | 0.0037932 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4107-1_0_7_load_56 | 72 | 0.011692 | 0.0029302 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4107-1_0_7_load_62 | 75 | 0.0020305 | 0.00050888 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4107-1_0_7_load_59 | 77 | 0.015602 | 0.0039103 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4107-1_0_7_load_66 | 78 | 0.0044419 | 0.0011132 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4107-1_0_7_load_63 | 79 | 0.0033334 | 0.00083543 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4107-1_0_7_load_70 | 80 | 0.0044243 | 0.0011088 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4107-1_0_7_load_69 | 81 | 0.0063862 | 0.0016005 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4107-1_0_7_load_77 | 83 | 0.0020079 | 0.00050323 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4107-1_0_7_load_79 | 84 | 0.0029026 | 0.00072746 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4107-1_0_7_load_91 | 86 | 0.0020585 | 0.00051592 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4107-1_0_7_load_74 | 87 | 0.001911 | 0.00047894 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4107-1_0_7_load_84 | 88 | 0.0020794 | 0.00052113 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4107-1_0_7_load_98 | 89 | 0.0010298 | 0.0002581 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4107-1_0_7_load_89 | 90 | 0.0024528 | 0.00061473 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4107-1_0_7_load_90 | 91 | 0.0080962 | 0.0020291 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4107-1_0_7_load_88 | 92 | 0.021633 | 0.0054218 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4107-1_0_7_load_95 | 94 | 0.00063001 | 0.00015789 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4107-1_0_7_line_0 |  | 0 | 1 | 0.0048806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4107-1_0_7_line_1 |  | 1 | 2 | 0.014332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4107-1_0_7_line_2 |  | 2 | 3 | 0.013168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4107-1_0_7_line_3 |  | 3 | 4 | 0.007667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4107-1_0_7_line_4 |  | 3 | 5 | 0.024703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4107-1_0_7_line_5 |  | 4 | 10 | 0.035376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4107-1_0_7_line_6 |  | 4 | 6 | 0.013376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4107-1_0_7_line_7 |  | 5 | 11 | 0.020948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4107-1_0_7_line_8 |  | 6 | 7 | 0.0079837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4107-1_0_7_line_9 |  | 7 | 12 | 0.010017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4107-1_0_7_line_10 |  | 8 | 9 | 0.0023565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4107-1_0_7_line_11 |  | 9 | 13 | 0.027775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4107-1_0_7_line_12 |  | 10 | 60 | 0.033672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4107-1_0_7_line_13 |  | 11 | 63 | 0.01391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4107-1_0_7_line_14 |  | 12 | 92 | 0.0030246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4107-1_0_7_line_15 |  | 13 | 51 | 0.0024104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4107-1_0_7_line_16 |  | 14 | 15 | 0.017761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4107-1_0_7_line_17 |  | 14 | 16 | 0.048333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4107-1_0_7_line_18 |  | 15 | 17 | 0.021145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4107-1_0_7_line_19 |  | 16 | 82 | 0.020794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4107-1_0_7_line_20 |  | 18 | 19 | 0.01989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_4107-1_0_7_line_21 |  | 18 | 20 | 0.016423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_4107-1_0_7_line_22 |  | 19 | 21 | 0.0056008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_4107-1_0_7_line_23 |  | 20 | 22 | 0.0022004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_4107-1_0_7_line_24 |  | 21 | 23 | 0.020211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_4107-1_0_7_line_25 |  | 21 | 24 | 0.036666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4107-1_0_7_line_26 |  | 22 | 25 | 0.015619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4107-1_0_7_line_27 |  | 22 | 26 | 0.01191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_4107-1_0_7_line_28 |  | 23 | 27 | 0.0051308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_4107-1_0_7_line_29 |  | 24 | 28 | 0.034653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4107-1_0_7_line_30 |  | 25 | 29 | 0.0013953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4107-1_0_7_line_31 |  | 26 | 30 | 0.036233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4107-1_0_7_line_32 |  | 26 | 31 | 0.016491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4107-1_0_7_line_33 |  | 27 | 32 | 0.014841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_4107-1_0_7_line_34 |  | 28 | 33 | 0.018345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4107-1_0_7_line_35 |  | 30 | 34 | 0.0044374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4107-1_0_7_line_36 |  | 31 | 35 | 0.040528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4107-1_0_7_line_37 |  | 32 | 57 | 0.0011816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_4107-1_0_7_line_38 |  | 33 | 54 | 0.012371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4107-1_0_7_line_39 |  | 34 | 47 | 0.018148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4107-1_0_7_line_40 |  | 35 | 76 | 0.0086752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4107-1_0_7_line_41 |  | 36 | 37 | 0.015899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4107-1_0_7_line_42 |  | 37 | 38 | 0.0059083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4107-1_0_7_line_43 |  | 38 | 41 | 0.025211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4107-1_0_7_line_44 |  | 39 | 40 | 0.024973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4107-1_0_7_line_45 |  | 40 | 42 | 0.023488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4107-1_0_7_line_46 |  | 40 | 43 | 0.013215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4107-1_0_7_line_47 |  | 41 | 42 | 0.0076506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4107-1_0_7_line_48 |  | 43 | 44 | 0.026376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4107-1_0_7_line_49 |  | 44 | 45 | 0.010149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4107-1_0_7_line_50 |  | 44 | 46 | 0.017546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4107-1_0_7_line_51 |  | 45 | 55 | 0.055082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4107-1_0_7_line_52 |  | 45 | 56 | 0.018899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4107-1_0_7_line_53 |  | 46 | 57 | 0.024752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4107-1_0_7_line_54 |  | 47 | 48 | 0.020619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4107-1_0_7_line_55 |  | 48 | 49 | 0.016899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4107-1_0_7_line_56 |  | 49 | 50 | 0.013126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4107-1_0_7_line_57 |  | 50 | 51 | 0.015929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4107-1_0_7_line_58 |  | 52 | 53 | 0.020831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4107-1_0_7_line_59 |  | 53 | 54 | 0.023129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4107-1_0_7_line_60 |  | 55 | 58 | 0.042393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4107-1_0_7_line_61 |  | 55 | 59 | 0.0019692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4107-1_0_7_line_62 |  | 57 | 60 | 0.040342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4107-1_0_7_line_63 |  | 58 | 61 | 0.0066576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4107-1_0_7_line_64 |  | 59 | 62 | 0.007977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4107-1_0_7_line_65 |  | 61 | 64 | 0.0073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4107-1_0_7_line_66 |  | 62 | 65 | 0.017983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4107-1_0_7_line_67 |  | 62 | 66 | 0.037181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4107-1_0_7_line_68 |  | 64 | 88 | 0.0075141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4107-1_0_7_line_69 |  | 66 | 85 | 0.095692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4107-1_0_7_line_70 |  | 66 | 86 | 0.036289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4107-1_0_7_line_71 |  | 67 | 68 | 0.011659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4107-1_0_7_line_72 |  | 67 | 69 | 0.019492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4107-1_0_7_line_73 |  | 68 | 70 | 0.02052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4107-1_0_7_line_74 |  | 69 | 71 | 0.021748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4107-1_0_7_line_75 |  | 71 | 74 | 0.029308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4107-1_0_7_line_76 |  | 71 | 75 | 0.013918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4107-1_0_7_line_77 |  | 72 | 73 | 0.021799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4107-1_0_7_line_78 |  | 73 | 76 | 0.007676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4107-1_0_7_line_79 |  | 73 | 77 | 0.030524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4107-1_0_7_line_80 |  | 74 | 78 | 0.0063957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4107-1_0_7_line_81 |  | 74 | 79 | 0.023582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4107-1_0_7_line_82 |  | 75 | 80 | 0.01112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4107-1_0_7_line_83 |  | 76 | 81 | 0.013475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4107-1_0_7_line_84 |  | 78 | 82 | 0.02884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4107-1_0_7_line_85 |  | 80 | 81 | 0.0076569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4107-1_0_7_line_86 |  | 82 | 83 | 0.021161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4107-1_0_7_line_87 |  | 83 | 84 | 0.014554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4107-1_0_7_line_88 |  | 84 | 90 | 0.010549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4107-1_0_7_line_89 |  | 85 | 89 | 0.053059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4107-1_0_7_line_90 |  | 87 | 88 | 0.0053941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4107-1_0_7_line_91 |  | 89 | 93 | 0.044581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4107-1_0_7_line_92 |  | 90 | 91 | 0.00723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4107-1_0_7_line_93 |  | 93 | 94 | 0.030685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4107-1_0_7_trafo_12 | 0.63 MVA 20/0.4 kV | 95 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2660248.2741 | 1256518.5953 | 2660253.021 | 1256519.7298
1 | 2660266.9609 | 1256523.0614 | 2660253.021 | 1256519.7298
2 | 2660275.9728 | 1256515.6478 | 2660274.36 | 1256515.5424 | 2660271.745 | 1256516.1051 | 2660269.8711 | 1256517.209 | 2660268.0936 | 1256519.2035 | 2660267.4777 | 1256520.4425 | 2660266.9609 | 1256523.0614
3 | 2660281.7779 | 1256520.2546 | 2660281.1044 | 1256519.0024 | 2660279.269 | 1256517.0601 | 2660275.9728 | 1256515.6478
4 | 2660275.9728 | 1256515.6478 | 2660280.3599 | 1256494.3661 | 2660282.538 | 1256492.3412
5 | 2660281.7779 | 1256520.2546 | 2660316.8545 | 1256524.8495
6 | 2660281.7779 | 1256520.2546 | 2660282.3622 | 1256522.8624 | 2660282.2703 | 1256524.4848 | 2660281.3774 | 1256526.9998 | 2660280.5051 | 1256528.2362 | 2660278.4368 | 1256529.9164 | 2660276.3397 | 1256530.7178
7 | 2660301.417 | 1256485.9326 | 2660288.0266 | 1256487.239 | 2660282.538 | 1256492.3412
8 | 2660276.3397 | 1256530.7178 | 2660275.6129 | 1256533.9572 | 2660276.7811 | 1256538.4723
9 | 2660276.7811 | 1256538.4723 | 2660280.0411 | 1256541.2186 | 2660285.716 | 1256542.1728
10 | 2660234.0109 | 1256584.4838 | 2660231.7828 | 1256583.7166
11 | 2660234.0109 | 1256584.4838 | 2660260.2725 | 1256593.5267
12 | 2660350.2417 | 1256529.2232 | 2660316.8545 | 1256524.8495
13 | 2660301.417 | 1256485.9326 | 2660315.2608 | 1256484.5819
14 | 2660288.6987 | 1256542.6744 | 2660285.716 | 1256542.1728
15 | 2660262.5516 | 1256594.3115 | 2660260.2725 | 1256593.5267
16 | 2660195.3646 | 1256654.9833 | 2660198.2281 | 1256637.4548
17 | 2660195.3646 | 1256654.9833 | 2660227.9626 | 1256661.8752 | 2660242.6835 | 1256664.8318
18 | 2660198.2281 | 1256637.4548 | 2660201.6372 | 1256616.5863
19 | 2660263.0701 | 1256668.9262 | 2660242.6835 | 1256664.8318
20 | 2660384.7263 | 1256599.4275 | 2660386.309 | 1256579.601
21 | 2660384.7263 | 1256599.4275 | 2660383.4195 | 1256615.798
22 | 2660386.7547 | 1256574.0179 | 2660386.309 | 1256579.601
23 | 2660383.2444 | 1256617.9914 | 2660383.4195 | 1256615.798
24 | 2660386.7547 | 1256574.0179 | 2660388.5372 | 1256553.8858
25 | 2660386.7547 | 1256574.0179 | 2660395.9028 | 1256574.7006 | 2660402.5576 | 1256576.5809 | 2660403.895 | 1256584.4557 | 2660406.7178 | 1256585.6965 | 2660411.5643 | 1256585.9461 | 2660416.2167 | 1256585.9936
26 | 2660383.2444 | 1256617.9914 | 2660398.8181 | 1256616.8031
27 | 2660383.2444 | 1256617.9914 | 2660382.5801 | 1256629.8821
28 | 2660388.5372 | 1256553.8858 | 2660388.9897 | 1256548.775
29 | 2660423.5129 | 1256619.8229 | 2660421.8444 | 1256609.4456 | 2660418.3608 | 1256593.8878 | 2660417.0328 | 1256588.0479 | 2660416.2167 | 1256585.9936
30 | 2660398.8181 | 1256616.8031 | 2660399.5686 | 1256616.7459 | 2660400.2111 | 1256616.7325
31 | 2660382.5801 | 1256629.8821 | 2660347.0894 | 1256622.5866
32 | 2660382.5801 | 1256629.8821 | 2660382.7979 | 1256637.3674 | 2660384.019 | 1256646.2863
33 | 2660390.2986 | 1256533.9915 | 2660388.9897 | 1256548.775
34 | 2660426.4251 | 1256637.935 | 2660423.5129 | 1256619.8229
35 | 2660342.844 | 1256621.3055 | 2660346.4959 | 1256622.4646 | 2660347.0894 | 1256622.5866
36 | 2660384.019 | 1256646.2863 | 2660384.4505 | 1256649.8265 | 2660382.3371 | 1256663.3146 | 2660375.3008 | 1256685.5366
37 | 2660390.4028 | 1256532.8145 | 2660390.2986 | 1256533.9915
38 | 2660426.4251 | 1256637.935 | 2660438.5696 | 1256635.4015
39 | 2660325.5465 | 1256615.8157 | 2660342.844 | 1256621.3055
40 | 2660368.1247 | 1256690.4114 | 2660375.3008 | 1256685.5366
41 | 2660462.4024 | 1256440.2383 | 2660462.4024 | 1256440.2383 | 2660463.1428 | 1256456.1197
42 | 2660463.1428 | 1256456.1197 | 2660463.418 | 1256462.0217
43 | 2660464.5922 | 1256487.2054 | 2660463.418 | 1256462.0217
44 | 2660433.4912 | 1256488.7335 | 2660432.3519 | 1256463.7867
45 | 2660433.4912 | 1256488.7335 | 2660456.9508 | 1256487.5808
46 | 2660433.4912 | 1256488.7335 | 2660420.2924 | 1256489.3782
47 | 2660464.5922 | 1256487.2054 | 2660456.9508 | 1256487.5808
48 | 2660393.9474 | 1256490.6649 | 2660420.2924 | 1256489.3782
49 | 2660394.6766 | 1256480.5429 | 2660393.9474 | 1256490.6649
50 | 2660393.9474 | 1256490.6649 | 2660392.477 | 1256508.1493
51 | 2660398.4951 | 1256425.598 | 2660394.6766 | 1256480.5429
52 | 2660394.6766 | 1256480.5429 | 2660375.828 | 1256481.9278
53 | 2660390.4028 | 1256532.8145 | 2660392.477 | 1256508.1493
54 | 2660305.8939 | 1256609.5784 | 2660325.5465 | 1256615.8157
55 | 2660305.8939 | 1256609.5784 | 2660304.1459 | 1256609.0236 | 2660289.962 | 1256603.9462
56 | 2660277.6037 | 1256599.5223 | 2660289.962 | 1256603.9462
57 | 2660262.5516 | 1256594.3115 | 2660275.5635 | 1256598.792 | 2660277.6037 | 1256599.5223
58 | 2660431.7031 | 1256651.3601 | 2660415.6893 | 1256655.3935 | 2660416.2097 | 1256659.679
59 | 2660438.5696 | 1256635.4015 | 2660441.4749 | 1256647.7622 | 2660434.1447 | 1256650.7451 | 2660431.7031 | 1256651.3601
60 | 2660398.4951 | 1256425.598 | 2660356.1624 | 1256429.5694
61 | 2660398.4951 | 1256425.598 | 2660398.6316 | 1256423.6335
62 | 2660390.4028 | 1256532.8145 | 2660384.2282 | 1256532.6403 | 2660360.8408 | 1256530.6116 | 2660350.2417 | 1256529.2232
63 | 2660356.1624 | 1256429.5694 | 2660357.1322 | 1256422.9828
64 | 2660399.1846 | 1256415.6757 | 2660398.6316 | 1256423.6335
65 | 2660357.1322 | 1256422.9828 | 2660358.1956 | 1256415.7607
66 | 2660399.1846 | 1256415.6757 | 2660381.2723 | 1256417.2662
67 | 2660399.1846 | 1256415.6757 | 2660400.228 | 1256400.6312 | 2660399.138 | 1256393.6373 | 2660392.9765 | 1256387.7369 | 2660399.3609 | 1256386.5678
68 | 2660359.2901 | 1256408.3268 | 2660358.1956 | 1256415.7607
69 | 2660306.504 | 1256366.474 | 2660317.1236 | 1256370.7963 | 2660332.3647 | 1256374.5209 | 2660349.737 | 1256377.8002 | 2660388.1167 | 1256386.5643 | 2660392.9765 | 1256387.7369 | 2660399.3609 | 1256386.5678
70 | 2660399.3609 | 1256386.5678 | 2660405.4401 | 1256386.4964 | 2660435.648 | 1256386.1766
71 | 2660292.2242 | 1256701.2689 | 2660303.8701 | 1256701.816
72 | 2660323.3409 | 1256702.7306 | 2660303.8701 | 1256701.816
73 | 2660292.2242 | 1256701.2689 | 2660271.7271 | 1256700.3061
74 | 2660323.3409 | 1256702.7306 | 2660322.9291 | 1256680.9886
75 | 2660322.9291 | 1256680.9886 | 2660301.0781 | 1256672.5379 | 2660297.7803 | 1256667.5896
76 | 2660322.9291 | 1256680.9886 | 2660329.9971 | 1256682.2727 | 2660336.5831 | 1256683.6785
77 | 2660370.5465 | 1256697.6969 | 2660367.0978 | 1256699.4185 | 2660361.0921 | 1256703.4046 | 2660350.3571 | 1256703.5498
78 | 2660370.5465 | 1256697.6969 | 2660368.1247 | 1256690.4114
79 | 2660370.5465 | 1256697.6969 | 2660373.7801 | 1256707.459 | 2660381.4683 | 1256726.1823
80 | 2660297.7803 | 1256667.5896 | 2660291.5829 | 1256669.1701
81 | 2660297.7803 | 1256667.5896 | 2660314.1981 | 1256661.5858 | 2660319.9296 | 1256659.494
82 | 2660347.4584 | 1256686 | 2660336.5831 | 1256683.6785
83 | 2660368.1247 | 1256690.4114 | 2660354.9465 | 1256687.5984
84 | 2660263.0701 | 1256668.9262 | 2660273.3142 | 1256670.8207 | 2660287.0894 | 1256670.3161 | 2660291.5829 | 1256669.1701
85 | 2660354.9465 | 1256687.5984 | 2660347.4584 | 1256686
86 | 2660263.0701 | 1256668.9262 | 2660258.5885 | 1256675.8078 | 2660253.2701 | 1256677.4771 | 2660246.4435 | 1256677.6633 | 2660245.9006 | 1256677.7164
87 | 2660236.3854 | 1256684.3836 | 2660237.2795 | 1256678.5597 | 2660245.9006 | 1256677.7164
88 | 2660236.5012 | 1256694.873 | 2660236.3105 | 1256694.4834 | 2660236.1972 | 1256685.6093 | 2660236.3854 | 1256684.3836
89 | 2660306.504 | 1256366.474 | 2660299.9913 | 1256359.5027 | 2660297.9534 | 1256353.0107 | 2660300.6258 | 1256343.8535 | 2660314.6324 | 1256320.5656
90 | 2660360.0759 | 1256402.9902 | 2660360.0759 | 1256402.9902 | 2660359.2901 | 1256408.3268
91 | 2660329.1655 | 1256279.9651 | 2660330.1908 | 1256291.1057 | 2660324.9599 | 1256303.3946 | 2660314.6324 | 1256320.5656
92 | 2660239.6792 | 1256701.3671 | 2660236.5012 | 1256694.873
93 | 2660329.1655 | 1256279.9651 | 2660323.9868 | 1256272.3291 | 2660306.9285 | 1256259.31

## bus_geodata
| x | y | coords
0 | 2660248.2741 | 1256518.5953
1 | 2660253.021 | 1256519.7298
2 | 2660266.9609 | 1256523.0614
3 | 2660275.9728 | 1256515.6478
4 | 2660281.7779 | 1256520.2546
5 | 2660282.538 | 1256492.3412
6 | 2660276.3397 | 1256530.7178
7 | 2660276.7811 | 1256538.4723
8 | 2660231.7828 | 1256583.7166
9 | 2660234.0109 | 1256584.4838
10 | 2660316.8545 | 1256524.8495
11 | 2660301.417 | 1256485.9326
12 | 2660285.716 | 1256542.1728
13 | 2660260.2725 | 1256593.5267
14 | 2660195.3646 | 1256654.9833
15 | 2660198.2281 | 1256637.4548
16 | 2660242.6835 | 1256664.8318
17 | 2660201.6372 | 1256616.5863
18 | 2660384.7263 | 1256599.4275
19 | 2660386.309 | 1256579.601
20 | 2660383.4195 | 1256615.798
21 | 2660386.7547 | 1256574.0179
22 | 2660383.2444 | 1256617.9914
23 | 2660388.5372 | 1256553.8858
24 | 2660416.2167 | 1256585.9936
25 | 2660398.8181 | 1256616.8031
26 | 2660382.5801 | 1256629.8821
27 | 2660388.9897 | 1256548.775
28 | 2660423.5129 | 1256619.8229
29 | 2660400.2111 | 1256616.7325
30 | 2660347.0894 | 1256622.5866
31 | 2660384.019 | 1256646.2863
32 | 2660390.2986 | 1256533.9915
33 | 2660426.4251 | 1256637.935
34 | 2660342.844 | 1256621.3055
35 | 2660375.3008 | 1256685.5366
36 | 2660462.4024 | 1256440.2383
37 | 2660463.1428 | 1256456.1197
38 | 2660463.418 | 1256462.0217
39 | 2660432.3519 | 1256463.7867
40 | 2660433.4912 | 1256488.7335
41 | 2660464.5922 | 1256487.2054
42 | 2660456.9508 | 1256487.5808
43 | 2660420.2924 | 1256489.3782
44 | 2660393.9474 | 1256490.6649
45 | 2660394.6766 | 1256480.5429
46 | 2660392.477 | 1256508.1493
47 | 2660325.5465 | 1256615.8157
48 | 2660305.8939 | 1256609.5784
49 | 2660289.962 | 1256603.9462
50 | 2660277.6037 | 1256599.5223
51 | 2660262.5516 | 1256594.3115
52 | 2660416.2097 | 1256659.679
53 | 2660431.7031 | 1256651.3601
54 | 2660438.5696 | 1256635.4015
55 | 2660398.4951 | 1256425.598
56 | 2660375.828 | 1256481.9278
57 | 2660390.4028 | 1256532.8145
58 | 2660356.1624 | 1256429.5694
59 | 2660398.6316 | 1256423.6335
60 | 2660350.2417 | 1256529.2232
61 | 2660357.1322 | 1256422.9828
62 | 2660399.1846 | 1256415.6757
63 | 2660315.2608 | 1256484.5819
64 | 2660358.1956 | 1256415.7607
65 | 2660381.2723 | 1256417.2662
66 | 2660399.3609 | 1256386.5678
67 | 2660303.8701 | 1256701.816
68 | 2660292.2242 | 1256701.2689
69 | 2660323.3409 | 1256702.7306
70 | 2660271.7271 | 1256700.3061
71 | 2660322.9291 | 1256680.9886
72 | 2660350.3571 | 1256703.5498
73 | 2660370.5465 | 1256697.6969
74 | 2660297.7803 | 1256667.5896
75 | 2660336.5831 | 1256683.6785
76 | 2660368.1247 | 1256690.4114
77 | 2660381.4683 | 1256726.1823
78 | 2660291.5829 | 1256669.1701
79 | 2660319.9296 | 1256659.494
80 | 2660347.4584 | 1256686
81 | 2660354.9465 | 1256687.5984
82 | 2660263.0701 | 1256668.9262
83 | 2660245.9006 | 1256677.7164
84 | 2660236.3854 | 1256684.3836
85 | 2660306.504 | 1256366.474
86 | 2660435.648 | 1256386.1766
87 | 2660360.0759 | 1256402.9902
88 | 2660359.2901 | 1256408.3268
89 | 2660314.6324 | 1256320.5656
90 | 2660236.5012 | 1256694.873
91 | 2660239.6792 | 1256701.3671
92 | 2660288.6987 | 1256542.6744
93 | 2660329.1655 | 1256279.9651
94 | 2660306.9285 | 1256259.31
95 | 2660390.4028 | 1256532.8145

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1