## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4207-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4207-4_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4207-4_0_3_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_4207-4_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_4207-4_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_4207-4_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_4207-4_0_3_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_4207-4_0_3_node_50 | 0.4 | n |  | TRUE
8 | bus_LV_4207-4_0_3_node_52 | 0.4 | n |  | TRUE
9 | bus_LV_4207-4_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_4207-4_0_3_node_86 | 0.4 | n |  | TRUE
11 | bus_LV_4207-4_0_3_node_38 | 0.4 | n |  | TRUE
12 | bus_LV_4207-4_0_3_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_4207-4_0_3_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_4207-4_0_3_node_41 | 0.4 | n |  | TRUE
15 | bus_LV_4207-4_0_3_node_42 | 0.4 | n |  | TRUE
16 | bus_LV_4207-4_0_3_node_43 | 0.4 | n |  | TRUE
17 | bus_LV_4207-4_0_3_node_56 | 0.4 | n |  | TRUE
18 | bus_LV_4207-4_0_3_node_54 | 0.4 | n |  | TRUE
19 | bus_LV_4207-4_0_3_node_61 | 0.4 | n |  | TRUE
20 | bus_LV_4207-4_0_3_node_44 | 0.4 | n |  | TRUE
21 | bus_LV_4207-4_0_3_node_45 | 0.4 | n |  | TRUE
22 | bus_LV_4207-4_0_3_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_4207-4_0_3_node_47 | 0.4 | n |  | TRUE
24 | bus_LV_4207-4_0_3_node_48 | 0.4 | n |  | TRUE
25 | bus_LV_4207-4_0_3_node_49 | 0.4 | n |  | TRUE
26 | bus_LV_4207-4_0_3_node_80 | 0.4 | n |  | TRUE
27 | bus_LV_4207-4_0_3_node_67 | 0.4 | n |  | TRUE
28 | bus_LV_4207-4_0_3_node_250 | 0.4 | n |  | TRUE
29 | bus_LV_4207-4_0_3_node_51 | 0.4 | n |  | TRUE
30 | bus_LV_4207-4_0_3_node_53 | 0.4 | n |  | TRUE
31 | bus_LV_4207-4_0_3_node_55 | 0.4 | n |  | TRUE
32 | bus_LV_4207-4_0_3_node_244 | 0.4 | n |  | TRUE
33 | bus_LV_4207-4_0_3_node_57 | 0.4 | n |  | TRUE
34 | bus_LV_4207-4_0_3_node_58 | 0.4 | n |  | TRUE
35 | bus_LV_4207-4_0_3_node_59 | 0.4 | n |  | TRUE
36 | bus_LV_4207-4_0_3_node_92 | 0.4 | n |  | TRUE
37 | bus_LV_4207-4_0_3_node_249 | 0.4 | n |  | TRUE
38 | bus_LV_4207-4_0_3_node_60 | 0.4 | n |  | TRUE
39 | bus_LV_4207-4_0_3_node_62 | 0.4 | n |  | TRUE
40 | bus_LV_4207-4_0_3_node_63 | 0.4 | n |  | TRUE
41 | bus_LV_4207-4_0_3_node_64 | 0.4 | n |  | TRUE
42 | bus_LV_4207-4_0_3_node_235 | 0.4 | n |  | TRUE
43 | bus_LV_4207-4_0_3_node_238 | 0.4 | n |  | TRUE
44 | bus_LV_4207-4_0_3_node_65 | 0.4 | n |  | TRUE
45 | bus_LV_4207-4_0_3_node_66 | 0.4 | n |  | TRUE
46 | bus_LV_4207-4_0_3_node_68 | 0.4 | n |  | TRUE
47 | bus_LV_4207-4_0_3_node_69 | 0.4 | n |  | TRUE
48 | bus_LV_4207-4_0_3_node_70 | 0.4 | n |  | TRUE
49 | bus_LV_4207-4_0_3_node_75 | 0.4 | n |  | TRUE
50 | bus_LV_4207-4_0_3_node_241 | 0.4 | n |  | TRUE
51 | bus_LV_4207-4_0_3_node_240 | 0.4 | n |  | TRUE
52 | bus_LV_4207-4_0_3_node_96 | 0.4 | n |  | TRUE
53 | bus_LV_4207-4_0_3_node_71 | 0.4 | n |  | TRUE
54 | bus_LV_4207-4_0_3_node_72 | 0.4 | n |  | TRUE
55 | bus_LV_4207-4_0_3_node_73 | 0.4 | n |  | TRUE
56 | bus_LV_4207-4_0_3_node_74 | 0.4 | n |  | TRUE
57 | bus_LV_4207-4_0_3_node_78 | 0.4 | n |  | TRUE
58 | bus_LV_4207-4_0_3_node_76 | 0.4 | n |  | TRUE
59 | bus_LV_4207-4_0_3_node_93 | 0.4 | n |  | TRUE
60 | bus_LV_4207-4_0_3_node_77 | 0.4 | n |  | TRUE
61 | bus_LV_4207-4_0_3_node_247 | 0.4 | n |  | TRUE
62 | bus_LV_4207-4_0_3_node_243 | 0.4 | n |  | TRUE
63 | bus_LV_4207-4_0_3_node_79 | 0.4 | n |  | TRUE
64 | bus_LV_4207-4_0_3_node_81 | 0.4 | n |  | TRUE
65 | bus_LV_4207-4_0_3_node_82 | 0.4 | n |  | TRUE
66 | bus_LV_4207-4_0_3_node_83 | 0.4 | n |  | TRUE
67 | bus_LV_4207-4_0_3_node_84 | 0.4 | n |  | TRUE
68 | bus_LV_4207-4_0_3_node_85 | 0.4 | n |  | TRUE
69 | bus_LV_4207-4_0_3_node_87 | 0.4 | n |  | TRUE
70 | bus_LV_4207-4_0_3_node_88 | 0.4 | n |  | TRUE
71 | bus_LV_4207-4_0_3_node_100 | 0.4 | n |  | TRUE
72 | bus_LV_4207-4_0_3_node_252 | 0.4 | n |  | TRUE
73 | bus_LV_4207-4_0_3_node_89 | 0.4 | n |  | TRUE
74 | bus_LV_4207-4_0_3_node_90 | 0.4 | n |  | TRUE
75 | bus_LV_4207-4_0_3_node_101 | 0.4 | n |  | TRUE
76 | bus_LV_4207-4_0_3_node_102 | 0.4 | n |  | TRUE
77 | bus_LV_4207-4_0_3_node_94 | 0.4 | n |  | TRUE
78 | bus_LV_4207-4_0_3_node_95 | 0.4 | n |  | TRUE
79 | bus_LV_4207-4_0_3_node_242 | 0.4 | n |  | TRUE
80 | bus_LV_4207-4_0_3_node_229 | 0.4 | n |  | TRUE
81 | bus_LV_4207-4_0_3_node_97 | 0.4 | n |  | TRUE
82 | bus_LV_4207-4_0_3_node_98 | 0.4 | n |  | TRUE
83 | bus_LV_4207-4_0_3_node_99 | 0.4 | n |  | TRUE
84 | bus_LV_4207-4_0_3_node_104 | 0.4 | n |  | TRUE
85 | bus_LV_4207-4_0_3_node_103 | 0.4 | n |  | TRUE
86 | bus_LV_4207-4_0_3_node_105 | 0.4 | n |  | TRUE
87 | bus_LV_4207-4_0_3_node_106 | 0.4 | n |  | TRUE
88 | bus_LV_4207-4_0_3_node_228 | 0.4 | n |  | TRUE
89 | bus_LV_4207-4_0_3_node_230 | 0.4 | n |  | TRUE
90 | bus_LV_4207-4_0_3_node_231 | 0.4 | n |  | TRUE
91 | bus_LV_4207-4_0_3_node_232 | 0.4 | n |  | TRUE
92 | bus_LV_4207-4_0_3_node_233 | 0.4 | n |  | TRUE
93 | bus_LV_4207-4_0_3_node_234 | 0.4 | n |  | TRUE
94 | bus_LV_4207-4_0_3_node_236 | 0.4 | n |  | TRUE
95 | bus_LV_4207-4_0_3_node_239 | 0.4 | n |  | TRUE
96 | bus_LV_4207-4_0_3_node_245 | 0.4 | n |  | TRUE
97 | bus_LV_4207-4_0_3_node_246 | 0.4 | n |  | TRUE
98 | bus_LV_4207-4_0_3_node_251 | 0.4 | n |  | TRUE
99 | bus_MV_434_0_node_83 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4207-4_0_3_load_0 | 0 | 0.00092594 | 0.00023206 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4207-4_0_3_load_4 | 2 | 0.0020177 | 0.00050567 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4207-4_0_3_load_5 | 4 | 0.003011 | 0.00075464 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4207-4_0_3_load_6 | 5 | 0.00095379 | 0.00023904 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4207-4_0_3_load_3 | 6 | 0.002107 | 0.00052806 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4207-4_0_3_load_50 | 7 | 0.0020604 | 0.00051638 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4207-4_0_3_load_52 | 8 | 0.0017199 | 0.00043104 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4207-4_0_3_load_7 | 9 | 0.0016542 | 0.00041458 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4207-4_0_3_load_38 | 11 | 0.0026159 | 0.0006556 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4207-4_0_3_load_39 | 12 | 0.0015807 | 0.00039617 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4207-4_0_3_load_41 | 14 | 0.001692 | 0.00042405 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4207-4_0_3_load_42 | 15 | 0.0016945 | 0.00042469 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4207-4_0_3_load_43 | 16 | 0.0014839 | 0.0003719 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4207-4_0_3_load_56 | 17 | 0.0025137 | 0.00062998 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4207-4_0_3_load_54 | 18 | 0.0016909 | 0.00042377 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4207-4_0_3_load_61 | 19 | 0.001156 | 0.00028972 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4207-4_0_3_load_44 | 20 | 0.0025603 | 0.00064168 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4207-4_0_3_load_45 | 21 | 0.0023386 | 0.00058612 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4207-4_0_3_load_47 | 23 | 0.0018016 | 0.00045152 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4207-4_0_3_load_48 | 24 | 0.0028058 | 0.0007032 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4207-4_0_3_load_80 | 26 | 0.0044106 | 0.0011054 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4207-4_0_3_load_250 | 28 | 0.0029088 | 0.00072902 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4207-4_0_3_load_51 | 29 | 0.0017322 | 0.00043412 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4207-4_0_3_load_55 | 31 | 0.0011605 | 0.00029084 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4207-4_0_3_load_244 | 32 | 0.0020892 | 0.0005236 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4207-4_0_3_load_58 | 34 | 0.0033972 | 0.00085142 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4207-4_0_3_load_59 | 35 | 0.0013087 | 0.000328 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4207-4_0_3_load_92 | 36 | 0.0021959 | 0.00055035 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4207-4_0_3_load_249 | 37 | 0.0012803 | 0.00032087 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4207-4_0_3_load_60 | 38 | 0.0022517 | 0.00056434 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4207-4_0_3_load_64 | 41 | 0.0023875 | 0.00059837 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4207-4_0_3_load_235 | 42 | 0.0017018 | 0.00042651 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4207-4_0_3_load_238 | 43 | 0.0017076 | 0.00042796 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4207-4_0_3_load_65 | 44 | 0.013738 | 0.003443 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4207-4_0_3_load_68 | 46 | 0.013765 | 0.0034499 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4207-4_0_3_load_70 | 48 | 0.0020778 | 0.00052074 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4207-4_0_3_load_240 | 51 | 0.0039511 | 0.00099023 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4207-4_0_3_load_96 | 52 | 0.0091926 | 0.0023039 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4207-4_0_3_load_71 | 53 | 0.0025464 | 0.00063818 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4207-4_0_3_load_72 | 54 | 0.0015091 | 0.00037821 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4207-4_0_3_load_73 | 55 | 0.0015367 | 0.00038513 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4207-4_0_3_load_74 | 56 | 0.0035291 | 0.00088447 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4207-4_0_3_load_78 | 57 | 0.0018476 | 0.00046304 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4207-4_0_3_load_76 | 58 | 0.0069847 | 0.0017505 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4207-4_0_3_load_247 | 61 | 0.0016338 | 0.00040947 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4207-4_0_3_load_243 | 62 | 0.0013621 | 0.00034138 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4207-4_0_3_load_79 | 63 | 0.001742 | 0.00043659 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4207-4_0_3_load_81 | 64 | 0.0066947 | 0.0016778 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4207-4_0_3_load_82 | 65 | 0.00057267 | 0.00014352 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4207-4_0_3_load_83 | 66 | 0.0012233 | 0.00030659 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4207-4_0_3_load_85 | 68 | 0.00041907 | 0.00010503 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4207-4_0_3_load_88 | 70 | 0.0057177 | 0.001433 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4207-4_0_3_load_100 | 71 | 0.0044024 | 0.0011034 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4207-4_0_3_load_252 | 72 | 0.0064279 | 0.001611 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4207-4_0_3_load_89 | 73 | 0.0014196 | 0.00035579 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4207-4_0_3_load_101 | 75 | 0.0015947 | 0.00039966 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4207-4_0_3_load_102 | 76 | 0.00093577 | 0.00023453 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4207-4_0_3_load_94 | 77 | 0.0030861 | 0.00077344 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4207-4_0_3_load_95 | 78 | 0.0012613 | 0.00031611 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4207-4_0_3_load_242 | 79 | 0.0014836 | 0.00037182 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4207-4_0_3_load_229 | 80 | 0.0012531 | 0.00031405 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4207-4_0_3_load_98 | 82 | 0.0034765 | 0.00087129 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4207-4_0_3_load_99 | 83 | 0.0068304 | 0.0017119 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4207-4_0_3_load_104 | 84 | 0.0015799 | 0.00039595 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4207-4_0_3_load_103 | 85 | 0.0042713 | 0.0010705 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4207-4_0_3_load_105 | 86 | 0.0013229 | 0.00033156 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4207-4_0_3_load_106 | 87 | 0.0022225 | 0.000557 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4207-4_0_3_load_228 | 88 | 0.0011757 | 0.00029466 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4207-4_0_3_load_230 | 89 | 0.0021879 | 0.00054835 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4207-4_0_3_load_231 | 90 | 0.0015493 | 0.00038828 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4207-4_0_3_load_232 | 91 | 0.0017232 | 0.00043187 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4207-4_0_3_load_233 | 92 | 0.0060311 | 0.0015115 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4207-4_0_3_load_234 | 93 | 0.0017552 | 0.00043989 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4207-4_0_3_load_236 | 94 | 0.0013026 | 0.00032647 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4207-4_0_3_load_239 | 95 | 0.0018413 | 0.00046149 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4207-4_0_3_load_246 | 97 | 0.010604 | 0.0026577 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4207-4_0_3_load_251 | 98 | 0.0014451 | 0.00036218 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 48 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4207-4_0_3_line_0 |  | 0 | 1 | 0.018504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4207-4_0_3_line_1 |  | 1 | 2 | 0.015501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4207-4_0_3_line_2 |  | 2 | 8 | 0.010186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4207-4_0_3_line_3 |  | 3 | 4 | 0.034312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4207-4_0_3_line_4 |  | 3 | 5 | 0.040694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4207-4_0_3_line_5 |  | 4 | 9 | 0.02855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4207-4_0_3_line_6 |  | 5 | 10 | 0.052251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4207-4_0_3_line_7 |  | 6 | 7 | 0.011909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4207-4_0_3_line_8 |  | 7 | 23 | 0.01891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4207-4_0_3_line_9 |  | 8 | 29 | 0.0099861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4207-4_0_3_line_10 |  | 10 | 69 | 0.047264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4207-4_0_3_line_11 |  | 11 | 12 | 0.01476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4207-4_0_3_line_12 |  | 11 | 13 | 0.016968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4207-4_0_3_line_13 |  | 12 | 14 | 0.0048845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4207-4_0_3_line_14 |  | 13 | 15 | 0.022494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4207-4_0_3_line_15 |  | 13 | 16 | 0.014878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4207-4_0_3_line_16 |  | 14 | 17 | 0.02337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4207-4_0_3_line_17 |  | 15 | 18 | 0.00055543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4207-4_0_3_line_18 |  | 16 | 19 | 0.020236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4207-4_0_3_line_19 |  | 17 | 33 | 0.013597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4207-4_0_3_line_20 |  | 18 | 30 | 0.016878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4207-4_0_3_line_21 |  | 20 | 21 | 0.025084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4207-4_0_3_line_22 |  | 20 | 22 | 0.0032992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4207-4_0_3_line_23 |  | 21 | 23 | 0.0063806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4207-4_0_3_line_24 |  | 22 | 24 | 0.013231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4207-4_0_3_line_25 |  | 22 | 25 | 0.025556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4207-4_0_3_line_26 |  | 24 | 26 | 0.0084023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4207-4_0_3_line_27 |  | 25 | 27 | 0.013329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4207-4_0_3_line_28 |  | 25 | 28 | 0.016832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4207-4_0_3_line_29 |  | 26 | 63 | 0.012164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4207-4_0_3_line_30 |  | 27 | 48 | 0.015361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_4207-4_0_3_line_31 |  | 27 | 44 | 0.026971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4207-4_0_3_line_32 |  | 28 | 37 | 0.029119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4207-4_0_3_line_33 |  | 29 | 30 | 0.019872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4207-4_0_3_line_34 |  | 30 | 31 | 0.02726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4207-4_0_3_line_35 |  | 31 | 32 | 0.02042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4207-4_0_3_line_36 |  | 33 | 34 | 0.0090594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4207-4_0_3_line_37 |  | 33 | 35 | 0.014345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4207-4_0_3_line_38 |  | 34 | 36 | 0.015209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4207-4_0_3_line_39 |  | 35 | 37 | 0.00048871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4207-4_0_3_line_40 |  | 36 | 41 | 0.010035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4207-4_0_3_line_41 |  | 38 | 39 | 0.018739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4207-4_0_3_line_42 |  | 39 | 40 | 0.031659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4207-4_0_3_line_43 |  | 39 | 41 | 0.022811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4207-4_0_3_line_44 |  | 40 | 42 | 0.011619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4207-4_0_3_line_45 |  | 40 | 43 | 0.027252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4207-4_0_3_line_46 |  | 42 | 93 | 0.025962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4207-4_0_3_line_47 |  | 43 | 95 | 0.028604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4207-4_0_3_line_48 |  | 44 | 45 | 0.030782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4207-4_0_3_line_49 |  | 45 | 46 | 0.026922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4207-4_0_3_line_50 |  | 45 | 47 | 0.01774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4207-4_0_3_line_51 |  | 46 | 49 | 0.01748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4207-4_0_3_line_52 |  | 47 | 50 | 0.011889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4207-4_0_3_line_53 |  | 47 | 51 | 0.027787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4207-4_0_3_line_54 |  | 48 | 52 | 0.052391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4207-4_0_3_line_55 |  | 49 | 58 | 0.036018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4207-4_0_3_line_56 |  | 50 | 96 | 0.045574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4207-4_0_3_line_57 |  | 51 | 92 | 0.024702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4207-4_0_3_line_58 |  | 52 | 81 | 0.035403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4207-4_0_3_line_59 |  | 53 | 54 | 0.0048132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4207-4_0_3_line_60 |  | 53 | 55 | 0.0021149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4207-4_0_3_line_61 |  | 54 | 56 | 0.018871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4207-4_0_3_line_62 |  | 56 | 57 | 0.0076419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4207-4_0_3_line_63 |  | 57 | 63 | 0.0077548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4207-4_0_3_line_64 |  | 58 | 59 | 0.044067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4207-4_0_3_line_65 |  | 59 | 77 | 0.007172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4207-4_0_3_line_66 |  | 59 | 78 | 0.017032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4207-4_0_3_line_67 |  | 60 | 61 | 0.0031533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4207-4_0_3_line_68 |  | 60 | 62 | 0.017048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4207-4_0_3_line_69 |  | 62 | 79 | 0.005007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4207-4_0_3_line_70 |  | 64 | 65 | 0.0012751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4207-4_0_3_line_71 |  | 64 | 66 | 0.031308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4207-4_0_3_line_72 |  | 65 | 67 | 0.046125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4207-4_0_3_line_73 |  | 66 | 68 | 0.0051735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4207-4_0_3_line_74 |  | 67 | 69 | 0.028067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4207-4_0_3_line_75 |  | 67 | 70 | 0.045318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4207-4_0_3_line_76 |  | 68 | 71 | 0.0070558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4207-4_0_3_line_77 |  | 69 | 72 | 0.018246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4207-4_0_3_line_78 |  | 70 | 73 | 0.045649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4207-4_0_3_line_79 |  | 72 | 98 | 0.017163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4207-4_0_3_line_80 |  | 73 | 74 | 0.007311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4207-4_0_3_line_81 |  | 74 | 75 | 0.015703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4207-4_0_3_line_82 |  | 74 | 76 | 0.011077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4207-4_0_3_line_83 |  | 75 | 84 | 0.0068505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4207-4_0_3_line_84 |  | 77 | 79 | 0.036416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4207-4_0_3_line_85 |  | 78 | 80 | 0.015972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4207-4_0_3_line_86 |  | 80 | 88 | 0.0017795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4207-4_0_3_line_87 |  | 81 | 82 | 0.026462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4207-4_0_3_line_88 |  | 81 | 83 | 0.011242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4207-4_0_3_line_89 |  | 84 | 85 | 0.01198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4207-4_0_3_line_90 |  | 85 | 86 | 0.01468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4207-4_0_3_line_91 |  | 86 | 87 | 0.00035069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4207-4_0_3_line_92 |  | 87 | 88 | 0.017882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4207-4_0_3_line_93 |  | 89 | 90 | 0.025204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4207-4_0_3_line_94 |  | 89 | 91 | 0.010588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4207-4_0_3_line_95 |  | 90 | 92 | 0.024004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4207-4_0_3_line_96 |  | 93 | 94 | 0.026016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4207-4_0_3_line_97 |  | 96 | 97 | 0.01409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4207-4_0_3_trafo_70 | 0.63 MVA 20/0.4 kV | 99 | 48 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2653011.028 | 1248042.7163 | 2653019.6643 | 1248026.3518
1 | 2653011.028 | 1248042.7163 | 2653004.3864 | 1248056.7221
2 | 2653000.0221 | 1248065.9256 | 2653004.3864 | 1248056.7221
3 | 2653046.1047 | 1247976.2513 | 2653069.4275 | 1247981.0743 | 2653075.4257 | 1247989.6868
4 | 2653046.1047 | 1247976.2513 | 2653064.5722 | 1247939.9887
5 | 2653085.5112 | 1248013.3512 | 2653087.0844 | 1248006.3383 | 2653086.631 | 1248001.3086 | 2653079.6275 | 1247995.7199 | 2653075.4257 | 1247989.6868
6 | 2653088.2843 | 1247893.4279 | 2653064.5722 | 1247939.9887
7 | 2652972.9722 | 1248017.7455 | 2652982.9625 | 1248024.2277
8 | 2652972.9722 | 1248017.7455 | 2652966.5131 | 1248013.5544 | 2652957.08 | 1248007.4975
9 | 2652995.7435 | 1248074.9486 | 2653000.0221 | 1248065.9256
10 | 2653070.5343 | 1247865.0275 | 2653096.5025 | 1247876.3898 | 2653092.8425 | 1247883.6731 | 2653088.2843 | 1247893.4279
11 | 2652941.4577 | 1248064.9405 | 2652928.7983 | 1248057.3521
12 | 2652951.3032 | 1248077.8401 | 2652949.4994 | 1248071.8088 | 2652945.0781 | 1248067.1106 | 2652941.4577 | 1248064.9405
13 | 2652928.7983 | 1248057.3521 | 2652924.6088 | 1248054.8409
14 | 2652951.3032 | 1248077.8401 | 2652954.7571 | 1248076.7035 | 2652971.5813 | 1248085.2212
15 | 2652951.3032 | 1248077.8401 | 2652947.5582 | 1248089.6036 | 2652946.2135 | 1248091.7503
16 | 2652904.5641 | 1248042.8257 | 2652924.6088 | 1248054.8409
17 | 2652971.5813 | 1248085.2212 | 2652972.0768 | 1248085.4721
18 | 2652946.2135 | 1248091.7503 | 2652935.4716 | 1248108.8994
19 | 2652892.9017 | 1248035.835 | 2652904.5641 | 1248042.8257
20 | 2652987.2288 | 1248092.9045 | 2652979.4608 | 1248089.2104 | 2652972.0768 | 1248085.4721
21 | 2652930.6034 | 1247990.4971 | 2652951.7109 | 1248004.05
22 | 2652927.8272 | 1247988.7145 | 2652930.6034 | 1247990.4971
23 | 2652951.7109 | 1248004.05 | 2652957.08 | 1248007.4975
24 | 2652927.8272 | 1247988.7145 | 2652933.5823 | 1247976.8005
25 | 2652905.3948 | 1247976.3505 | 2652927.8272 | 1247988.7145
26 | 2652937.237 | 1247969.2346 | 2652933.5823 | 1247976.8005
27 | 2652905.3948 | 1247976.3505 | 2652894.0849 | 1247969.2448
28 | 2652905.3948 | 1247976.3505 | 2652902.0786 | 1247992.8528
29 | 2652937.237 | 1247969.2346 | 2652941.9615 | 1247959.4541 | 2652942.342 | 1247958.2085
30 | 2652894.0849 | 1247969.2448 | 2652901.4789 | 1247955.7804
31 | 2652894.0849 | 1247969.2448 | 2652870.3221 | 1247956.4879
32 | 2652896.0782 | 1248021.3458 | 2652899.3728 | 1248006.3171 | 2652902.0786 | 1247992.8528
33 | 2652987.2288 | 1248092.9045 | 2652995.7435 | 1248074.9486
34 | 2652987.2288 | 1248092.9045 | 2652985.3355 | 1248096.8903 | 2652974.8914 | 1248116.3102 | 2652974.5154 | 1248117.0134
35 | 2652964.888 | 1248135.0213 | 2652974.5154 | 1248117.0134
36 | 2652892.9017 | 1248035.835 | 2652891.2292 | 1248044.7387
37 | 2652892.9017 | 1248035.835 | 2652895.9735 | 1248021.8231
38 | 2652891.2292 | 1248044.7387 | 2652888.4212 | 1248059.6865
39 | 2652895.9735 | 1248021.8231 | 2652896.0782 | 1248021.3458
40 | 2652886.5685 | 1248069.5488 | 2652888.4212 | 1248059.6865
41 | 2652882.357 | 1248091.9681 | 2652898.0956 | 1248102.139
42 | 2652882.357 | 1248091.9681 | 2652877.6092 | 1248112.8733 | 2652880.2549 | 1248122.748
43 | 2652882.357 | 1248091.9681 | 2652886.5685 | 1248069.5488
44 | 2652880.2549 | 1248122.748 | 2652889.6775 | 1248129.5456
45 | 2652880.2549 | 1248122.748 | 2652857.7153 | 1248107.4309
46 | 2652910.7324 | 1248144.7347 | 2652889.6775 | 1248129.5456
47 | 2652857.7153 | 1248107.4309 | 2652834.0571 | 1248091.3537
48 | 2652843.2012 | 1247941.9283 | 2652870.3221 | 1247956.4879
49 | 2652843.2012 | 1247941.9283 | 2652856.5331 | 1247918.5396
50 | 2652827.361 | 1247933.8484 | 2652843.2012 | 1247941.9283
51 | 2652865.1894 | 1247903.3536 | 2652856.5331 | 1247918.5396
52 | 2652816.9685 | 1247928.0186 | 2652827.361 | 1247933.8484
53 | 2652827.361 | 1247933.8484 | 2652824.2347 | 1247944.8392 | 2652824.4292 | 1247961.1979
54 | 2652901.4789 | 1247955.7804 | 2652926.6976 | 1247909.8578
55 | 2652865.1894 | 1247903.3536 | 2652878.5531 | 1247896.9683 | 2652884.6907 | 1247895.5332 | 2652892.3022 | 1247882.7188
56 | 2652816.9685 | 1247928.0186 | 2652803.5759 | 1247919.0044 | 2652794.6861 | 1247910.6307 | 2652782.5692 | 1247898.2923
57 | 2652824.4292 | 1247961.1979 | 2652824.5239 | 1247969.1694 | 2652824.3518 | 1247985.8988
58 | 2652943.7388 | 1247878.8263 | 2652926.6976 | 1247909.8578
59 | 2652958.6019 | 1247922.89 | 2652956.2643 | 1247927.0974
60 | 2652959.629 | 1247921.0412 | 2652958.6019 | 1247922.89
61 | 2652947.0993 | 1247943.5936 | 2652956.2643 | 1247927.0974
62 | 2652944.6079 | 1247950.7922 | 2652946.4502 | 1247944.7619 | 2652947.0993 | 1247943.5936
63 | 2652944.6079 | 1247950.7922 | 2652942.342 | 1247958.2085
64 | 2652894.3915 | 1247842.617 | 2652902.1721 | 1247866.1024 | 2652892.3022 | 1247882.7188
65 | 2652894.3915 | 1247842.617 | 2652887.8408 | 1247845.5372
66 | 2652894.3915 | 1247842.617 | 2652900.0706 | 1247840.0882 | 2652909.5405 | 1247834.864
67 | 2652837.2755 | 1247872.1504 | 2652835.3051 | 1247874.6123
68 | 2652837.2755 | 1247872.1504 | 2652842.4993 | 1247865.6258 | 2652849.6238 | 1247860.6508
69 | 2652849.6238 | 1247860.6508 | 2652853.729 | 1247857.7841
70 | 2653020.5331 | 1247894.5006 | 2653021.1749 | 1247893.3988
71 | 2653013.4668 | 1247923.0996 | 2653018.6237 | 1247912.8403 | 2653016.1067 | 1247902.0994 | 2653020.5331 | 1247894.5006
72 | 2653044.7539 | 1247853.756 | 2653024.8887 | 1247887.0232 | 2653021.1749 | 1247893.3988
73 | 2653013.4668 | 1247923.0996 | 2653011.1434 | 1247927.722
74 | 2653070.5343 | 1247865.0275 | 2653044.7539 | 1247853.756
75 | 2653044.7539 | 1247853.756 | 2653003.5284 | 1247834.9359
76 | 2653007.9746 | 1247934.0262 | 2653011.1434 | 1247927.722
77 | 2653070.5343 | 1247865.0275 | 2653062.2567 | 1247881.2878
78 | 2653003.5284 | 1247834.9359 | 2652980.4377 | 1247824.3947 | 2652979.1654 | 1247819.7135 | 2652979.9494 | 1247814.806 | 2652982.7801 | 1247810.7397 | 2652986.1868 | 1247806.4338
79 | 2653054.4705 | 1247896.5827 | 2653062.2567 | 1247881.2878
80 | 2652986.8251 | 1247799.2346 | 2652986.942 | 1247803.9055 | 2652986.1868 | 1247806.4338
81 | 2652986.8251 | 1247799.2346 | 2652972.6536 | 1247805.9989
82 | 2652986.8251 | 1247799.2346 | 2652995.1817 | 1247791.9633
83 | 2652972.6536 | 1247805.9989 | 2652966.4712 | 1247808.9499
84 | 2652887.8408 | 1247845.5372 | 2652879.2799 | 1247849.3536 | 2652865.6259 | 1247852.7008 | 2652855.2968 | 1247856.6893 | 2652853.729 | 1247857.7841
85 | 2652909.5405 | 1247834.864 | 2652920.6383 | 1247828.7417 | 2652923.5971 | 1247827.286
86 | 2652925.1938 | 1247826.5005 | 2652923.5971 | 1247827.286
87 | 2652920.7319 | 1247865.6342 | 2652943.7388 | 1247878.8263
88 | 2652953.4757 | 1247884.4948 | 2652943.7388 | 1247878.8263
89 | 2652966.4712 | 1247808.9499 | 2652960.5977 | 1247811.7534 | 2652955.4907 | 1247813.7183
90 | 2652941.7894 | 1247818.99 | 2652955.4907 | 1247813.7183
91 | 2652941.4621 | 1247819.1159 | 2652941.7894 | 1247818.99
92 | 2652925.1938 | 1247826.5005 | 2652935.688 | 1247821.3376 | 2652941.4621 | 1247819.1159
93 | 2652823.8454 | 1248035.1043 | 2652824.1047 | 1248009.9019
94 | 2652823.7364 | 1248045.6922 | 2652823.8454 | 1248035.1043
95 | 2652824.1047 | 1248009.9019 | 2652824.3518 | 1247985.8988
96 | 2652910.7324 | 1248144.7347 | 2652931.8309 | 1248159.9553
97 | 2652782.5692 | 1247898.2923 | 2652775.6698 | 1247891.1371 | 2652772.9773 | 1247887.9786

## bus_geodata
| x | y | coords
0 | 2653019.6643 | 1248026.3518
1 | 2653011.028 | 1248042.7163
2 | 2653004.3864 | 1248056.7221
3 | 2653046.1047 | 1247976.2513
4 | 2653075.4257 | 1247989.6868
5 | 2653064.5722 | 1247939.9887
6 | 2652982.9625 | 1248024.2277
7 | 2652972.9722 | 1248017.7455
8 | 2653000.0221 | 1248065.9256
9 | 2653085.5112 | 1248013.3512
10 | 2653088.2843 | 1247893.4279
11 | 2652941.4577 | 1248064.9405
12 | 2652928.7983 | 1248057.3521
13 | 2652951.3032 | 1248077.8401
14 | 2652924.6088 | 1248054.8409
15 | 2652971.5813 | 1248085.2212
16 | 2652946.2135 | 1248091.7503
17 | 2652904.5641 | 1248042.8257
18 | 2652972.0768 | 1248085.4721
19 | 2652935.4716 | 1248108.8994
20 | 2652930.6034 | 1247990.4971
21 | 2652951.7109 | 1248004.05
22 | 2652927.8272 | 1247988.7145
23 | 2652957.08 | 1248007.4975
24 | 2652933.5823 | 1247976.8005
25 | 2652905.3948 | 1247976.3505
26 | 2652937.237 | 1247969.2346
27 | 2652894.0849 | 1247969.2448
28 | 2652902.0786 | 1247992.8528
29 | 2652995.7435 | 1248074.9486
30 | 2652987.2288 | 1248092.9045
31 | 2652974.5154 | 1248117.0134
32 | 2652964.888 | 1248135.0213
33 | 2652892.9017 | 1248035.835
34 | 2652891.2292 | 1248044.7387
35 | 2652895.9735 | 1248021.8231
36 | 2652888.4212 | 1248059.6865
37 | 2652896.0782 | 1248021.3458
38 | 2652898.0956 | 1248102.139
39 | 2652882.357 | 1248091.9681
40 | 2652880.2549 | 1248122.748
41 | 2652886.5685 | 1248069.5488
42 | 2652889.6775 | 1248129.5456
43 | 2652857.7153 | 1248107.4309
44 | 2652870.3221 | 1247956.4879
45 | 2652843.2012 | 1247941.9283
46 | 2652856.5331 | 1247918.5396
47 | 2652827.3611 | 1247933.8484
48 | 2652901.4789 | 1247955.7804
49 | 2652865.1894 | 1247903.3536
50 | 2652816.9685 | 1247928.0186
51 | 2652824.4292 | 1247961.1979
52 | 2652926.6976 | 1247909.8578
53 | 2652958.6019 | 1247922.89
54 | 2652956.2643 | 1247927.0974
55 | 2652959.629 | 1247921.0412
56 | 2652947.0993 | 1247943.5936
57 | 2652944.6079 | 1247950.7922
58 | 2652892.3022 | 1247882.7188
59 | 2652894.3915 | 1247842.617
60 | 2652837.2755 | 1247872.1504
61 | 2652835.3051 | 1247874.6123
62 | 2652849.6238 | 1247860.6508
63 | 2652942.342 | 1247958.2085
64 | 2653020.5331 | 1247894.5006
65 | 2653021.1749 | 1247893.3988
66 | 2653013.4668 | 1247923.0996
67 | 2653044.7539 | 1247853.756
68 | 2653011.1434 | 1247927.722
69 | 2653070.5343 | 1247865.0275
70 | 2653003.5284 | 1247834.9359
71 | 2653007.9746 | 1247934.0262
72 | 2653062.2567 | 1247881.2878
73 | 2652986.1868 | 1247806.4338
74 | 2652986.8251 | 1247799.2346
75 | 2652972.6536 | 1247805.9989
76 | 2652995.1817 | 1247791.9633
77 | 2652887.8408 | 1247845.5372
78 | 2652909.5405 | 1247834.864
79 | 2652853.729 | 1247857.7841
80 | 2652923.5971 | 1247827.286
81 | 2652943.7388 | 1247878.8263
82 | 2652920.7319 | 1247865.6342
83 | 2652953.4757 | 1247884.4948
84 | 2652966.4712 | 1247808.9499
85 | 2652955.4907 | 1247813.7183
86 | 2652941.7894 | 1247818.99
87 | 2652941.4621 | 1247819.1159
88 | 2652925.1938 | 1247826.5005
89 | 2652823.8454 | 1248035.1043
90 | 2652824.1047 | 1248009.9019
91 | 2652823.7364 | 1248045.6922
92 | 2652824.3518 | 1247985.8988
93 | 2652910.7324 | 1248144.7347
94 | 2652931.8309 | 1248159.9553
95 | 2652834.0571 | 1248091.3537
96 | 2652782.5692 | 1247898.2923
97 | 2652772.9773 | 1247887.9786
98 | 2653054.4705 | 1247896.5827
99 | 2652894.0849 | 1247969.2448

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1