## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4239-11_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4239-11_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4239-11_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4239-11_0_3_node_37 | 0.4 | n |  | TRUE
4 | bus_LV_4239-11_0_3_node_38 | 0.4 | n |  | TRUE
5 | bus_LV_4239-11_0_3_node_44 | 0.4 | n |  | TRUE
6 | bus_LV_4239-11_0_3_node_40 | 0.4 | n |  | TRUE
7 | bus_LV_4239-11_0_3_node_51 | 0.4 | n |  | TRUE
8 | bus_LV_4239-11_0_3_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_4239-11_0_3_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_4239-11_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_4239-11_0_3_node_78 | 0.4 | n |  | TRUE
12 | bus_LV_4239-11_0_3_node_79 | 0.4 | n |  | TRUE
13 | bus_LV_4239-11_0_3_node_30 | 0.4 | n |  | TRUE
14 | bus_LV_4239-11_0_3_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_4239-11_0_3_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_4239-11_0_3_node_58 | 0.4 | n |  | TRUE
17 | bus_LV_4239-11_0_3_node_48 | 0.4 | n |  | TRUE
18 | bus_LV_4239-11_0_3_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_4239-11_0_3_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_4239-11_0_3_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_4239-11_0_3_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_4239-11_0_3_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_4239-11_0_3_node_57 | 0.4 | n |  | TRUE
24 | bus_LV_4239-11_0_3_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_4239-11_0_3_node_54 | 0.4 | n |  | TRUE
26 | bus_LV_4239-11_0_3_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_4239-11_0_3_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_4239-11_0_3_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_4239-11_0_3_node_76 | 0.4 | n |  | TRUE
30 | bus_LV_4239-11_0_3_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_4239-11_0_3_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_4239-11_0_3_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_4239-11_0_3_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_4239-11_0_3_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_4239-11_0_3_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_4239-11_0_3_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_4239-11_0_3_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_4239-11_0_3_node_46 | 0.4 | n |  | TRUE
39 | bus_LV_4239-11_0_3_node_53 | 0.4 | n |  | TRUE
40 | bus_LV_4239-11_0_3_node_64 | 0.4 | n |  | TRUE
41 | bus_LV_4239-11_0_3_node_45 | 0.4 | n |  | TRUE
42 | bus_LV_4239-11_0_3_node_55 | 0.4 | n |  | TRUE
43 | bus_LV_4239-11_0_3_node_52 | 0.4 | n |  | TRUE
44 | bus_LV_4239-11_0_3_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_4239-11_0_3_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_4239-11_0_3_node_25 | 0.4 | n |  | TRUE
47 | bus_LV_4239-11_0_3_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_4239-11_0_3_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_4239-11_0_3_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_4239-11_0_3_node_66 | 0.4 | n |  | TRUE
51 | bus_LV_4239-11_0_3_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_4239-11_0_3_node_65 | 0.4 | n |  | TRUE
53 | bus_LV_4239-11_0_3_node_29 | 0.4 | n |  | TRUE
54 | bus_LV_4239-11_0_3_node_31 | 0.4 | n |  | TRUE
55 | bus_LV_4239-11_0_3_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_4239-11_0_3_node_62 | 0.4 | n |  | TRUE
57 | bus_LV_4239-11_0_3_node_47 | 0.4 | n |  | TRUE
58 | bus_LV_4239-11_0_3_node_73 | 0.4 | n |  | TRUE
59 | bus_LV_4239-11_0_3_node_59 | 0.4 | n |  | TRUE
60 | bus_LV_4239-11_0_3_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_4239-11_0_3_node_34 | 0.4 | n |  | TRUE
62 | bus_LV_4239-11_0_3_node_36 | 0.4 | n |  | TRUE
63 | bus_LV_4239-11_0_3_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_4239-11_0_3_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_4239-11_0_3_node_42 | 0.4 | n |  | TRUE
66 | bus_LV_4239-11_0_3_node_71 | 0.4 | n |  | TRUE
67 | bus_LV_4239-11_0_3_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_4239-11_0_3_node_89 | 0.4 | n |  | TRUE
69 | bus_LV_4239-11_0_3_node_101 | 0.4 | n |  | TRUE
70 | bus_LV_4239-11_0_3_node_69 | 0.4 | n |  | TRUE
71 | bus_LV_4239-11_0_3_node_88 | 0.4 | n |  | TRUE
72 | bus_LV_4239-11_0_3_node_60 | 0.4 | n |  | TRUE
73 | bus_LV_4239-11_0_3_node_56 | 0.4 | n |  | TRUE
74 | bus_LV_4239-11_0_3_node_72 | 0.4 | n |  | TRUE
75 | bus_LV_4239-11_0_3_node_67 | 0.4 | n |  | TRUE
76 | bus_LV_4239-11_0_3_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_4239-11_0_3_node_75 | 0.4 | n |  | TRUE
78 | bus_MV_435_0_node_33 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4239-11_0_3_load_0 | 0 | 0.0058166 | 0.0014578 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4239-11_0_3_load_1 | 1 | 0.0051936 | 0.0013016 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4239-11_0_3_load_38 | 4 | 0.0051348 | 0.0012869 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4239-11_0_3_load_44 | 5 | 0.003355 | 0.00084084 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4239-11_0_3_load_40 | 6 | 0.003135 | 0.00078572 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4239-11_0_3_load_3 | 8 | 0.00194 | 0.0004862 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4239-11_0_3_load_5 | 10 | 0.0035373 | 0.00088652 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4239-11_0_3_load_78 | 11 | 0.004601 | 0.0011531 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4239-11_0_3_load_28 | 15 | 0.0047327 | 0.0011861 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4239-11_0_3_load_58 | 16 | 0.0038077 | 0.00095429 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4239-11_0_3_load_48 | 17 | 0.0036942 | 0.00092584 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4239-11_0_3_load_7 | 18 | 0.0066355 | 0.001663 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4239-11_0_3_load_8 | 19 | 0.003316 | 0.00083106 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4239-11_0_3_load_9 | 20 | 0.0033195 | 0.00083195 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4239-11_0_3_load_10 | 21 | 0.0033195 | 0.00083195 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4239-11_0_3_load_11 | 22 | 0.003316 | 0.00083107 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4239-11_0_3_load_57 | 23 | 0.003316 | 0.00083106 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4239-11_0_3_load_14 | 24 | 0.00083314 | 0.0002088 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4239-11_0_3_load_12 | 26 | 0.00083314 | 0.0002088 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4239-11_0_3_load_13 | 27 | 0.00083226 | 0.00020858 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4239-11_0_3_load_15 | 28 | 0.00060943 | 0.00015274 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4239-11_0_3_load_76 | 29 | 0.0013096 | 0.00032823 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4239-11_0_3_load_16 | 30 | 0.0032054 | 0.00080334 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4239-11_0_3_load_17 | 31 | 0.0034494 | 0.00086451 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4239-11_0_3_load_19 | 33 | 0.0011383 | 0.00028528 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4239-11_0_3_load_20 | 34 | 0.0024323 | 0.00060959 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4239-11_0_3_load_21 | 35 | 0.0038135 | 0.00095576 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4239-11_0_3_load_63 | 37 | 0.0033862 | 0.00084865 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4239-11_0_3_load_64 | 40 | 0.0034234 | 0.00085799 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4239-11_0_3_load_45 | 41 | 0.004719 | 0.0011827 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4239-11_0_3_load_55 | 42 | 0.0041261 | 0.0010341 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4239-11_0_3_load_52 | 43 | 0.0066359 | 0.0016631 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4239-11_0_3_load_23 | 44 | 0.003316 | 0.00083106 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4239-11_0_3_load_24 | 45 | 0.0033195 | 0.00083195 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4239-11_0_3_load_25 | 46 | 0.007591 | 0.0019025 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4239-11_0_3_load_26 | 47 | 0.0066359 | 0.0016631 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4239-11_0_3_load_35 | 49 | 0.00090321 | 0.00022637 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4239-11_0_3_load_66 | 50 | 0.031914 | 0.0079984 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4239-11_0_3_load_33 | 51 | 0.0016654 | 0.00041739 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4239-11_0_3_load_65 | 52 | 0.0033195 | 0.00083194 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4239-11_0_3_load_29 | 53 | 0.0047177 | 0.0011824 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4239-11_0_3_load_31 | 54 | 0.0047205 | 0.0011831 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4239-11_0_3_load_39 | 55 | 0.004722 | 0.0011835 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4239-11_0_3_load_73 | 58 | 0.0013096 | 0.00032822 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4239-11_0_3_load_59 | 59 | 0.0047327 | 0.0011861 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4239-11_0_3_load_34 | 61 | 0.00083226 | 0.00020858 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4239-11_0_3_load_36 | 62 | 0.00083268 | 0.00020869 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4239-11_0_3_load_50 | 64 | 0.0053851 | 0.0013496 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4239-11_0_3_load_68 | 67 | 0.0026618 | 0.00066711 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4239-11_0_3_load_89 | 68 | 0.0012984 | 0.00032541 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4239-11_0_3_load_101 | 69 | 0.00056228 | 0.00014092 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4239-11_0_3_load_69 | 70 | 0.0030267 | 0.00075856 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4239-11_0_3_load_88 | 71 | 0.010896 | 0.0027307 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4239-11_0_3_load_60 | 72 | 0.00083226 | 0.00020858 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4239-11_0_3_load_56 | 73 | 0.0033178 | 0.00083153 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4239-11_0_3_load_72 | 74 | 0.0029439 | 0.00073781 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4239-11_0_3_load_67 | 75 | 0.003316 | 0.00083106 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4239-11_0_3_load_70 | 76 | 0.0052001 | 0.0013033 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4239-11_0_3_load_75 | 77 | 0.030642 | 0.0076796 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4239-11_0_3_line_0 |  | 0 | 1 | 0.027573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4239-11_0_3_line_1 |  | 1 | 2 | 0.01447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4239-11_0_3_line_2 |  | 2 | 3 | 0.029099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4239-11_0_3_line_3 |  | 2 | 4 | 0.015702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4239-11_0_3_line_4 |  | 3 | 5 | 0.030184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4239-11_0_3_line_5 |  | 3 | 6 | 0.015421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4239-11_0_3_line_6 |  | 4 | 7 | 0.0069208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4239-11_0_3_line_7 |  | 5 | 40 | 0.002191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4239-11_0_3_line_8 |  | 7 | 63 | 0.008978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4239-11_0_3_line_9 |  | 7 | 64 | 0.013495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4239-11_0_3_line_10 |  | 8 | 9 | 0.014224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4239-11_0_3_line_11 |  | 9 | 10 | 0.021923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4239-11_0_3_line_12 |  | 10 | 11 | 0.03169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4239-11_0_3_line_13 |  | 11 | 12 | 0.029933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4239-11_0_3_line_14 |  | 12 | 35 | 0.044725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4239-11_0_3_line_15 |  | 13 | 14 | 0.023025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4239-11_0_3_line_16 |  | 13 | 15 | 0.019545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4239-11_0_3_line_17 |  | 14 | 56 | 0.10883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4239-11_0_3_line_18 |  | 15 | 53 | 8.2015e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4239-11_0_3_line_19 |  | 16 | 17 | 0.025597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4239-11_0_3_line_20 |  | 17 | 38 | 0.014581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4239-11_0_3_line_21 |  | 18 | 19 | 0.0054764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4239-11_0_3_line_22 |  | 18 | 20 | 0.019468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4239-11_0_3_line_23 |  | 19 | 21 | 4.3965e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4239-11_0_3_line_24 |  | 20 | 22 | 4.3966e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4239-11_0_3_line_25 |  | 21 | 23 | 0.025073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4239-11_0_3_line_26 |  | 22 | 24 | 0.0057951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4239-11_0_3_line_27 |  | 23 | 25 | 0.010704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4239-11_0_3_line_28 |  | 24 | 26 | 0.018814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4239-11_0_3_line_29 |  | 25 | 73 | 0.014596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4239-11_0_3_line_30 |  | 25 | 43 | 0.016679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4239-11_0_3_line_31 |  | 26 | 27 | 4.3966e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4239-11_0_3_line_32 |  | 27 | 28 | 0.011566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4239-11_0_3_line_33 |  | 28 | 29 | 0.010532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4239-11_0_3_line_34 |  | 30 | 31 | 0.0071234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4239-11_0_3_line_35 |  | 30 | 32 | 0.027783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4239-11_0_3_line_36 |  | 31 | 33 | 0.021976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4239-11_0_3_line_37 |  | 32 | 34 | 0.0062819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4239-11_0_3_line_38 |  | 32 | 35 | 0.010675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4239-11_0_3_line_39 |  | 33 | 36 | 0.019566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4239-11_0_3_line_40 |  | 34 | 37 | 0.0098811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4239-11_0_3_line_41 |  | 36 | 38 | 0.009074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4239-11_0_3_line_42 |  | 36 | 39 | 0.021155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4239-11_0_3_line_43 |  | 37 | 40 | 0.019834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4239-11_0_3_line_44 |  | 38 | 41 | 0.018264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4239-11_0_3_line_45 |  | 39 | 42 | 0.006124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4239-11_0_3_line_46 |  | 39 | 43 | 0.02428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_4239-11_0_3_line_47 |  | 41 | 57 | 0.013829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4239-11_0_3_line_48 |  | 42 | 74 | 0.033573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4239-11_0_3_line_49 |  | 44 | 45 | 8.6356e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4239-11_0_3_line_50 |  | 44 | 46 | 0.024141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4239-11_0_3_line_51 |  | 45 | 47 | 0.0012846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4239-11_0_3_line_52 |  | 46 | 48 | 0.010711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4239-11_0_3_line_53 |  | 47 | 49 | 0.023666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4239-11_0_3_line_54 |  | 48 | 50 | 0.005209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4239-11_0_3_line_55 |  | 49 | 51 | 0.0016909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4239-11_0_3_line_56 |  | 50 | 52 | 0.0074467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4239-11_0_3_line_57 |  | 51 | 61 | 0.024907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4239-11_0_3_line_58 |  | 52 | 75 | 0.0071321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4239-11_0_3_line_59 |  | 53 | 54 | 0.028648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4239-11_0_3_line_60 |  | 54 | 55 | 0.00073027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4239-11_0_3_line_61 |  | 55 | 57 | 0.014134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4239-11_0_3_line_62 |  | 56 | 58 | 0.11256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4239-11_0_3_line_63 |  | 57 | 60 | 0.023212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4239-11_0_3_line_64 |  | 59 | 60 | 0.014786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4239-11_0_3_line_65 |  | 60 | 72 | 0.0079172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4239-11_0_3_line_66 |  | 61 | 62 | 8.5192e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4239-11_0_3_line_67 |  | 63 | 68 | 0.0043417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4239-11_0_3_line_68 |  | 65 | 66 | 0.028984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4239-11_0_3_line_69 |  | 65 | 67 | 0.0080525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4239-11_0_3_line_70 |  | 66 | 69 | 0.070709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4239-11_0_3_line_71 |  | 67 | 70 | 0.031828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4239-11_0_3_line_72 |  | 68 | 71 | 0.059394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4239-11_0_3_line_73 |  | 69 | 77 | 0.05145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4239-11_0_3_line_74 |  | 70 | 76 | 0.010042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4239-11_0_3_line_75 |  | 73 | 75 | 0.015399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4239-11_0_3_line_76 |  | 74 | 76 | 0.017468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4239-11_0_3_trafo_52 | 0.63 MVA 20/0.4 kV | 78 | 43 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2672283.3555 | 1227101.1398 | 2672275.5342 | 1227102.6185 | 2672255.925 | 1227103.0008
1 | 2672241.4578 | 1227103.2829 | 2672255.925 | 1227103.0008
2 | 2672239.6884 | 1227074.2423 | 2672241.4578 | 1227103.2829
3 | 2672241.4578 | 1227103.2829 | 2672225.7555 | 1227103.2737
4 | 2672239.6884 | 1227074.2423 | 2672253.783 | 1227071.9674 | 2672259.9799 | 1227065.3383 | 2672261.7648 | 1227058.7427
5 | 2672239.6884 | 1227074.2423 | 2672224.2721 | 1227074.6039
6 | 2672218.9175 | 1227103.8987 | 2672221.252 | 1227103.271 | 2672225.7555 | 1227103.2737
7 | 2672261.7648 | 1227058.7427 | 2672262.3372 | 1227056.6278
8 | 2672218.9175 | 1227103.8987 | 2672219.6741 | 1227107.7549 | 2672220.1941 | 1227111.1189 | 2672220.7057 | 1227112.6817
9 | 2672218.9175 | 1227103.8987 | 2672205.8912 | 1227107.4225
10 | 2672300.7555 | 1226947.5445 | 2672314.9711 | 1226947.0654
11 | 2672300.7555 | 1226947.5445 | 2672302.751 | 1226969.3769
12 | 2672305.9699 | 1227000.9026 | 2672302.9764 | 1226971.8431 | 2672302.751 | 1226969.3769
13 | 2672309.037 | 1227030.6779 | 2672305.9699 | 1227000.9026
14 | 2672309.037 | 1227030.6779 | 2672292.9306 | 1227017.6291 | 2672275.6848 | 1227019.7433 | 2672269.0839 | 1227020.2589
15 | 2672272.1727 | 1226889.0031 | 2672271.7353 | 1226888.1973 | 2672265.8789 | 1226877.3857 | 2672261.2012 | 1226868.7454
16 | 2672272.1727 | 1226889.0031 | 2672264.8901 | 1226892.6393 | 2672263.3012 | 1226895.5331 | 2672256.1302 | 1226899.3082
17 | 2672261.2012 | 1226868.7454 | 2672250.2595 | 1226848.5326 | 2672217.9526 | 1226788.8677 | 2672215.5304 | 1226782.3563 | 2672216.145 | 1226776.0596 | 2672216.4524 | 1226771.3491
18 | 2672256.1302 | 1226899.3082 | 2672256.0577 | 1226899.3464
19 | 2672245.1397 | 1226940.7879 | 2672267.3591 | 1226928.08
20 | 2672232.4824 | 1226948.027 | 2672245.1397 | 1226940.7879
21 | 2672170.6742 | 1226921.1657 | 2672170.1646 | 1226926.6184
22 | 2672172.4856 | 1226901.7825 | 2672170.6742 | 1226921.1657
23 | 2672170.1605 | 1226926.6622 | 2672170.1646 | 1226926.6184
24 | 2672172.4856 | 1226901.7825 | 2672172.4897 | 1226901.7387
25 | 2672170.1605 | 1226926.6622 | 2672167.8275 | 1226951.6268
26 | 2672173.0289 | 1226895.9687 | 2672172.4897 | 1226901.7387
27 | 2672166.8315 | 1226962.2844 | 2672167.8275 | 1226951.6268
28 | 2672173.0289 | 1226895.9687 | 2672174.7795 | 1226877.2362
29 | 2672166.8315 | 1226962.2844 | 2672152.2756 | 1226961.2016
30 | 2672166.8315 | 1226962.2844 | 2672183.4644 | 1226963.5185
31 | 2672174.7795 | 1226877.2362 | 2672174.7836 | 1226877.1924
32 | 2672175.8598 | 1226865.6769 | 2672174.7836 | 1226877.1924
33 | 2672176.8397 | 1226855.1906 | 2672175.8598 | 1226865.6769
34 | 2672246.139 | 1226996.1797 | 2672242.9848 | 1226989.7927
35 | 2672258.4408 | 1227021.0903 | 2672246.139 | 1226996.1797
36 | 2672233.2542 | 1226970.0887 | 2672242.9848 | 1226989.7927
37 | 2672258.4408 | 1227021.0903 | 2672259.4231 | 1227027.295
38 | 2672258.4408 | 1227021.0903 | 2672269.0839 | 1227020.2589
39 | 2672224.5905 | 1226952.5453 | 2672233.2542 | 1226970.0887
40 | 2672259.4231 | 1227027.295 | 2672260.088 | 1227031.495 | 2672260.8729 | 1227037.0688
41 | 2672224.5905 | 1226952.5453 | 2672232.4824 | 1226948.027
42 | 2672207.6776 | 1226965.3152 | 2672224.5905 | 1226952.5453
43 | 2672260.8729 | 1227037.0688 | 2672263.1859 | 1227053.4916 | 2672262.3372 | 1227056.6278
44 | 2672232.4824 | 1226948.027 | 2672223.9874 | 1226931.8584
45 | 2672207.6776 | 1226965.3152 | 2672204.4448 | 1226970.5164
46 | 2672207.6776 | 1226965.3152 | 2672183.4644 | 1226963.5185
47 | 2672217.555 | 1226919.6159 | 2672223.9874 | 1226931.8584
48 | 2672190.9842 | 1227001.0061 | 2672196.9093 | 1226982.6404 | 2672204.4448 | 1226970.5164
49 | 2672120.6436 | 1226923.824 | 2672120.635 | 1226923.91
50 | 2672118.2461 | 1226947.933 | 2672120.635 | 1226923.91
51 | 2672120.7707 | 1226922.5457 | 2672120.6436 | 1226923.824
52 | 2672117.1862 | 1226958.5913 | 2672118.2461 | 1226947.933
53 | 2672120.7707 | 1226922.5457 | 2672123.1126 | 1226898.9957
54 | 2672117.1862 | 1226958.5913 | 2672122.3808 | 1226958.9777
55 | 2672123.1126 | 1226898.9957 | 2672123.2799 | 1226897.313
56 | 2672129.807 | 1226959.5301 | 2672122.3808 | 1226958.9777
57 | 2672125.7446 | 1226872.5281 | 2672123.2799 | 1226897.313
58 | 2672129.807 | 1226959.5301 | 2672136.9194 | 1226960.0592
59 | 2672256.0577 | 1226899.3464 | 2672230.7076 | 1226912.6918
60 | 2672230.7076 | 1226912.6918 | 2672230.0614 | 1226913.032
61 | 2672217.555 | 1226919.6159 | 2672230.0614 | 1226913.032
62 | 2672216.4524 | 1226771.3491 | 2672187.0716 | 1226784.0344 | 2672163.6338 | 1226800.4276 | 2672143.5086 | 1226818.0508 | 2672127.9463 | 1226837.8755
63 | 2672217.555 | 1226919.6159 | 2672206.7463 | 1226899.0601
64 | 2672206.7463 | 1226899.0601 | 2672219.6653 | 1226891.8682
65 | 2672206.7463 | 1226899.0601 | 2672203.0647 | 1226892.0509
66 | 2672125.7531 | 1226872.4433 | 2672125.7446 | 1226872.5281
67 | 2672220.7057 | 1227112.6817 | 2672224.9647 | 1227111.8384
68 | 2672186.162 | 1227068.1777 | 2672158.775 | 1227058.4614
69 | 2672186.162 | 1227068.1777 | 2672186.6695 | 1227060.1412
70 | 2672158.775 | 1227058.4614 | 2672092.0328 | 1227035.1105
71 | 2672186.6695 | 1227060.1412 | 2672188.6754 | 1227028.3769
72 | 2672284.0581 | 1227112.8065 | 2672261.4996 | 1227111.8097 | 2672235.3079 | 1227109.7904 | 2672224.9647 | 1227111.8384
73 | 2672062.6033 | 1227001.0523 | 2672068.4425 | 1227026.857 | 2672092.0328 | 1227035.1105
74 | 2672189.3568 | 1227018.3577 | 2672188.9768 | 1227023.6046 | 2672188.6754 | 1227028.3769
75 | 2672152.2756 | 1226961.2016 | 2672136.9194 | 1226960.0592
76 | 2672189.3568 | 1227018.3577 | 2672190.5064 | 1227002.487 | 2672190.9842 | 1227001.0061

## bus_geodata
| x | y | coords
0 | 2672283.3555 | 1227101.1398
1 | 2672255.925 | 1227103.0008
2 | 2672241.4578 | 1227103.2829
3 | 2672239.6884 | 1227074.2423
4 | 2672225.7555 | 1227103.2737
5 | 2672261.7648 | 1227058.7427
6 | 2672224.2721 | 1227074.6039
7 | 2672218.9175 | 1227103.8987
8 | 2672314.9711 | 1226947.0654
9 | 2672300.7555 | 1226947.5445
10 | 2672302.751 | 1226969.3769
11 | 2672305.9699 | 1227000.9026
12 | 2672309.037 | 1227030.6779
13 | 2672272.1727 | 1226889.0031
14 | 2672261.2012 | 1226868.7454
15 | 2672256.1302 | 1226899.3082
16 | 2672267.3591 | 1226928.08
17 | 2672245.1397 | 1226940.7879
18 | 2672170.6742 | 1226921.1657
19 | 2672170.1646 | 1226926.6184
20 | 2672172.4856 | 1226901.7825
21 | 2672170.1605 | 1226926.6622
22 | 2672172.4897 | 1226901.7387
23 | 2672167.8275 | 1226951.6268
24 | 2672173.0289 | 1226895.9687
25 | 2672166.8315 | 1226962.2844
26 | 2672174.7795 | 1226877.2362
27 | 2672174.7836 | 1226877.1924
28 | 2672175.8598 | 1226865.677
29 | 2672176.8397 | 1226855.1906
30 | 2672246.139 | 1226996.1797
31 | 2672242.9848 | 1226989.7927
32 | 2672258.4408 | 1227021.0903
33 | 2672233.2542 | 1226970.0887
34 | 2672259.4231 | 1227027.295
35 | 2672269.0839 | 1227020.2589
36 | 2672224.5905 | 1226952.5453
37 | 2672260.8729 | 1227037.0688
38 | 2672232.4824 | 1226948.027
39 | 2672207.6776 | 1226965.3152
40 | 2672262.3372 | 1227056.6278
41 | 2672223.9874 | 1226931.8584
42 | 2672204.4448 | 1226970.5164
43 | 2672183.4644 | 1226963.5186
44 | 2672120.635 | 1226923.91
45 | 2672120.6436 | 1226923.824
46 | 2672118.2461 | 1226947.933
47 | 2672120.7707 | 1226922.5457
48 | 2672117.1862 | 1226958.5913
49 | 2672123.1126 | 1226898.9957
50 | 2672122.3808 | 1226958.9777
51 | 2672123.2799 | 1226897.313
52 | 2672129.807 | 1226959.5301
53 | 2672256.0577 | 1226899.3464
54 | 2672230.7076 | 1226912.6918
55 | 2672230.0614 | 1226913.032
56 | 2672216.4524 | 1226771.3491
57 | 2672217.555 | 1226919.6159
58 | 2672127.9463 | 1226837.8755
59 | 2672219.6653 | 1226891.8682
60 | 2672206.7463 | 1226899.0601
61 | 2672125.7446 | 1226872.5281
62 | 2672125.7531 | 1226872.4433
63 | 2672220.7057 | 1227112.6817
64 | 2672205.8912 | 1227107.4225
65 | 2672186.162 | 1227068.1777
66 | 2672158.775 | 1227058.4614
67 | 2672186.6695 | 1227060.1412
68 | 2672224.9647 | 1227111.8384
69 | 2672092.0328 | 1227035.1105
70 | 2672188.6754 | 1227028.3769
71 | 2672284.0581 | 1227112.8065
72 | 2672203.0647 | 1226892.0509
73 | 2672152.2756 | 1226961.2016
74 | 2672190.9842 | 1227001.0061
75 | 2672136.9194 | 1226960.0592
76 | 2672189.3568 | 1227018.3577
77 | 2672062.6033 | 1227001.0523
78 | 2672166.8315 | 1226962.2844

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1