## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4591-1_0_1_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4591-1_0_1_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4591-1_0_1_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4591-1_0_1_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_4591-1_0_1_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_4591-1_0_1_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_4591-1_0_1_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_4591-1_0_1_node_29 | 0.4 | n |  | TRUE
8 | bus_LV_4591-1_0_1_node_31 | 0.4 | n |  | TRUE
9 | bus_LV_4591-1_0_1_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_4591-1_0_1_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_4591-1_0_1_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_4591-1_0_1_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_4591-1_0_1_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_4591-1_0_1_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_4591-1_0_1_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_4591-1_0_1_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_4591-1_0_1_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_4591-1_0_1_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_4591-1_0_1_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_4591-1_0_1_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_4591-1_0_1_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_4591-1_0_1_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_4591-1_0_1_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_4591-1_0_1_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_4591-1_0_1_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_4591-1_0_1_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_4591-1_0_1_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_4591-1_0_1_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_4591-1_0_1_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_4591-1_0_1_node_287 | 0.4 | n |  | TRUE
31 | bus_LV_4591-1_0_1_node_43 | 0.4 | n |  | TRUE
32 | bus_LV_4591-1_0_1_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_4591-1_0_1_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_4591-1_0_1_node_46 | 0.4 | n |  | TRUE
35 | bus_LV_4591-1_0_1_node_47 | 0.4 | n |  | TRUE
36 | bus_LV_4591-1_0_1_node_48 | 0.4 | n |  | TRUE
37 | bus_LV_4591-1_0_1_node_49 | 0.4 | n |  | TRUE
38 | bus_LV_4591-1_0_1_node_50 | 0.4 | n |  | TRUE
39 | bus_LV_4591-1_0_1_node_51 | 0.4 | n |  | TRUE
40 | bus_LV_4591-1_0_1_node_85 | 0.4 | n |  | TRUE
41 | bus_LV_4591-1_0_1_node_77 | 0.4 | n |  | TRUE
42 | bus_LV_4591-1_0_1_node_75 | 0.4 | n |  | TRUE
43 | bus_LV_4591-1_0_1_node_63 | 0.4 | n |  | TRUE
44 | bus_LV_4591-1_0_1_node_61 | 0.4 | n |  | TRUE
45 | bus_LV_4591-1_0_1_node_53 | 0.4 | n |  | TRUE
46 | bus_LV_4591-1_0_1_node_54 | 0.4 | n |  | TRUE
47 | bus_LV_4591-1_0_1_node_55 | 0.4 | n |  | TRUE
48 | bus_LV_4591-1_0_1_node_56 | 0.4 | n |  | TRUE
49 | bus_LV_4591-1_0_1_node_58 | 0.4 | n |  | TRUE
50 | bus_LV_4591-1_0_1_node_70 | 0.4 | n |  | TRUE
51 | bus_LV_4591-1_0_1_node_59 | 0.4 | n |  | TRUE
52 | bus_LV_4591-1_0_1_node_83 | 0.4 | n |  | TRUE
53 | bus_LV_4591-1_0_1_node_78 | 0.4 | n |  | TRUE
54 | bus_LV_4591-1_0_1_node_62 | 0.4 | n |  | TRUE
55 | bus_LV_4591-1_0_1_node_65 | 0.4 | n |  | TRUE
56 | bus_LV_4591-1_0_1_node_66 | 0.4 | n |  | TRUE
57 | bus_LV_4591-1_0_1_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_4591-1_0_1_node_64 | 0.4 | n |  | TRUE
59 | bus_LV_4591-1_0_1_node_68 | 0.4 | n |  | TRUE
60 | bus_LV_4591-1_0_1_node_69 | 0.4 | n |  | TRUE
61 | bus_LV_4591-1_0_1_node_72 | 0.4 | n |  | TRUE
62 | bus_LV_4591-1_0_1_node_73 | 0.4 | n |  | TRUE
63 | bus_LV_4591-1_0_1_node_71 | 0.4 | n |  | TRUE
64 | bus_LV_4591-1_0_1_node_84 | 0.4 | n |  | TRUE
65 | bus_LV_4591-1_0_1_node_74 | 0.4 | n |  | TRUE
66 | bus_LV_4591-1_0_1_node_80 | 0.4 | n |  | TRUE
67 | bus_LV_4591-1_0_1_node_79 | 0.4 | n |  | TRUE
68 | bus_LV_4591-1_0_1_node_86 | 0.4 | n |  | TRUE
69 | bus_LV_4591-1_0_1_node_286 | 0.4 | n |  | TRUE
70 | bus_MV_0_node_33 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4591-1_0_1_load_0 | 0 | 0.00073875 | 0.00018515 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4591-1_0_1_load_1 | 1 | 0.00016801 | 4.2107e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4591-1_0_1_load_4 | 3 | 0.00037417 | 9.3777e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4591-1_0_1_load_5 | 4 | 0.0010926 | 0.00027382 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4591-1_0_1_load_8 | 5 | 0.0023366 | 0.0005856 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4591-1_0_1_load_9 | 6 | 0.00048343 | 0.00012116 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4591-1_0_1_load_29 | 7 | 0.0020135 | 0.00050463 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4591-1_0_1_load_31 | 8 | 0.0012856 | 0.0003222 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4591-1_0_1_load_10 | 9 | 0.0004738 | 0.00011874 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4591-1_0_1_load_11 | 10 | 0.00062788 | 0.00015736 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4591-1_0_1_load_13 | 12 | 0.0057574 | 0.0014429 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4591-1_0_1_load_17 | 15 | 0.0019113 | 0.00047902 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4591-1_0_1_load_22 | 16 | 0.0020212 | 0.00050655 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4591-1_0_1_load_18 | 18 | 0.00017644 | 4.422e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4591-1_0_1_load_19 | 19 | 0.002586 | 0.00064811 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4591-1_0_1_load_20 | 20 | 0.0015047 | 0.00037711 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4591-1_0_1_load_27 | 23 | 0.0011903 | 0.00029833 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4591-1_0_1_load_28 | 24 | 0.0030484 | 0.00076399 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4591-1_0_1_load_30 | 27 | 0.00066813 | 0.00016745 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4591-1_0_1_load_33 | 29 | 0.00057795 | 0.00014485 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4591-1_0_1_load_43 | 31 | 0.00053992 | 0.00013532 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4591-1_0_1_load_44 | 32 | 0.00046472 | 0.00011647 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4591-1_0_1_load_47 | 35 | 9.7608e-05 | 2.4463e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4591-1_0_1_load_48 | 36 | 0.00015516 | 3.8888e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4591-1_0_1_load_49 | 37 | 0.00015332 | 3.8426e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4591-1_0_1_load_85 | 40 | 0.00019017 | 4.7662e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4591-1_0_1_load_77 | 41 | 0.00016862 | 4.2261e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4591-1_0_1_load_75 | 42 | 0.00052115 | 0.00013061 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4591-1_0_1_load_61 | 44 | 0.00058883 | 0.00014757 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4591-1_0_1_load_53 | 45 | 0.00078252 | 0.00019612 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4591-1_0_1_load_54 | 46 | 0.00032168 | 8.0622e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4591-1_0_1_load_55 | 47 | 0.00055467 | 0.00013901 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4591-1_0_1_load_56 | 48 | 0.00037612 | 9.4264e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4591-1_0_1_load_58 | 49 | 0.00029932 | 7.5016e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4591-1_0_1_load_83 | 52 | 0.00052314 | 0.00013111 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4591-1_0_1_load_65 | 55 | 0.00039143 | 9.8101e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4591-1_0_1_load_66 | 56 | 0.00024113 | 6.0432e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4591-1_0_1_load_67 | 57 | 0.00040234 | 0.00010083 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4591-1_0_1_load_64 | 58 | 0.00013572 | 3.4014e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4591-1_0_1_load_68 | 59 | 0.00026698 | 6.691e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4591-1_0_1_load_69 | 60 | 0.00025155 | 6.3043e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4591-1_0_1_load_72 | 61 | 9.087e-05 | 2.2774e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4591-1_0_1_load_71 | 63 | 0.00046816 | 0.00011733 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4591-1_0_1_load_84 | 64 | 8.528e-05 | 2.1373e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4591-1_0_1_load_74 | 65 | 0.0017172 | 0.00043038 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4591-1_0_1_load_80 | 66 | 0.0010135 | 0.000254 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4591-1_0_1_load_79 | 67 | 0.00020218 | 5.067e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4591-1_0_1_load_86 | 68 | 0.0017534 | 0.00043944 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4591-1_0_1_load_286 | 69 | 0.00012163 | 3.0483e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4591-1_0_1_line_0 |  | 0 | 1 | 0.033997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4591-1_0_1_line_1 |  | 0 | 2 | 0.097267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4591-1_0_1_line_2 |  | 2 | 3 | 0.008183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4591-1_0_1_line_3 |  | 2 | 4 | 0.018291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4591-1_0_1_line_4 |  | 3 | 5 | 0.028334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4591-1_0_1_line_5 |  | 4 | 6 | 0.016689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4591-1_0_1_line_6 |  | 5 | 7 | 0.014673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4591-1_0_1_line_7 |  | 6 | 8 | 0.0033386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4591-1_0_1_line_8 |  | 7 | 28 | 0.031774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4591-1_0_1_line_9 |  | 8 | 27 | 0.02752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4591-1_0_1_line_10 |  | 9 | 10 | 0.031487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4591-1_0_1_line_11 |  | 10 | 11 | 0.007833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4591-1_0_1_line_12 |  | 11 | 12 | 0.029017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4591-1_0_1_line_13 |  | 12 | 13 | 0.006401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4591-1_0_1_line_14 |  | 13 | 17 | 0.018842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4591-1_0_1_line_15 |  | 13 | 15 | 0.041069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4591-1_0_1_line_16 |  | 14 | 15 | 0.0015561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4591-1_0_1_line_17 |  | 14 | 16 | 0.036508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4591-1_0_1_line_18 |  | 16 | 23 | 0.02184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4591-1_0_1_line_19 |  | 16 | 20 | 0.013014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4591-1_0_1_line_20 |  | 17 | 18 | 0.0087176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4591-1_0_1_line_21 |  | 19 | 20 | 0.019275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4591-1_0_1_line_22 |  | 19 | 21 | 0.013745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4591-1_0_1_line_23 |  | 21 | 22 | 0.058362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4591-1_0_1_line_24 |  | 22 | 24 | 0.05145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4591-1_0_1_line_25 |  | 24 | 28 | 0.031972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4591-1_0_1_line_26 |  | 25 | 26 | 0.12714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4591-1_0_1_line_27 |  | 25 | 27 | 0.031128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4591-1_0_1_line_28 |  | 26 | 29 | 0.12004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4591-1_0_1_line_29 |  | 26 | 30 | 0.78632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4591-1_0_1_line_30 |  | 30 | 55 | 0.11227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4591-1_0_1_line_31 |  | 30 | 69 | 0.064012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4591-1_0_1_line_32 |  | 31 | 32 | 0.041347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4591-1_0_1_line_33 |  | 31 | 33 | 0.016552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4591-1_0_1_line_34 |  | 32 | 34 | 0.037146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4591-1_0_1_line_35 |  | 33 | 35 | 0.0068802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4591-1_0_1_line_36 |  | 33 | 36 | 0.019969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4591-1_0_1_line_37 |  | 34 | 37 | 0.016171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4591-1_0_1_line_38 |  | 34 | 38 | 0.035617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4591-1_0_1_line_39 |  | 35 | 39 | 0.10195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4591-1_0_1_line_40 |  | 37 | 40 | 0.02855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4591-1_0_1_line_41 |  | 38 | 41 | 0.037004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4591-1_0_1_line_42 |  | 38 | 42 | 0.034548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4591-1_0_1_line_43 |  | 39 | 43 | 0.15699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4591-1_0_1_line_44 |  | 39 | 44 | 0.050559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4591-1_0_1_line_45 |  | 40 | 68 | 0.02157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4591-1_0_1_line_46 |  | 41 | 66 | 0.044196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4591-1_0_1_line_47 |  | 42 | 65 | 0.057079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4591-1_0_1_line_48 |  | 43 | 56 | 0.04455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4591-1_0_1_line_49 |  | 43 | 57 | 0.071718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4591-1_0_1_line_50 |  | 44 | 54 | 0.030761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4591-1_0_1_line_51 |  | 45 | 46 | 0.012372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4591-1_0_1_line_52 |  | 45 | 47 | 0.015313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4591-1_0_1_line_53 |  | 46 | 48 | 0.015782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4591-1_0_1_line_54 |  | 48 | 49 | 0.0035994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4591-1_0_1_line_55 |  | 49 | 50 | 0.014603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4591-1_0_1_line_56 |  | 50 | 63 | 0.021709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4591-1_0_1_line_57 |  | 50 | 57 | 0.026014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4591-1_0_1_line_58 |  | 51 | 52 | 0.020122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4591-1_0_1_line_59 |  | 51 | 53 | 0.002448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4591-1_0_1_line_60 |  | 53 | 67 | 0.045919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4591-1_0_1_line_61 |  | 53 | 62 | 0.025272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4591-1_0_1_line_62 |  | 54 | 55 | 0.039877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4591-1_0_1_line_63 |  | 55 | 60 | 0.038557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4591-1_0_1_line_64 |  | 56 | 61 | 0.0060073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4591-1_0_1_line_65 |  | 58 | 59 | 0.051321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4591-1_0_1_line_66 |  | 59 | 62 | 0.029862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4591-1_0_1_line_67 |  | 61 | 64 | 0.0020906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4591-1_0_1_line_68 |  | 62 | 63 | 0.05635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4591-1_0_1_trafo_33 | 0.63 MVA 20/0.4 kV | 70 | 29 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2712649.836 | 1266933.1593 | 2712629.6086 | 1266913.9893 | 2712625.2235 | 1266909.7077
1 | 2712724.6557 | 1266993.4932 | 2712718.5432 | 1266991.8196 | 2712710.4366 | 1266988.1062 | 2712700.2548 | 1266981.4729 | 2712691.6289 | 1266974.1909 | 2712662.3371 | 1266945.0069 | 2712649.836 | 1266933.1593
2 | 2712724.6557 | 1266993.4932 | 2712724.1981 | 1267001.6634
3 | 2712724.6557 | 1266993.4932 | 2712726.1584 | 1266985.3814 | 2712728.4683 | 1266977.5853 | 2712729.3804 | 1266975.9068
4 | 2712723.8471 | 1267029.9903 | 2712723.9589 | 1267005.9353 | 2712724.1981 | 1267001.6634
5 | 2712742.7797 | 1266968.6415 | 2712738.5531 | 1266968.7921 | 2712734.8961 | 1266969.4452 | 2712731.746 | 1266971.5536 | 2712729.3804 | 1266975.9068
6 | 2712724.1563 | 1267044.6526 | 2712723.8062 | 1267038.7834 | 2712723.8471 | 1267029.9903
7 | 2712742.7797 | 1266968.6415 | 2712746.1161 | 1266968.5226
8 | 2712726.0479 | 1267076.3702 | 2712724.1563 | 1267044.6526
9 | 2712746.1161 | 1266968.5226 | 2712770.4565 | 1266967.6553 | 2712773.6161 | 1266967.8296
10 | 2712478.442 | 1267127.1015 | 2712466.9924 | 1267120.685 | 2712451.5087 | 1267110.8156
11 | 2712485.2752 | 1267130.9308 | 2712478.442 | 1267127.1015
12 | 2712485.2752 | 1267130.9308 | 2712493.0302 | 1267134.5149 | 2712510.1223 | 1267140.8569 | 2712512.2484 | 1267141.5728
13 | 2712518.3148 | 1267143.6153 | 2712512.2484 | 1267141.5728
14 | 2712518.3148 | 1267143.6153 | 2712515.6546 | 1267138.5936 | 2712507.3881 | 1267132.6088 | 2712504.8115 | 1267131.1028
15 | 2712518.3148 | 1267143.6153 | 2712530.3681 | 1267147.6594 | 2712557.4235 | 1267156.1451
16 | 2712558.9082 | 1267156.6107 | 2712557.4235 | 1267156.1451
17 | 2712558.9082 | 1267156.6107 | 2712593.8885 | 1267167.4087
18 | 2712593.8885 | 1267167.4087 | 2712583.6335 | 1267186.6908
19 | 2712593.8885 | 1267167.4087 | 2712606.2619 | 1267171.4429
20 | 2712504.8115 | 1267131.1028 | 2712507.7433 | 1267122.893
21 | 2712624.37 | 1267178.0196 | 2712621.1361 | 1267176.6137 | 2712610.5535 | 1267172.8421 | 2712606.2619 | 1267171.4429
22 | 2712636.9752 | 1267183.4994 | 2712624.37 | 1267178.0196
23 | 2712676.2515 | 1267140.3991 | 2712669.3869 | 1267150.1323 | 2712653.7374 | 1267166.8598 | 2712636.9752 | 1267183.4994
24 | 2712676.2515 | 1267140.3991 | 2712686.3167 | 1267123.1425 | 2712691.702 | 1267106.8865 | 2712700.6123 | 1267095.6406
25 | 2712726.0479 | 1267076.3702 | 2712712.6183 | 1267086.4452 | 2712701.7014 | 1267094.2661 | 2712700.6123 | 1267095.6406
26 | 2712804.6967 | 1266969.5437 | 2712805.3261 | 1266960.2476 | 2712806.2241 | 1266951.0789 | 2712807.8692 | 1266937.098 | 2712809.3641 | 1266926.6396 | 2712810.4319 | 1266922.3785 | 2712812.0181 | 1266918.1828 | 2712815.7334 | 1266910.5359 | 2712829.4022 | 1266894.2826 | 2712833.4038 | 1266889.388 | 2712838.2547 | 1266882.608 | 2712847.2383 | 1266868.8007 | 2712852.7351 | 1266862.9005 | 2712857.3629 | 1266858.7297
27 | 2712804.6967 | 1266969.5437 | 2712773.6161 | 1266967.8296
28 | 2712857.3629 | 1266858.7297 | 2712853.2971 | 1266853.9812 | 2712849.6156 | 1266851.1862 | 2712846.7894 | 1266849.3418 | 2712844.3306 | 1266848.761 | 2712840.8578 | 1266849.2284 | 2712838.1679 | 1266850.5004 | 2712835.1979 | 1266852.6345 | 2712831.7281 | 1266856.4938 | 2712827.8868 | 1266862.0587 | 2712825.0541 | 1266867.654 | 2712822.4462 | 1266871.3297 | 2712819.2591 | 1266874.5828 | 2712814.7204 | 1266878.4218 | 2712808.3728 | 1266882.7488 | 2712802.1018 | 1266886.6103 | 2712798.8144 | 1266888.0155 | 2712794.6745 | 1266888.3256 | 2712762.8225 | 1266888.7182 | 2712762.7849 | 1266894.2335
29 | 2712710.3655 | 1266086.2708 | 2712857.3629 | 1266858.7297
30 | 2712712.8657 | 1265974.0293 | 2712710.3655 | 1266086.2708
31 | 2712710.3655 | 1266086.2708 | 2712646.475 | 1266082.3265
32 | 2712681.7459 | 1265865.8021 | 2712663.7017 | 1265847.4727 | 2712653.4167 | 1265837.0565 | 2712653.077 | 1265836.1284
33 | 2712693.3578 | 1265877.5976 | 2712681.7459 | 1265865.8021
34 | 2712658.0318 | 1265801.2131 | 2712649.2147 | 1265825.5775 | 2712653.077 | 1265836.1284
35 | 2712693.3578 | 1265877.5976 | 2712695.2048 | 1265879.4789 | 2712697.4123 | 1265883.1033
36 | 2712693.3578 | 1265877.5976 | 2712701.0019 | 1265872.0829 | 2712706.8364 | 1265863.3006
37 | 2712658.0318 | 1265801.2131 | 2712645.0252 | 1265798.0403 | 2712642.2622 | 1265797.7113
38 | 2712658.0318 | 1265801.2131 | 2712667.0261 | 1265778.6093 | 2712673.6256 | 1265769.427
39 | 2712765.0372 | 1265951.5624 | 2712750.7461 | 1265945.0842 | 2712730.0607 | 1265934.6694 | 2712715.4472 | 1265923.7702 | 2712707.8772 | 1265910.8034 | 2712702.4416 | 1265891.3606 | 2712697.4123 | 1265883.1033
40 | 2712616.1652 | 1265806.6883 | 2712620.1218 | 1265803.415 | 2712636.241 | 1265796.9942 | 2712642.2622 | 1265797.7113
41 | 2712673.6256 | 1265769.427 | 2712637.5142 | 1265761.3468
42 | 2712673.6256 | 1265769.427 | 2712670.6855 | 1265760.4965 | 2712664.2651 | 1265749.231 | 2712655.7025 | 1265740.5697
43 | 2712920.3513 | 1265927.2726 | 2712864.737 | 1265934.9394 | 2712779.311 | 1265946.7194 | 2712765.0372 | 1265951.5624
44 | 2712765.0372 | 1265951.5624 | 2712757.8294 | 1265957.8971 | 2712730.96 | 1265959.7641 | 2712717.4189 | 1265956.0955
45 | 2712599.5453 | 1265820.4379 | 2712616.1652 | 1265806.6883
46 | 2712637.5142 | 1265761.3468 | 2712598.106 | 1265752.529 | 2712594.2925 | 1265752.5359
47 | 2712613.6116 | 1265702.0984 | 2712638.4703 | 1265723.1389 | 2712655.7025 | 1265740.5697
48 | 2712920.3513 | 1265927.2726 | 2712920.5095 | 1265932.3912 | 2712914.1245 | 1265935.0715 | 2712905.9919 | 1265937.3738 | 2712901.6621 | 1265943.2518 | 2712900.8539 | 1265948.4965 | 2712902.1344 | 1265955.1823 | 2712906.7328 | 1265955.7805
49 | 2712920.3513 | 1265927.2726 | 2712957.0425 | 1265922.2136 | 2712972.6114 | 1265922.9117 | 2712990.7025 | 1265929.0228
50 | 2712687.7283 | 1265948.0518 | 2712717.4189 | 1265956.0955
51 | 2713056.5482 | 1265932.4817 | 2713044.5204 | 1265935.3794
52 | 2713056.5482 | 1265932.4817 | 2713071.4353 | 1265928.8952
53 | 2713044.5204 | 1265935.3794 | 2713029.1771 | 1265939.0759
54 | 2713025.6778 | 1265939.9189 | 2713029.1771 | 1265939.0759
55 | 2713011.4811 | 1265943.3391 | 2713025.6778 | 1265939.9189
56 | 2713011.4811 | 1265943.3391 | 2713009.5441 | 1265964.962
57 | 2713011.4811 | 1265943.3391 | 2713006.2643 | 1265936.1331 | 2712992.1194 | 1265929.5014 | 2712990.7025 | 1265929.0228
58 | 2713049.8674 | 1266017.3378 | 2713069.4532 | 1266021.951
59 | 2713048.9578 | 1266019.6113 | 2713049.8674 | 1266017.3378
60 | 2713048.9578 | 1266019.6113 | 2713047.9707 | 1266034.5944 | 2713053.0371 | 1266053.5857 | 2713058.4204 | 1266063.4614
61 | 2713048.9578 | 1266019.6113 | 2713024.1269 | 1266014.5321
62 | 2712687.7283 | 1265948.0518 | 2712690.7048 | 1265959.8077 | 2712695.622 | 1265967.3414 | 2712699.5641 | 1265970.3302 | 2712712.8657 | 1265974.0293
63 | 2712750.5931 | 1265977.9544 | 2712739.1068 | 1265979.5923 | 2712731.3802 | 1265979.1779 | 2712712.8657 | 1265974.0293
64 | 2712912.6899 | 1265956.5553 | 2712906.7328 | 1265955.7805
65 | 2712946.6632 | 1265992.8753 | 2712962.6544 | 1265996.975 | 2712982.9406 | 1266006.5711 | 2712990.9498 | 1266009.9271 | 2712994.5337 | 1266010.7942
66 | 2713024.1269 | 1266014.5321 | 2712998.986 | 1266011.8713 | 2712994.5337 | 1266010.7942
67 | 2712914.763 | 1265956.825 | 2712912.6899 | 1265956.5553
68 | 2713024.1269 | 1266014.5321 | 2713016.2099 | 1266008.7201 | 2713010.3582 | 1266002.0246 | 2713008.0629 | 1265996.031 | 2713007.2961 | 1265990.0556 | 2713009.5441 | 1265964.962

## bus_geodata
| x | y | coords
0 | 2712649.836 | 1266933.1593
1 | 2712625.2235 | 1266909.7077
2 | 2712724.6557 | 1266993.4932
3 | 2712724.1981 | 1267001.6634
4 | 2712729.3804 | 1266975.9068
5 | 2712723.8471 | 1267029.9903
6 | 2712742.7797 | 1266968.6415
7 | 2712724.1563 | 1267044.6526
8 | 2712746.1161 | 1266968.5226
9 | 2712451.5087 | 1267110.8156
10 | 2712478.442 | 1267127.1015
11 | 2712485.2751 | 1267130.9308
12 | 2712512.2484 | 1267141.5728
13 | 2712518.3148 | 1267143.6153
14 | 2712558.9082 | 1267156.6107
15 | 2712557.4235 | 1267156.1451
16 | 2712593.8885 | 1267167.4087
17 | 2712504.8115 | 1267131.1028
18 | 2712507.7433 | 1267122.893
19 | 2712624.37 | 1267178.0196
20 | 2712606.2619 | 1267171.4429
21 | 2712636.9752 | 1267183.4994
22 | 2712676.2515 | 1267140.3991
23 | 2712583.6335 | 1267186.6908
24 | 2712700.6123 | 1267095.6406
25 | 2712804.6967 | 1266969.5437
26 | 2712857.3629 | 1266858.7297
27 | 2712773.6161 | 1266967.8296
28 | 2712726.0479 | 1267076.3702
29 | 2712762.7849 | 1266894.2335
30 | 2712710.3655 | 1266086.2708
31 | 2712681.7459 | 1265865.8021
32 | 2712653.077 | 1265836.1284
33 | 2712693.3578 | 1265877.5976
34 | 2712658.0318 | 1265801.2131
35 | 2712697.4123 | 1265883.1033
36 | 2712706.8364 | 1265863.3006
37 | 2712642.2622 | 1265797.7113
38 | 2712673.6256 | 1265769.427
39 | 2712765.0372 | 1265951.5624
40 | 2712616.1652 | 1265806.6883
41 | 2712637.5142 | 1265761.3468
42 | 2712655.7025 | 1265740.5697
43 | 2712920.3513 | 1265927.2726
44 | 2712717.4189 | 1265956.0955
45 | 2713056.5482 | 1265932.4817
46 | 2713044.5204 | 1265935.3794
47 | 2713071.4353 | 1265928.8952
48 | 2713029.1771 | 1265939.0759
49 | 2713025.6778 | 1265939.9189
50 | 2713011.4811 | 1265943.3391
51 | 2713049.8674 | 1266017.3378
52 | 2713069.4532 | 1266021.951
53 | 2713048.9578 | 1266019.6113
54 | 2712687.7283 | 1265948.0518
55 | 2712712.8657 | 1265974.0293
56 | 2712906.7328 | 1265955.7805
57 | 2712990.7025 | 1265929.0228
58 | 2712946.6632 | 1265992.8753
59 | 2712994.5337 | 1266010.7942
60 | 2712750.5931 | 1265977.9544
61 | 2712912.6899 | 1265956.5553
62 | 2713024.1269 | 1266014.5321
63 | 2713009.5441 | 1265964.962
64 | 2712914.763 | 1265956.825
65 | 2712613.6116 | 1265702.0984
66 | 2712594.2925 | 1265752.5359
67 | 2713058.4204 | 1266063.4614
68 | 2712599.5453 | 1265820.4379
69 | 2712646.475 | 1266082.3265
70 | 2712762.7849 | 1266894.2335

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1