## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_538-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_538-7_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_538-7_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_538-7_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_538-7_0_3_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_538-7_0_3_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_538-7_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_538-7_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_538-7_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_538-7_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_538-7_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_538-7_0_3_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_538-7_0_3_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_538-7_0_3_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_538-7_0_3_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_538-7_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_538-7_0_3_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_538-7_0_3_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_538-7_0_3_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_538-7_0_3_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_538-7_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_538-7_0_3_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_538-7_0_3_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_538-7_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_538-7_0_3_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_538-7_0_3_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_538-7_0_3_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_538-7_0_3_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_538-7_0_3_node_38 | 0.4 | n |  | TRUE
29 | bus_LV_538-7_0_3_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_538-7_0_3_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_538-7_0_3_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_538-7_0_3_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_538-7_0_3_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_538-7_0_3_node_119 | 0.4 | n |  | TRUE
35 | bus_LV_538-7_0_3_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_538-7_0_3_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_538-7_0_3_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_538-7_0_3_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_538-7_0_3_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_538-7_0_3_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_538-7_0_3_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_538-7_0_3_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_538-7_0_3_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_538-7_0_3_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_538-7_0_3_node_47 | 0.4 | n |  | TRUE
46 | bus_LV_538-7_0_3_node_158 | 0.4 | n |  | TRUE
47 | bus_LV_538-7_0_3_node_160 | 0.4 | n |  | TRUE
48 | bus_LV_538-7_0_3_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_538-7_0_3_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_538-7_0_3_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_538-7_0_3_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_538-7_0_3_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_538-7_0_3_node_50 | 0.4 | n |  | TRUE
54 | bus_LV_538-7_0_3_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_538-7_0_3_node_56 | 0.4 | n |  | TRUE
56 | bus_LV_538-7_0_3_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_538-7_0_3_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_538-7_0_3_node_147 | 0.4 | n |  | TRUE
59 | bus_LV_538-7_0_3_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_538-7_0_3_node_55 | 0.4 | n |  | TRUE
61 | bus_LV_538-7_0_3_node_57 | 0.4 | n |  | TRUE
62 | bus_LV_538-7_0_3_node_74 | 0.4 | n |  | TRUE
63 | bus_LV_538-7_0_3_node_70 | 0.4 | n |  | TRUE
64 | bus_LV_538-7_0_3_node_58 | 0.4 | n |  | TRUE
65 | bus_LV_538-7_0_3_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_538-7_0_3_node_162 | 0.4 | n |  | TRUE
67 | bus_LV_538-7_0_3_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_538-7_0_3_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_538-7_0_3_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_538-7_0_3_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_538-7_0_3_node_64 | 0.4 | n |  | TRUE
72 | bus_LV_538-7_0_3_node_65 | 0.4 | n |  | TRUE
73 | bus_LV_538-7_0_3_node_134 | 0.4 | n |  | TRUE
74 | bus_LV_538-7_0_3_node_71 | 0.4 | n |  | TRUE
75 | bus_LV_538-7_0_3_node_68 | 0.4 | n |  | TRUE
76 | bus_LV_538-7_0_3_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_538-7_0_3_node_67 | 0.4 | n |  | TRUE
78 | bus_LV_538-7_0_3_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_538-7_0_3_node_75 | 0.4 | n |  | TRUE
80 | bus_LV_538-7_0_3_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_538-7_0_3_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_538-7_0_3_node_127 | 0.4 | n |  | TRUE
83 | bus_LV_538-7_0_3_node_132 | 0.4 | n |  | TRUE
84 | bus_LV_538-7_0_3_node_129 | 0.4 | n |  | TRUE
85 | bus_LV_538-7_0_3_node_403 | 0.4 | n |  | TRUE
86 | bus_LV_538-7_0_3_node_76 | 0.4 | n |  | TRUE
87 | bus_LV_538-7_0_3_node_80 | 0.4 | n |  | TRUE
88 | bus_LV_538-7_0_3_node_77 | 0.4 | n |  | TRUE
89 | bus_LV_538-7_0_3_node_78 | 0.4 | n |  | TRUE
90 | bus_LV_538-7_0_3_node_79 | 0.4 | n |  | TRUE
91 | bus_LV_538-7_0_3_node_81 | 0.4 | n |  | TRUE
92 | bus_LV_538-7_0_3_node_85 | 0.4 | n |  | TRUE
93 | bus_LV_538-7_0_3_node_82 | 0.4 | n |  | TRUE
94 | bus_LV_538-7_0_3_node_83 | 0.4 | n |  | TRUE
95 | bus_LV_538-7_0_3_node_84 | 0.4 | n |  | TRUE
96 | bus_LV_538-7_0_3_node_86 | 0.4 | n |  | TRUE
97 | bus_LV_538-7_0_3_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_538-7_0_3_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_538-7_0_3_node_89 | 0.4 | n |  | TRUE
100 | bus_LV_538-7_0_3_node_90 | 0.4 | n |  | TRUE
101 | bus_LV_538-7_0_3_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_538-7_0_3_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_538-7_0_3_node_102 | 0.4 | n |  | TRUE
104 | bus_LV_538-7_0_3_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_538-7_0_3_node_94 | 0.4 | n |  | TRUE
106 | bus_LV_538-7_0_3_node_95 | 0.4 | n |  | TRUE
107 | bus_LV_538-7_0_3_node_99 | 0.4 | n |  | TRUE
108 | bus_LV_538-7_0_3_node_96 | 0.4 | n |  | TRUE
109 | bus_LV_538-7_0_3_node_150 | 0.4 | n |  | TRUE
110 | bus_LV_538-7_0_3_node_97 | 0.4 | n |  | TRUE
111 | bus_LV_538-7_0_3_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_538-7_0_3_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_538-7_0_3_node_101 | 0.4 | n |  | TRUE
114 | bus_LV_538-7_0_3_node_103 | 0.4 | n |  | TRUE
115 | bus_LV_538-7_0_3_node_404 | 0.4 | n |  | TRUE
116 | bus_LV_538-7_0_3_node_405 | 0.4 | n |  | TRUE
117 | bus_LV_538-7_0_3_node_106 | 0.4 | n |  | TRUE
118 | bus_LV_538-7_0_3_node_109 | 0.4 | n |  | TRUE
119 | bus_LV_538-7_0_3_node_104 | 0.4 | n |  | TRUE
120 | bus_LV_538-7_0_3_node_105 | 0.4 | n |  | TRUE
121 | bus_LV_538-7_0_3_node_107 | 0.4 | n |  | TRUE
122 | bus_LV_538-7_0_3_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_538-7_0_3_node_110 | 0.4 | n |  | TRUE
124 | bus_LV_538-7_0_3_node_111 | 0.4 | n |  | TRUE
125 | bus_LV_538-7_0_3_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_538-7_0_3_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_538-7_0_3_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_538-7_0_3_node_116 | 0.4 | n |  | TRUE
129 | bus_LV_538-7_0_3_node_117 | 0.4 | n |  | TRUE
130 | bus_LV_538-7_0_3_node_120 | 0.4 | n |  | TRUE
131 | bus_LV_538-7_0_3_node_121 | 0.4 | n |  | TRUE
132 | bus_LV_538-7_0_3_node_123 | 0.4 | n |  | TRUE
133 | bus_LV_538-7_0_3_node_122 | 0.4 | n |  | TRUE
134 | bus_LV_538-7_0_3_node_124 | 0.4 | n |  | TRUE
135 | bus_LV_538-7_0_3_node_125 | 0.4 | n |  | TRUE
136 | bus_LV_538-7_0_3_node_126 | 0.4 | n |  | TRUE
137 | bus_LV_538-7_0_3_node_146 | 0.4 | n |  | TRUE
138 | bus_LV_538-7_0_3_node_128 | 0.4 | n |  | TRUE
139 | bus_LV_538-7_0_3_node_130 | 0.4 | n |  | TRUE
140 | bus_LV_538-7_0_3_node_131 | 0.4 | n |  | TRUE
141 | bus_LV_538-7_0_3_node_133 | 0.4 | n |  | TRUE
142 | bus_LV_538-7_0_3_node_143 | 0.4 | n |  | TRUE
143 | bus_LV_538-7_0_3_node_135 | 0.4 | n |  | TRUE
144 | bus_LV_538-7_0_3_node_136 | 0.4 | n |  | TRUE
145 | bus_LV_538-7_0_3_node_137 | 0.4 | n |  | TRUE
146 | bus_LV_538-7_0_3_node_138 | 0.4 | n |  | TRUE
147 | bus_LV_538-7_0_3_node_139 | 0.4 | n |  | TRUE
148 | bus_LV_538-7_0_3_node_140 | 0.4 | n |  | TRUE
149 | bus_LV_538-7_0_3_node_141 | 0.4 | n |  | TRUE
150 | bus_LV_538-7_0_3_node_142 | 0.4 | n |  | TRUE
151 | bus_LV_538-7_0_3_node_144 | 0.4 | n |  | TRUE
152 | bus_LV_538-7_0_3_node_145 | 0.4 | n |  | TRUE
153 | bus_LV_538-7_0_3_node_148 | 0.4 | n |  | TRUE
154 | bus_LV_538-7_0_3_node_149 | 0.4 | n |  | TRUE
155 | bus_LV_538-7_0_3_node_151 | 0.4 | n |  | TRUE
156 | bus_LV_538-7_0_3_node_152 | 0.4 | n |  | TRUE
157 | bus_LV_538-7_0_3_node_153 | 0.4 | n |  | TRUE
158 | bus_LV_538-7_0_3_node_154 | 0.4 | n |  | TRUE
159 | bus_LV_538-7_0_3_node_155 | 0.4 | n |  | TRUE
160 | bus_LV_538-7_0_3_node_156 | 0.4 | n |  | TRUE
161 | bus_LV_538-7_0_3_node_157 | 0.4 | n |  | TRUE
162 | bus_LV_538-7_0_3_node_161 | 0.4 | n |  | TRUE
163 | bus_LV_538-7_0_3_node_163 | 0.4 | n |  | TRUE
164 | bus_LV_538-7_0_3_node_164 | 0.4 | n |  | TRUE
165 | bus_LV_538-7_0_3_node_165 | 0.4 | n |  | TRUE
166 | bus_LV_538-7_0_3_node_166 | 0.4 | n |  | TRUE
167 | bus_MV_387_0_node_178 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_538-7_0_3_load_0 | 0 | 0.0029851 | 0.00074813 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_538-7_0_3_load_3 | 3 | 0.0024099 | 0.00060398 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_538-7_0_3_load_10 | 4 | 0.0008499 | 0.00021301 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_538-7_0_3_load_8 | 5 | 0.0013054 | 0.00032715 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_538-7_0_3_load_4 | 6 | 0.0016431 | 0.00041181 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_538-7_0_3_load_5 | 7 | 0.0014061 | 0.00035239 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_538-7_0_3_load_6 | 8 | 0.00050326 | 0.00012613 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_538-7_0_3_load_7 | 9 | 0.0006024 | 0.00015098 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_538-7_0_3_load_9 | 10 | 0.0011151 | 0.00027946 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_538-7_0_3_load_13 | 11 | 0.0010548 | 0.00026435 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_538-7_0_3_load_11 | 12 | 0.00075374 | 0.00018891 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_538-7_0_3_load_30 | 14 | 0.0009214 | 0.00023092 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_538-7_0_3_load_15 | 16 | 0.002555 | 0.00064033 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_538-7_0_3_load_16 | 17 | 0.0033328 | 0.00083527 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_538-7_0_3_load_17 | 18 | 0.0048255 | 0.0012094 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_538-7_0_3_load_18 | 19 | 0.00026085 | 6.5374e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_538-7_0_3_load_19 | 20 | 0.00040698 | 0.000102 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_538-7_0_3_load_20 | 21 | 0.002204 | 0.00055237 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_538-7_0_3_load_21 | 22 | 0.0010938 | 0.00027412 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_538-7_0_3_load_22 | 23 | 0.00082552 | 0.0002069 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_538-7_0_3_load_26 | 24 | 0.00078269 | 0.00019616 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_538-7_0_3_load_23 | 25 | 0.00024075 | 6.0337e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_538-7_0_3_load_24 | 26 | 0.00021758 | 5.453e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_538-7_0_3_load_25 | 27 | 0.00020543 | 5.1486e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_538-7_0_3_load_38 | 28 | 0.0014103 | 0.00035346 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_538-7_0_3_load_29 | 31 | 0.00069639 | 0.00017453 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_538-7_0_3_load_39 | 32 | 0.00041846 | 0.00010488 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_538-7_0_3_load_31 | 33 | 0.00034318 | 8.6009e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_538-7_0_3_load_119 | 34 | 0.00090024 | 0.00022562 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_538-7_0_3_load_32 | 35 | 0.0025094 | 0.0006289 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_538-7_0_3_load_33 | 36 | 0.0007432 | 0.00018626 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_538-7_0_3_load_37 | 40 | 0.00039323 | 9.8552e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_538-7_0_3_load_41 | 41 | 0.0040326 | 0.0010107 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_538-7_0_3_load_42 | 42 | 0.0004045 | 0.00010138 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_538-7_0_3_load_40 | 43 | 0.00098303 | 0.00024637 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_538-7_0_3_load_158 | 46 | 0.00084459 | 0.00021168 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_538-7_0_3_load_160 | 47 | 0.0011568 | 0.00028991 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_538-7_0_3_load_45 | 49 | 0.00010416 | 2.6105e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_538-7_0_3_load_49 | 50 | 0.0014584 | 0.00036551 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_538-7_0_3_load_46 | 51 | 0.00024408 | 6.1172e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_538-7_0_3_load_48 | 52 | 0.00051095 | 0.00012806 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_538-7_0_3_load_56 | 55 | 0.0021349 | 0.00053506 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_538-7_0_3_load_53 | 56 | 0.00069084 | 0.00017314 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_538-7_0_3_load_52 | 57 | 0.0012506 | 0.00031343 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_538-7_0_3_load_147 | 58 | 0.0055127 | 0.0013816 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_538-7_0_3_load_54 | 59 | 0.00046894 | 0.00011753 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_538-7_0_3_load_55 | 60 | 0.00017082 | 4.281e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_538-7_0_3_load_57 | 61 | 0.00098234 | 0.0002462 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_538-7_0_3_load_70 | 63 | 0.0045588 | 0.0011425 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_538-7_0_3_load_58 | 64 | 0.0013082 | 0.00032786 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_538-7_0_3_load_59 | 65 | 0.00023677 | 5.9339e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_538-7_0_3_load_162 | 66 | 0.00060931 | 0.00015271 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_538-7_0_3_load_60 | 67 | 0.0049431 | 0.0012389 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_538-7_0_3_load_61 | 68 | 0.00051133 | 0.00012815 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_538-7_0_3_load_63 | 70 | 0.0017199 | 0.00043105 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_538-7_0_3_load_64 | 71 | 0.0051743 | 0.0012968 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_538-7_0_3_load_65 | 72 | 0.00192 | 0.0004812 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_538-7_0_3_load_134 | 73 | 0.00099202 | 0.00024862 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_538-7_0_3_load_66 | 76 | 0.0034143 | 0.0008557 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_538-7_0_3_load_67 | 77 | 0.00049281 | 0.00012351 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_538-7_0_3_load_69 | 78 | 0.00086628 | 0.00021711 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_538-7_0_3_load_132 | 83 | 0.00051299 | 0.00012857 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_538-7_0_3_load_129 | 84 | 0.00071631 | 0.00017952 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_538-7_0_3_load_403 | 85 | 0.0061381 | 0.0015384 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_538-7_0_3_load_80 | 87 | 0.0011138 | 0.00027915 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_538-7_0_3_load_77 | 88 | 0.00089066 | 0.00022322 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_538-7_0_3_load_78 | 89 | 0.00066069 | 0.00016558 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_538-7_0_3_load_79 | 90 | 0.003746 | 0.00093883 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_538-7_0_3_load_81 | 91 | 0.00029604 | 7.4194e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_538-7_0_3_load_85 | 92 | 0.00027189 | 6.8143e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_538-7_0_3_load_82 | 93 | 0.0018258 | 0.00045759 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_538-7_0_3_load_83 | 94 | 0.0028538 | 0.00071523 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_538-7_0_3_load_84 | 95 | 0.00068048 | 0.00017054 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_538-7_0_3_load_86 | 96 | 0.00022992 | 5.7624e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_538-7_0_3_load_87 | 97 | 0.00083861 | 0.00021018 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_538-7_0_3_load_88 | 98 | 0.00083925 | 0.00021034 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_538-7_0_3_load_90 | 100 | 0.00096825 | 0.00024267 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_538-7_0_3_load_91 | 101 | 0.00062976 | 0.00015783 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_538-7_0_3_load_102 | 103 | 0.00082452 | 0.00020664 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_538-7_0_3_load_93 | 104 | 0.00054854 | 0.00013748 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_538-7_0_3_load_94 | 105 | 0.00094451 | 0.00023672 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_538-7_0_3_load_95 | 106 | 0.00029442 | 7.3788e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_538-7_0_3_load_96 | 108 | 0.0020994 | 0.00052615 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_538-7_0_3_load_150 | 109 | 0.00045716 | 0.00011457 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_538-7_0_3_load_97 | 110 | 0.0010133 | 0.00025397 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_538-7_0_3_load_98 | 111 | 0.0020971 | 0.00052559 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_538-7_0_3_load_404 | 115 | 0.002741 | 0.00068695 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_538-7_0_3_load_405 | 116 | 0.0011462 | 0.00028727 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_538-7_0_3_load_109 | 118 | 0.00098374 | 0.00024655 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_538-7_0_3_load_104 | 119 | 0.0011098 | 0.00027814 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_538-7_0_3_load_105 | 120 | 0.00020145 | 5.0488e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_538-7_0_3_load_107 | 121 | 0.0014455 | 0.00036226 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_538-7_0_3_load_113 | 122 | 0.00056199 | 0.00014085 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_538-7_0_3_load_110 | 123 | 0.00020232 | 5.0705e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_538-7_0_3_load_111 | 124 | 0.0003673 | 9.2055e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_538-7_0_3_load_112 | 125 | 0.00013647 | 3.4203e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_538-7_0_3_load_114 | 126 | 0.001958 | 0.00049072 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_538-7_0_3_load_116 | 128 | 0.0031172 | 0.00078124 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_538-7_0_3_load_117 | 129 | 0.00051304 | 0.00012858 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_538-7_0_3_load_120 | 130 | 0.001045 | 0.0002619 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_538-7_0_3_load_121 | 131 | 0.0014459 | 0.00036238 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_538-7_0_3_load_122 | 133 | 0.00082657 | 0.00020716 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_538-7_0_3_load_125 | 135 | 0.00069948 | 0.00017531 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_538-7_0_3_load_126 | 136 | 0.0029945 | 0.0007505 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_538-7_0_3_load_128 | 138 | 0.0041551 | 0.0010414 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_538-7_0_3_load_130 | 139 | 0.0034247 | 0.00085832 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_538-7_0_3_load_131 | 140 | 0.00060819 | 0.00015243 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_538-7_0_3_load_143 | 142 | 0.00025146 | 6.3022e-05 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_538-7_0_3_load_135 | 143 | 0.0037734 | 0.00094569 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_538-7_0_3_load_137 | 145 | 0.0011252 | 0.00028199 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_538-7_0_3_load_138 | 146 | 0.0021382 | 0.00053589 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_538-7_0_3_load_140 | 148 | 0.00091044 | 0.00022818 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_538-7_0_3_load_141 | 149 | 0.0023358 | 0.00058542 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_538-7_0_3_load_142 | 150 | 0.0064831 | 0.0016248 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_538-7_0_3_load_144 | 151 | 0.00056127 | 0.00014067 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_538-7_0_3_load_148 | 153 | 0.003625 | 0.00090852 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_538-7_0_3_load_152 | 156 | 0.00030926 | 7.7509e-05 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_538-7_0_3_load_153 | 157 | 0.000911 | 0.00022832 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_538-7_0_3_load_154 | 158 | 0.00041544 | 0.00010412 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_538-7_0_3_load_155 | 159 | 0.00068823 | 0.00017249 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_538-7_0_3_load_156 | 160 | 0.0024213 | 0.00060682 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_538-7_0_3_load_157 | 161 | 0.00044095 | 0.00011051 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_538-7_0_3_load_161 | 162 | 0.00080944 | 0.00020286 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_538-7_0_3_load_163 | 163 | 0.0016326 | 0.00040916 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_538-7_0_3_load_164 | 164 | 0.00036035 | 9.0312e-05 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_538-7_0_3_load_166 | 166 | 0.0004059 | 0.00010173 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 74 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_538-7_0_3_line_0 |  | 0 | 1 | 0.02184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_538-7_0_3_line_1 |  | 1 | 2 | 0.056492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_538-7_0_3_line_2 |  | 1 | 3 | 0.018591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_538-7_0_3_line_3 |  | 2 | 4 | 0.065384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_538-7_0_3_line_4 |  | 2 | 5 | 0.016933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_538-7_0_3_line_5 |  | 3 | 6 | 0.030052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_538-7_0_3_line_6 |  | 4 | 11 | 0.0094866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_538-7_0_3_line_7 |  | 5 | 10 | 0.018187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_538-7_0_3_line_8 |  | 6 | 7 | 0.0072221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_538-7_0_3_line_9 |  | 7 | 8 | 0.032821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_538-7_0_3_line_10 |  | 8 | 9 | 6.9442e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_538-7_0_3_line_11 |  | 11 | 15 | 0.042374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_538-7_0_3_line_12 |  | 12 | 13 | 0.013399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_538-7_0_3_line_13 |  | 13 | 14 | 0.03619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_538-7_0_3_line_14 |  | 14 | 31 | 0.030373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_538-7_0_3_line_15 |  | 15 | 16 | 0.018476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_538-7_0_3_line_16 |  | 15 | 17 | 0.025949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_538-7_0_3_line_17 |  | 16 | 18 | 0.0067124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_538-7_0_3_line_18 |  | 17 | 19 | 0.0057756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_538-7_0_3_line_19 |  | 19 | 20 | 0.00041565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_538-7_0_3_line_20 |  | 20 | 21 | 0.015865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_538-7_0_3_line_21 |  | 21 | 22 | 0.010976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_538-7_0_3_line_22 |  | 22 | 23 | 0.013776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_538-7_0_3_line_23 |  | 23 | 24 | 0.021664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_538-7_0_3_line_24 |  | 24 | 29 | 0.037103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_538-7_0_3_line_25 |  | 25 | 26 | 0.078438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_538-7_0_3_line_26 |  | 26 | 27 | 0.018547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_538-7_0_3_line_27 |  | 27 | 28 | 0.00015753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_538-7_0_3_line_28 |  | 28 | 30 | 0.0063706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_538-7_0_3_line_29 |  | 29 | 30 | 0.01821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_538-7_0_3_line_30 |  | 29 | 31 | 0.034085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_538-7_0_3_line_31 |  | 30 | 32 | 0.035299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_538-7_0_3_line_32 |  | 32 | 39 | 0.05756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_538-7_0_3_line_33 |  | 33 | 34 | 0.00023686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_538-7_0_3_line_34 |  | 34 | 130 | 0.020257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_538-7_0_3_line_35 |  | 35 | 36 | 0.034321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_538-7_0_3_line_36 |  | 35 | 37 | 0.012843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_538-7_0_3_line_37 |  | 36 | 38 | 0.0063321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_538-7_0_3_line_38 |  | 37 | 39 | 0.052355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_538-7_0_3_line_39 |  | 37 | 40 | 0.027307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_538-7_0_3_line_40 |  | 38 | 41 | 0.04448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_538-7_0_3_line_41 |  | 38 | 42 | 0.041003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_538-7_0_3_line_42 |  | 39 | 43 | 0.015055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_538-7_0_3_line_43 |  | 40 | 44 | 0.022272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_538-7_0_3_line_44 |  | 41 | 46 | 0.01656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_538-7_0_3_line_45 |  | 42 | 47 | 0.0029159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_538-7_0_3_line_46 |  | 43 | 45 | 0.00084121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_538-7_0_3_line_47 |  | 44 | 48 | 0.029702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_538-7_0_3_line_48 |  | 44 | 49 | 0.0076747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_538-7_0_3_line_49 |  | 45 | 52 | 0.018668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_538-7_0_3_line_50 |  | 45 | 51 | 0.009576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_538-7_0_3_line_51 |  | 46 | 160 | 0.012025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_538-7_0_3_line_52 |  | 48 | 50 | 0.016746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_538-7_0_3_line_53 |  | 52 | 53 | 0.051888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_538-7_0_3_line_54 |  | 53 | 54 | 0.010956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_538-7_0_3_line_55 |  | 54 | 55 | 0.034242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_538-7_0_3_line_56 |  | 54 | 56 | 0.018586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_538-7_0_3_line_57 |  | 55 | 62 | 0.024178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_538-7_0_3_line_58 |  | 55 | 63 | 0.018252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_538-7_0_3_line_59 |  | 56 | 59 | 0.030308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_538-7_0_3_line_60 |  | 57 | 58 | 0.0015517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_538-7_0_3_line_61 |  | 58 | 80 | 0.0071137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_538-7_0_3_line_62 |  | 59 | 60 | 0.025305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_538-7_0_3_line_63 |  | 60 | 61 | 0.025233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_538-7_0_3_line_64 |  | 61 | 64 | 0.088967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_538-7_0_3_line_65 |  | 62 | 85 | 0.027523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_538-7_0_3_line_66 |  | 63 | 75 | 0.027154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_538-7_0_3_line_67 |  | 64 | 65 | 0.032698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_538-7_0_3_line_68 |  | 65 | 66 | 0.018548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_538-7_0_3_line_69 |  | 66 | 163 | 0.0099083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_538-7_0_3_line_70 |  | 66 | 162 | 0.11156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_538-7_0_3_line_71 |  | 67 | 68 | 0.030643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_538-7_0_3_line_72 |  | 67 | 69 | 0.022567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_538-7_0_3_line_73 |  | 68 | 70 | 0.0035116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_538-7_0_3_line_74 |  | 69 | 71 | 0.015758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_538-7_0_3_line_75 |  | 69 | 72 | 0.036729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_538-7_0_3_line_76 |  | 70 | 73 | 0.013757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_538-7_0_3_line_77 |  | 71 | 74 | 0.00098194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_538-7_0_3_line_78 |  | 72 | 75 | 0.011491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_538-7_0_3_line_79 |  | 73 | 143 | 0.023498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_538-7_0_3_line_80 |  | 74 | 80 | 0.017852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_538-7_0_3_line_81 |  | 75 | 76 | 0.0014664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_538-7_0_3_line_82 |  | 76 | 77 | 0.029564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_538-7_0_3_line_83 |  | 77 | 78 | 0.038716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_538-7_0_3_line_84 |  | 78 | 79 | 0.0047646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_538-7_0_3_line_85 |  | 79 | 86 | 0.029305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_538-7_0_3_line_86 |  | 80 | 84 | 0.021007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_538-7_0_3_line_87 |  | 81 | 82 | 0.013305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_538-7_0_3_line_88 |  | 81 | 83 | 0.024397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_538-7_0_3_line_89 |  | 82 | 138 | 0.016697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_538-7_0_3_line_90 |  | 82 | 134 | 0.011336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_538-7_0_3_line_91 |  | 83 | 139 | 0.0051905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_538-7_0_3_line_92 |  | 84 | 138 | 0.025982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_538-7_0_3_line_93 |  | 86 | 87 | 0.017211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_538-7_0_3_line_94 |  | 86 | 88 | 0.0028772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_538-7_0_3_line_95 |  | 87 | 92 | 0.015272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_538-7_0_3_line_96 |  | 88 | 89 | 0.011252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_538-7_0_3_line_97 |  | 89 | 90 | 0.028502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_538-7_0_3_line_98 |  | 90 | 91 | 0.020441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_538-7_0_3_line_99 |  | 91 | 93 | 0.043824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_538-7_0_3_line_100 |  | 92 | 94 | 0.013207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_538-7_0_3_line_101 |  | 94 | 95 | 0.06074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_538-7_0_3_line_102 |  | 95 | 96 | 0.02371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_538-7_0_3_line_103 |  | 96 | 97 | 0.0023994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_538-7_0_3_line_104 |  | 97 | 98 | 0.027057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_538-7_0_3_line_105 |  | 98 | 99 | 0.022134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_538-7_0_3_line_106 |  | 99 | 100 | 0.0055507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_538-7_0_3_line_107 |  | 99 | 101 | 0.014801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_538-7_0_3_line_108 |  | 100 | 102 | 0.011704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_538-7_0_3_line_109 |  | 101 | 103 | 0.022923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_538-7_0_3_line_110 |  | 102 | 104 | 0.018269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_538-7_0_3_line_111 |  | 102 | 105 | 0.027135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_538-7_0_3_line_112 |  | 103 | 112 | 0.016531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_538-7_0_3_line_113 |  | 104 | 106 | 0.051038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_538-7_0_3_line_114 |  | 105 | 107 | 0.0021273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_538-7_0_3_line_115 |  | 106 | 108 | 1.9809e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_538-7_0_3_line_116 |  | 107 | 110 | 0.018874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_538-7_0_3_line_117 |  | 108 | 109 | 0.021325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_538-7_0_3_line_118 |  | 109 | 155 | 0.037847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_538-7_0_3_line_119 |  | 110 | 111 | 0.0060765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_538-7_0_3_line_120 |  | 112 | 113 | 0.019496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_538-7_0_3_line_121 |  | 112 | 114 | 0.051401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_538-7_0_3_line_122 |  | 113 | 115 | 0.013152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_538-7_0_3_line_123 |  | 113 | 116 | 0.022831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_538-7_0_3_line_124 |  | 114 | 117 | 0.051994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_538-7_0_3_line_125 |  | 114 | 118 | 0.018788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_538-7_0_3_line_126 |  | 117 | 119 | 0.028357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_538-7_0_3_line_127 |  | 118 | 123 | 0.026373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_538-7_0_3_line_128 |  | 119 | 120 | 0.020829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_538-7_0_3_line_129 |  | 120 | 121 | 0.017204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_538-7_0_3_line_130 |  | 121 | 122 | 0.037402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_538-7_0_3_line_131 |  | 122 | 126 | 0.00098527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_538-7_0_3_line_132 |  | 123 | 124 | 0.0062275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_538-7_0_3_line_133 |  | 124 | 125 | 0.016153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_538-7_0_3_line_134 |  | 126 | 127 | 0.055873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_538-7_0_3_line_135 |  | 127 | 128 | 0.039473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_538-7_0_3_line_136 |  | 128 | 129 | 0.051505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_538-7_0_3_line_137 |  | 130 | 131 | 0.02916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_538-7_0_3_line_138 |  | 131 | 132 | 0.031708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_538-7_0_3_line_139 |  | 132 | 135 | 0.047961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_538-7_0_3_line_140 |  | 132 | 133 | 0.0079286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_538-7_0_3_line_141 |  | 133 | 134 | 0.030198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_538-7_0_3_line_142 |  | 134 | 136 | 0.017567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_538-7_0_3_line_143 |  | 135 | 137 | 0.011881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_538-7_0_3_line_144 |  | 137 | 152 | 0.020408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_538-7_0_3_line_145 |  | 139 | 140 | 0.025505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_538-7_0_3_line_146 |  | 140 | 141 | 0.025677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_538-7_0_3_line_147 |  | 141 | 142 | 0.03507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_538-7_0_3_line_148 |  | 143 | 144 | 0.0078357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_538-7_0_3_line_149 |  | 144 | 145 | 0.017592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_538-7_0_3_line_150 |  | 145 | 146 | 0.01095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_538-7_0_3_line_151 |  | 146 | 147 | 0.01707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_538-7_0_3_line_152 |  | 147 | 148 | 0.0018737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_538-7_0_3_line_153 |  | 148 | 149 | 0.017724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_538-7_0_3_line_154 |  | 149 | 150 | 0.015519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_538-7_0_3_line_155 |  | 151 | 152 | 0.014236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_538-7_0_3_line_156 |  | 153 | 154 | 0.026601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_538-7_0_3_line_157 |  | 154 | 155 | 0.088118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_538-7_0_3_line_158 |  | 155 | 156 | 0.016444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_538-7_0_3_line_159 |  | 156 | 157 | 0.1721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_538-7_0_3_line_160 |  | 157 | 158 | 0.013345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_538-7_0_3_line_161 |  | 159 | 160 | 0.012761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_538-7_0_3_line_162 |  | 159 | 161 | 0.033096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_538-7_0_3_line_163 |  | 163 | 164 | 0.034505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_538-7_0_3_line_164 |  | 164 | 165 | 0.11877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_538-7_0_3_line_165 |  | 165 | 166 | 0.032794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_538-7_0_3_trafo_71 | 0.63 MVA 20/0.4 kV | 167 | 74 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2602441.0555 | 1216640.2723 | 2602430.1018 | 1216659.1672
1 | 2602441.0555 | 1216640.2723 | 2602445.2248 | 1216636.305 | 2602451.4971 | 1216631.7161 | 2602461.3225 | 1216626.2947 | 2602471.9447 | 1216621.7297 | 2602483.6145 | 1216617.2652 | 2602491.1233 | 1216615.1004
2 | 2602441.0555 | 1216640.2723 | 2602456.3083 | 1216650.9014
3 | 2602491.1233 | 1216615.1004 | 2602500.7048 | 1216612.3361 | 2602521.143 | 1216607.1971 | 2602553.0522 | 1216601.0735 | 2602554.8757 | 1216600.7897
4 | 2602491.1233 | 1216615.1004 | 2602498.0092 | 1216630.5706
5 | 2602456.3083 | 1216650.9014 | 2602461.759 | 1216654.6998 | 2602466.3432 | 1216657.1364 | 2602470.0017 | 1216658.5609 | 2602474.3056 | 1216659.352 | 2602481.7375 | 1216659.5884 | 2602484.2167 | 1216659.6103
6 | 2602554.8757 | 1216600.7897 | 2602564.2495 | 1216599.3307
7 | 2602503.4353 | 1216647.7066 | 2602503.2425 | 1216644.0773 | 2602502.9625 | 1216642.0427 | 2602502.1207 | 1216639.8077 | 2602498.0092 | 1216630.5706
8 | 2602484.2167 | 1216659.6103 | 2602491.4385 | 1216659.6738
9 | 2602524.2585 | 1216659.9628 | 2602491.4385 | 1216659.6738
10 | 2602524.2585 | 1216659.9628 | 2602524.328 | 1216659.9634
11 | 2602606.1728 | 1216593.1914 | 2602591.5205 | 1216595.0862 | 2602564.2495 | 1216599.3307
12 | 2602686.741 | 1216661.5649 | 2602679.3019 | 1216660.7612 | 2602673.3861 | 1216660.8355
13 | 2602686.741 | 1216661.5649 | 2602704.5442 | 1216630.0565
14 | 2602719.4856 | 1216603.6127 | 2602704.5442 | 1216630.0565
15 | 2602606.1728 | 1216593.1914 | 2602607.7438 | 1216611.6
16 | 2602606.1728 | 1216593.1914 | 2602631.9076 | 1216589.8642
17 | 2602608.3145 | 1216618.2881 | 2602607.7438 | 1216611.6
18 | 2602631.9076 | 1216589.8642 | 2602637.6356 | 1216589.1237
19 | 2602637.6356 | 1216589.1237 | 2602638.0478 | 1216589.0704
20 | 2602653.7816 | 1216587.0362 | 2602638.0478 | 1216589.0704
21 | 2602653.7816 | 1216587.0362 | 2602664.6666 | 1216585.629
22 | 2602664.6666 | 1216585.629 | 2602676.4507 | 1216584.1054 | 2602678.3176 | 1216583.788
23 | 2602699.6748 | 1216580.1566 | 2602678.3176 | 1216583.788
24 | 2602736.2531 | 1216573.9372 | 2602699.6748 | 1216580.1566
25 | 2602663.2472 | 1216526.1654 | 2602734.2481 | 1216559.5025
26 | 2602750.7913 | 1216567.8198 | 2602747.9779 | 1216565.9491 | 2602734.2481 | 1216559.5025
27 | 2602750.7913 | 1216567.8198 | 2602750.9225 | 1216567.9071
28 | 2602754.4729 | 1216573.1116 | 2602753.2519 | 1216570.4874 | 2602750.9225 | 1216567.9071 | 2602750.9225 | 1216567.9071
29 | 2602736.2531 | 1216573.9372 | 2602742.9642 | 1216573.2176 | 2602749.1514 | 1216572.9869 | 2602754.4729 | 1216573.1116
30 | 2602736.2531 | 1216573.9372 | 2602719.4856 | 1216603.6127
31 | 2602754.4729 | 1216573.1116 | 2602781.8159 | 1216576.4592 | 2602789.5678 | 1216576.5172
32 | 2602844.1571 | 1216559.734 | 2602829.3202 | 1216566.5532 | 2602816.0328 | 1216571.5388 | 2602806.1474 | 1216574.4025 | 2602797.7126 | 1216575.9551 | 2602791.3051 | 1216576.5303 | 2602789.5678 | 1216576.5172
33 | 2602782.5463 | 1216687.4122 | 2602782.3271 | 1216687.3222 | 2602782.3271 | 1216687.3222
34 | 2602800.6228 | 1216696.4841 | 2602798.2198 | 1216695.0116 | 2602793.2867 | 1216692.2856 | 2602788.1562 | 1216689.7151 | 2602782.5463 | 1216687.4122
35 | 2602798.0146 | 1216513.6024 | 2602785.1081 | 1216498.4944 | 2602778.0292 | 1216489.7529 | 2602776.0697 | 1216487.2205
36 | 2602806.7252 | 1216523.0404 | 2602798.0676 | 1216513.6644 | 2602798.0146 | 1216513.6024
37 | 2602772.1947 | 1216482.2126 | 2602776.0697 | 1216487.2205
38 | 2602844.1571 | 1216559.734 | 2602818.4561 | 1216535.1415 | 2602808.2579 | 1216524.7865 | 2602806.7252 | 1216523.0404
39 | 2602806.7252 | 1216523.0404 | 2602831.9954 | 1216512.6933
40 | 2602772.1947 | 1216482.2126 | 2602759.472 | 1216463.5741 | 2602747.8478 | 1216444.9987
41 | 2602772.1947 | 1216482.2126 | 2602794.4529 | 1216466.1915 | 2602805.9423 | 1216458.9556
42 | 2602844.1571 | 1216559.734 | 2602850.0991 | 1216564.1726 | 2602856.6005 | 1216568.1814
43 | 2602852.291 | 1216503.5504 | 2602841.8199 | 1216508.6707 | 2602831.9954 | 1216512.6933
44 | 2602739.0632 | 1216430.961 | 2602747.8478 | 1216444.9987
45 | 2602805.9423 | 1216458.9556 | 2602808.4097 | 1216457.4017
46 | 2602857.3166 | 1216568.6229 | 2602856.6005 | 1216568.1814
47 | 2602878.5762 | 1216512.8903 | 2602875.7305 | 1216510.4876 | 2602864.2937 | 1216502.6889 | 2602854.0679 | 1216502.6841 | 2602852.291 | 1216503.5504
48 | 2602852.291 | 1216503.5504 | 2602858.6169 | 1216507.8961
49 | 2602857.3166 | 1216568.6229 | 2602873.5959 | 1216577.7602
50 | 2602857.3166 | 1216568.6229 | 2602862.5294 | 1216560.5902
51 | 2602739.0632 | 1216430.961 | 2602737.8363 | 1216429.0004 | 2602732.2222 | 1216421.0755
52 | 2602868.4959 | 1216526.282 | 2602878.5762 | 1216512.8903
53 | 2602918.1605 | 1216603.9161 | 2602916.5975 | 1216602.2033 | 2602914.1541 | 1216600.0342 | 2602910.5417 | 1216597.5311 | 2602884.039 | 1216583.6218 | 2602873.5959 | 1216577.7602
54 | 2602918.1605 | 1216603.9161 | 2602927.2504 | 1216597.7614
55 | 2602927.2504 | 1216597.7614 | 2602931.7973 | 1216598.4084 | 2602937.3763 | 1216599.8453 | 2602940.4428 | 1216600.6917 | 2602944.7767 | 1216602.4169 | 2602948.7537 | 1216604.4311 | 2602953.1021 | 1216607.3126 | 2602956.4183 | 1216610.0158 | 2602957.9282 | 1216611.5729
56 | 2602927.2504 | 1216597.7614 | 2602933.8991 | 1216580.4051
57 | 2602957.9282 | 1216611.5729 | 2602964.2478 | 1216604.3719 | 2602972.4979 | 1216592.3024
58 | 2602957.9282 | 1216611.5729 | 2602959.514 | 1216613.2191 | 2602968.0948 | 1216623.7848 | 2602969.6858 | 1216625.5214
59 | 2602933.8991 | 1216580.4051 | 2602944.741 | 1216552.1027
60 | 2602924.271 | 1216644.7087 | 2602924.3617 | 1216646.2578
61 | 2602925.045 | 1216653.3363 | 2602924.4931 | 1216648.5 | 2602924.3617 | 1216646.2578
62 | 2602944.741 | 1216552.1027 | 2602949.1109 | 1216540.6952 | 2602951.5502 | 1216535.6602 | 2602954.0348 | 1216531.2367 | 2602955.3828 | 1216529.2254
63 | 2602971.3596 | 1216509.7274 | 2602963.0821 | 1216519.1453 | 2602957.4762 | 1216526.1021 | 2602955.3828 | 1216529.2254
64 | 2602971.3596 | 1216509.7274 | 2603023.3929 | 1216450.525 | 2603025.9606 | 1216447.091 | 2603027.3055 | 1216444.5791 | 2603028.1872 | 1216442.4228 | 2603028.3336 | 1216441.7573
65 | 2602972.4979 | 1216592.3024 | 2602999.2696 | 1216599.0082
66 | 2602988.0267 | 1216645.5179 | 2602982.4655 | 1216638.8003 | 2602974.066 | 1216630.3025 | 2602969.6858 | 1216625.5214
67 | 2603025.5444 | 1216411.5223 | 2603029.9233 | 1216416.6535 | 2603031.1599 | 1216418.4107 | 2603031.721 | 1216419.8673 | 2603031.9404 | 1216421.3572 | 2603031.8483 | 1216423.3916 | 2603029.1459 | 1216438.0652 | 2603028.3336 | 1216441.7573
68 | 2603023.5216 | 1216394.6235 | 2603021.618 | 1216401.4408 | 2603021.2676 | 1216403.8531 | 2603021.4716 | 1216405.7654 | 2603022.3513 | 1216407.7225 | 2603025.1206 | 1216411.0257 | 2603025.5444 | 1216411.5223
69 | 2603023.5216 | 1216394.6235 | 2603026.1864 | 1216385.0802
70 | 2603023.5216 | 1216394.6235 | 2602912.5113 | 1216383.5443
71 | 2602968.6615 | 1216689.0508 | 2602993.3284 | 1216707.232
72 | 2602950.4956 | 1216675.6612 | 2602968.6615 | 1216689.0508
73 | 2602993.3284 | 1216707.232 | 2602996.1551 | 1216709.3155
74 | 2602950.4956 | 1216675.6612 | 2602937.5942 | 1216666.613
75 | 2602950.4956 | 1216675.6612 | 2602961.4698 | 1216665.8609 | 2602973.3552 | 1216655.8388 | 2602978.5024 | 1216651.9212
76 | 2603007.2293 | 1216717.478 | 2602996.1551 | 1216709.3155
77 | 2602937.5942 | 1216666.613 | 2602936.7903 | 1216666.0491
78 | 2602988.0267 | 1216645.5179 | 2602982.3619 | 1216648.9838 | 2602978.5024 | 1216651.9212
79 | 2603007.2293 | 1216717.478 | 2603026.1444 | 1216731.4198
80 | 2602925.045 | 1216653.3363 | 2602926.0531 | 1216656.5164 | 2602926.6522 | 1216657.7729 | 2602927.6309 | 1216659.0074 | 2602929.4672 | 1216660.7426 | 2602930.78 | 1216661.7438 | 2602936.7903 | 1216666.0491
81 | 2602988.0267 | 1216645.5179 | 2602989.3892 | 1216644.9757
82 | 2603018.2347 | 1216638.6146 | 2603003.7124 | 1216641.6123 | 2602993.949 | 1216643.553 | 2602990.4261 | 1216644.563 | 2602989.3892 | 1216644.9757
83 | 2603018.2347 | 1216638.6146 | 2603056.1515 | 1216630.7878
84 | 2603060.6297 | 1216632.1019 | 2603058.7855 | 1216631.1115 | 2603057.404 | 1216630.7884 | 2603056.1515 | 1216630.7878 | 2603056.1515 | 1216630.7878
85 | 2603085.8256 | 1216617.0171 | 2603060.6297 | 1216632.1019
86 | 2602925.045 | 1216653.3363 | 2602921.5953 | 1216660.0384 | 2602919.8624 | 1216664.2956 | 2602917.2925 | 1216672.7876
87 | 2602914.7666 | 1216716.3004 | 2602901.9543 | 1216712.581
88 | 2602914.7666 | 1216716.3004 | 2602916.4047 | 1216719.603 | 2602919.5683 | 1216723.7069 | 2602927.1258 | 1216730.9257 | 2602930.9335 | 1216734.284
89 | 2602901.9543 | 1216712.581 | 2602908.4439 | 1216697.1973
90 | 2602893.4186 | 1216719.0696 | 2602896.5845 | 1216718.3373 | 2602898.46 | 1216717.4266 | 2602900.0245 | 1216715.8709 | 2602901.9543 | 1216712.581
91 | 2602934.8262 | 1216737.7173 | 2602930.9335 | 1216734.284
92 | 2602917.2925 | 1216672.7876 | 2602915.7718 | 1216677.8124 | 2602911.4541 | 1216690.0617 | 2602908.4439 | 1216697.1973
93 | 2603085.8256 | 1216617.0171 | 2603093.6861 | 1216625.2369 | 2603098.0099 | 1216629.1591
94 | 2603085.8256 | 1216617.0171 | 2603088.3131 | 1216615.5713
95 | 2603098.0099 | 1216629.1591 | 2603109.1123 | 1216639.2304 | 2603109.3281 | 1216639.4123
96 | 2603098.0408 | 1216609.9171 | 2603088.3131 | 1216615.5713
97 | 2603098.0408 | 1216609.9171 | 2603122.6828 | 1216595.5942
98 | 2603122.6828 | 1216595.5942 | 2603140.3555 | 1216585.3222
99 | 2603175.809 | 1216559.7161 | 2603173.9224 | 1216561.4754 | 2603165.0593 | 1216568.8527 | 2603158.7104 | 1216573.6744 | 2603150.691 | 1216578.9399 | 2603140.5001 | 1216585.2382 | 2603140.3555 | 1216585.3222
100 | 2603109.3281 | 1216639.4123 | 2603116.3893 | 1216645.3598 | 2603119.6187 | 1216647.6765
101 | 2603119.6187 | 1216647.6765 | 2603126.3303 | 1216652.4912 | 2603137.0913 | 1216659.4562 | 2603146.2588 | 1216664.8529 | 2603171.8335 | 1216678.5756
102 | 2603171.8335 | 1216678.5756 | 2603185.2901 | 1216685.7961 | 2603192.9312 | 1216689.3775
103 | 2603195.1038 | 1216690.3958 | 2603192.9312 | 1216689.3775
104 | 2603195.1038 | 1216690.3958 | 2603219.6037 | 1216701.8789
105 | 2603239.6456 | 1216711.2725 | 2603219.6037 | 1216701.8789
106 | 2603239.6456 | 1216711.2725 | 2603245.0448 | 1216712.5604
107 | 2603239.6456 | 1216711.2725 | 2603235.1404 | 1216725.3717
108 | 2603256.5191 | 1216714.8391 | 2603249.6421 | 1216713.657 | 2603245.0448 | 1216712.5604
109 | 2603235.1404 | 1216725.3717 | 2603228.1631 | 1216747.2073
110 | 2603256.5191 | 1216714.8391 | 2603272.3208 | 1216705.6707
111 | 2603256.5191 | 1216714.8391 | 2603264.7289 | 1216722.37 | 2603277.1991 | 1216732.3852
112 | 2603221.7259 | 1216762.3475 | 2603223.3822 | 1216759.6913 | 2603225.7153 | 1216754.8676 | 2603228.1631 | 1216747.2073
113 | 2603272.3208 | 1216705.6707 | 2603281.2137 | 1216700.5109 | 2603312.3981 | 1216687.7984 | 2603319.4332 | 1216686.9933
114 | 2603278.8577 | 1216733.7174 | 2603277.1991 | 1216732.3852
115 | 2603319.4529 | 1216686.9911 | 2603319.4332 | 1216686.9933
116 | 2603278.8577 | 1216733.7174 | 2603264.4565 | 1216745.9169
117 | 2603340.6397 | 1216684.5666 | 2603319.4529 | 1216686.9911
118 | 2603378.2417 | 1216680.2636 | 2603340.6397 | 1216684.5666
119 | 2603264.4565 | 1216745.9169 | 2603261.3747 | 1216748.5275 | 2603259.6927 | 1216749.6777
120 | 2603221.7259 | 1216762.3475 | 2603219.0248 | 1216759.8336 | 2603216.5888 | 1216758.2647 | 2603204.9013 | 1216752.6887
121 | 2603221.7259 | 1216762.3475 | 2603214.9057 | 1216768.6253 | 2603210.8195 | 1216772.6587 | 2603206.6116 | 1216777.1813 | 2603192.0726 | 1216795.1172 | 2603187.4923 | 1216800.5734
122 | 2603204.9013 | 1216752.6887 | 2603194.5274 | 1216760.8101
123 | 2603196.0453 | 1216732.4393 | 2603199.0124 | 1216734.6421 | 2603200.2868 | 1216736.4215 | 2603201.1589 | 1216738.0563 | 2603204.9013 | 1216752.6887
124 | 2603156.142 | 1216842.114 | 2603187.4923 | 1216800.5734
125 | 2603187.4923 | 1216800.5734 | 2603203.5546 | 1216810.3198
126 | 2603156.142 | 1216842.114 | 2603179.6441 | 1216857.9807
127 | 2603226.1011 | 1216824.0007 | 2603203.5546 | 1216810.3198
128 | 2603196.9074 | 1216869.6355 | 2603179.6441 | 1216857.9807
129 | 2603196.9074 | 1216869.6355 | 2603211.1663 | 1216879.262
130 | 2603211.1663 | 1216879.262 | 2603229.6433 | 1216891.7361 | 2603241.9156 | 1216900.549
131 | 2603242.7159 | 1216901.1237 | 2603241.9156 | 1216900.549
132 | 2603226.1011 | 1216824.0007 | 2603231.4251 | 1216827.2312
133 | 2603245.4818 | 1216828.0084 | 2603240.7355 | 1216831.4412 | 2603235.8856 | 1216829.9378 | 2603231.4251 | 1216827.2312
134 | 2603284.6155 | 1216938.0473 | 2603253.295 | 1216909.5811 | 2603245.2293 | 1216902.9285 | 2603242.7159 | 1216901.1237
135 | 2603284.6155 | 1216938.0473 | 2603313.6408 | 1216964.7985
136 | 2603313.6408 | 1216964.7985 | 2603335.5253 | 1216984.9683 | 2603351.8571 | 1216999.3222
137 | 2602825.6253 | 1216711.4857 | 2602824.4481 | 1216710.8549 | 2602810.1121 | 1216702.299 | 2602800.6228 | 1216696.4841
138 | 2602855.3624 | 1216721.3863 | 2602851.5213 | 1216721.2066 | 2602846.0333 | 1216720.2035 | 2602840.7429 | 1216718.7558 | 2602834.4357 | 1216716.207 | 2602825.6253 | 1216711.4857
139 | 2602855.3624 | 1216721.3863 | 2602844.7073 | 1216747.4516 | 2602844.6609 | 1216749.4639 | 2602845.0016 | 1216751.3651 | 2602846.056 | 1216753.0888 | 2602847.8162 | 1216755.1686 | 2602851.5119 | 1216757.7718 | 2602857.2963 | 1216760.9322
140 | 2602855.3624 | 1216721.3863 | 2602863.2764 | 1216720.9045
141 | 2602893.4186 | 1216719.0696 | 2602863.2764 | 1216720.9045
142 | 2602893.4186 | 1216719.0696 | 2602884.6966 | 1216734.3296
143 | 2602867.7226 | 1216766.6288 | 2602857.2963 | 1216760.9322
144 | 2602874.1669 | 1216784.1195 | 2602871.0097 | 1216782.4838 | 2602869.2873 | 1216780.6708 | 2602868.3773 | 1216778.7805 | 2602867.5894 | 1216775.3448 | 2602867.3332 | 1216771.3313 | 2602867.7226 | 1216766.6288
145 | 2602934.8262 | 1216737.7173 | 2602939.9647 | 1216742.2494 | 2602944.5171 | 1216747.0432 | 2602948.3484 | 1216751.8255 | 2602951.7772 | 1216756.6444
146 | 2602966.0384 | 1216777.9933 | 2602954.7738 | 1216760.8559 | 2602951.7772 | 1216756.6444
147 | 2602966.0384 | 1216777.9933 | 2602962.8704 | 1216783.1725 | 2602960.1736 | 1216787.0734 | 2602954.1197 | 1216794.9082 | 2602944.5436 | 1216805.6019
148 | 2603032.4519 | 1216736.0689 | 2603026.1444 | 1216731.4198
149 | 2603032.4519 | 1216736.0689 | 2603046.7667 | 1216746.2938
150 | 2603046.7667 | 1216746.2938 | 2603055.6768 | 1216752.6583
151 | 2603069.5674 | 1216762.5803 | 2603055.6768 | 1216752.6583
152 | 2603069.5674 | 1216762.5803 | 2603070.9939 | 1216763.795
153 | 2603070.9939 | 1216763.795 | 2603084.4882 | 1216775.2861
154 | 2603096.2527 | 1216785.4041 | 2603095.4195 | 1216784.5947 | 2603084.4882 | 1216775.2861
155 | 2602874.1669 | 1216784.1195 | 2602876.8466 | 1216784.0652 | 2602879.9366 | 1216783.2885 | 2602882.2525 | 1216782.0222 | 2602883.6651 | 1216780.5776 | 2602885.3214 | 1216777.5322 | 2602885.4087 | 1216777.305
156 | 2603397.2783 | 1216766.3007 | 2603423.2611 | 1216772.002
157 | 2603378.2417 | 1216680.2636 | 2603397.2783 | 1216766.3007
158 | 2603378.2417 | 1216680.2636 | 2603383.0763 | 1216664.5461
159 | 2603383.0763 | 1216664.5461 | 2603434.2065 | 1216500.2194
160 | 2603434.2065 | 1216500.2194 | 2603439.1048 | 1216487.8059
161 | 2602724.8455 | 1216410.6625 | 2602732.2222 | 1216421.0755
162 | 2602724.8455 | 1216410.6625 | 2602716.2895 | 1216398.5847 | 2602705.2113 | 1216384.0261
163 | 2603026.1864 | 1216385.0802 | 2603033.1551 | 1216360.1231 | 2603036.4392 | 1216352.1824
164 | 2603036.4392 | 1216352.1824 | 2603011.3142 | 1216236.0977
165 | 2603011.3142 | 1216236.0977 | 2603007.8148 | 1216235.1621 | 2603003.2453 | 1216233.4589 | 2602981.8958 | 1216221.8633

## bus_geodata
| x | y | coords
0 | 2602430.1018 | 1216659.1672
1 | 2602441.0555 | 1216640.2723
2 | 2602491.1233 | 1216615.1004
3 | 2602456.3083 | 1216650.9014
4 | 2602554.8757 | 1216600.7897
5 | 2602498.0092 | 1216630.5706
6 | 2602484.2167 | 1216659.6103
7 | 2602491.4385 | 1216659.6738
8 | 2602524.2585 | 1216659.9628
9 | 2602524.328 | 1216659.9634
10 | 2602503.4353 | 1216647.7066
11 | 2602564.2495 | 1216599.3307
12 | 2602673.3861 | 1216660.8355
13 | 2602686.741 | 1216661.5649
14 | 2602704.5442 | 1216630.0565
15 | 2602606.1728 | 1216593.1914
16 | 2602607.7438 | 1216611.6
17 | 2602631.9076 | 1216589.8642
18 | 2602608.3145 | 1216618.2881
19 | 2602637.6356 | 1216589.1237
20 | 2602638.0478 | 1216589.0704
21 | 2602653.7816 | 1216587.0362
22 | 2602664.6666 | 1216585.629
23 | 2602678.3176 | 1216583.788
24 | 2602699.6748 | 1216580.1566
25 | 2602663.2472 | 1216526.1654
26 | 2602734.2481 | 1216559.5025
27 | 2602750.7913 | 1216567.8198
28 | 2602750.9225 | 1216567.9071
29 | 2602736.2531 | 1216573.9372
30 | 2602754.4729 | 1216573.1116
31 | 2602719.4856 | 1216603.6127
32 | 2602789.5678 | 1216576.5172
33 | 2602782.3271 | 1216687.3222
34 | 2602782.5463 | 1216687.4122
35 | 2602798.0146 | 1216513.6024
36 | 2602776.0697 | 1216487.2205
37 | 2602806.7252 | 1216523.0404
38 | 2602772.1947 | 1216482.2126
39 | 2602844.1571 | 1216559.734
40 | 2602831.9954 | 1216512.6933
41 | 2602747.8478 | 1216444.9987
42 | 2602805.9423 | 1216458.9556
43 | 2602856.6005 | 1216568.1814
44 | 2602852.291 | 1216503.5504
45 | 2602857.3166 | 1216568.6229
46 | 2602739.0632 | 1216430.961
47 | 2602808.4097 | 1216457.4017
48 | 2602878.5762 | 1216512.8903
49 | 2602858.6169 | 1216507.8961
50 | 2602868.4959 | 1216526.282
51 | 2602862.5294 | 1216560.5902
52 | 2602873.5959 | 1216577.7602
53 | 2602918.1605 | 1216603.9161
54 | 2602927.2504 | 1216597.7614
55 | 2602957.9282 | 1216611.5729
56 | 2602933.8991 | 1216580.4051
57 | 2602924.271 | 1216644.7087
58 | 2602924.3617 | 1216646.2578
59 | 2602944.741 | 1216552.1027
60 | 2602955.3828 | 1216529.2254
61 | 2602971.3596 | 1216509.7274
62 | 2602972.4979 | 1216592.3024
63 | 2602969.6858 | 1216625.5214
64 | 2603028.3336 | 1216441.7573
65 | 2603025.5444 | 1216411.5223
66 | 2603023.5216 | 1216394.6235
67 | 2602968.6615 | 1216689.0508
68 | 2602993.3284 | 1216707.232
69 | 2602950.4956 | 1216675.6612
70 | 2602996.1551 | 1216709.3155
71 | 2602937.5942 | 1216666.613
72 | 2602978.5024 | 1216651.9212
73 | 2603007.2293 | 1216717.478
74 | 2602936.7903 | 1216666.0491
75 | 2602988.0267 | 1216645.5179
76 | 2602989.3892 | 1216644.9757
77 | 2603018.2347 | 1216638.6146
78 | 2603056.1515 | 1216630.7878
79 | 2603060.6297 | 1216632.1019
80 | 2602925.045 | 1216653.3363
81 | 2602914.7666 | 1216716.3004
82 | 2602901.9543 | 1216712.581
83 | 2602930.9335 | 1216734.284
84 | 2602917.2925 | 1216672.7876
85 | 2602999.2696 | 1216599.0082
86 | 2603085.8256 | 1216617.0171
87 | 2603098.0099 | 1216629.1591
88 | 2603088.3131 | 1216615.5713
89 | 2603098.0408 | 1216609.9171
90 | 2603122.6828 | 1216595.5942
91 | 2603140.3555 | 1216585.3222
92 | 2603109.3281 | 1216639.4123
93 | 2603175.809 | 1216559.7161
94 | 2603119.6187 | 1216647.6765
95 | 2603171.8335 | 1216678.5756
96 | 2603192.9312 | 1216689.3775
97 | 2603195.1038 | 1216690.3958
98 | 2603219.6037 | 1216701.8789
99 | 2603239.6456 | 1216711.2725
100 | 2603245.0448 | 1216712.5604
101 | 2603235.1404 | 1216725.3717
102 | 2603256.5191 | 1216714.8391
103 | 2603228.1631 | 1216747.2073
104 | 2603272.3208 | 1216705.6707
105 | 2603277.1991 | 1216732.3852
106 | 2603319.4332 | 1216686.9933
107 | 2603278.8577 | 1216733.7174
108 | 2603319.4529 | 1216686.9911
109 | 2603340.6397 | 1216684.5666
110 | 2603264.4565 | 1216745.9169
111 | 2603259.6927 | 1216749.6777
112 | 2603221.7259 | 1216762.3475
113 | 2603204.9013 | 1216752.6887
114 | 2603187.4923 | 1216800.5734
115 | 2603194.5274 | 1216760.8101
116 | 2603196.0453 | 1216732.4393
117 | 2603156.142 | 1216842.114
118 | 2603203.5546 | 1216810.3198
119 | 2603179.6441 | 1216857.9807
120 | 2603196.9075 | 1216869.6355
121 | 2603211.1663 | 1216879.262
122 | 2603241.9156 | 1216900.549
123 | 2603226.1011 | 1216824.0007
124 | 2603231.4251 | 1216827.2312
125 | 2603245.4818 | 1216828.0084
126 | 2603242.7159 | 1216901.1237
127 | 2603284.6155 | 1216938.0473
128 | 2603313.6408 | 1216964.7985
129 | 2603351.8571 | 1216999.3222
130 | 2602800.6228 | 1216696.4841
131 | 2602825.6253 | 1216711.4857
132 | 2602855.3624 | 1216721.3863
133 | 2602863.2764 | 1216720.9045
134 | 2602893.4186 | 1216719.0696
135 | 2602857.2963 | 1216760.9322
136 | 2602884.6966 | 1216734.3296
137 | 2602867.7226 | 1216766.6288
138 | 2602908.4439 | 1216697.1973
139 | 2602934.8262 | 1216737.7173
140 | 2602951.7772 | 1216756.6444
141 | 2602966.0384 | 1216777.9933
142 | 2602944.5436 | 1216805.6019
143 | 2603026.1444 | 1216731.4198
144 | 2603032.4519 | 1216736.0689
145 | 2603046.7667 | 1216746.2938
146 | 2603055.6768 | 1216752.6583
147 | 2603069.5674 | 1216762.5802
148 | 2603070.9939 | 1216763.795
149 | 2603084.4882 | 1216775.2861
150 | 2603096.2527 | 1216785.4041
151 | 2602885.4087 | 1216777.305
152 | 2602874.1669 | 1216784.1195
153 | 2603423.2611 | 1216772.002
154 | 2603397.2783 | 1216766.3007
155 | 2603378.2417 | 1216680.2636
156 | 2603383.0763 | 1216664.5461
157 | 2603434.2065 | 1216500.2194
158 | 2603439.1048 | 1216487.8059
159 | 2602724.8455 | 1216410.6625
160 | 2602732.2222 | 1216421.0755
161 | 2602705.2113 | 1216384.0261
162 | 2602912.5113 | 1216383.5443
163 | 2603026.1864 | 1216385.0802
164 | 2603036.4392 | 1216352.1824
165 | 2603011.3142 | 1216236.0977
166 | 2602981.8958 | 1216221.8633
167 | 2602950.4956 | 1216675.6612

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1