## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_546-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_546-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_546-5_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_546-5_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_546-5_0_4_node_38 | 0.4 | n |  | TRUE
5 | bus_LV_546-5_0_4_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_546-5_0_4_node_61 | 0.4 | n |  | TRUE
7 | bus_LV_546-5_0_4_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_546-5_0_4_node_36 | 0.4 | n |  | TRUE
9 | bus_LV_546-5_0_4_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_546-5_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_546-5_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_546-5_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_546-5_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_546-5_0_4_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_546-5_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_546-5_0_4_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_546-5_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_546-5_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_546-5_0_4_node_56 | 0.4 | n |  | TRUE
20 | bus_LV_546-5_0_4_node_54 | 0.4 | n |  | TRUE
21 | bus_LV_546-5_0_4_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_546-5_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_546-5_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_546-5_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_546-5_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_546-5_0_4_node_58 | 0.4 | n |  | TRUE
27 | bus_LV_546-5_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_546-5_0_4_node_59 | 0.4 | n |  | TRUE
29 | bus_LV_546-5_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_546-5_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_546-5_0_4_node_63 | 0.4 | n |  | TRUE
32 | bus_LV_546-5_0_4_node_55 | 0.4 | n |  | TRUE
33 | bus_LV_546-5_0_4_node_53 | 0.4 | n |  | TRUE
34 | bus_LV_546-5_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_546-5_0_4_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_546-5_0_4_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_546-5_0_4_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_546-5_0_4_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_546-5_0_4_node_44 | 0.4 | n |  | TRUE
40 | bus_LV_546-5_0_4_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_546-5_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_546-5_0_4_node_49 | 0.4 | n |  | TRUE
43 | bus_LV_546-5_0_4_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_546-5_0_4_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_546-5_0_4_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_546-5_0_4_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_546-5_0_4_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_546-5_0_4_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_546-5_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_546-5_0_4_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_546-5_0_4_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_546-5_0_4_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_546-5_0_4_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_546-5_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_546-5_0_4_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_546-5_0_4_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_546-5_0_4_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_546-5_0_4_node_62 | 0.4 | n |  | TRUE
59 | bus_MV_415_0_node_30 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_546-5_0_4_load_0 | 0 | 0.015539 | 0.0038945 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_546-5_0_4_load_1 | 1 | 0.016067 | 0.0040267 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_546-5_0_4_load_3 | 2 | 0.0091755 | 0.0022996 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_546-5_0_4_load_38 | 4 | 0.0069052 | 0.0017306 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_546-5_0_4_load_61 | 6 | 0.020694 | 0.0051865 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_546-5_0_4_load_10 | 10 | 0.0024477 | 0.00061345 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_546-5_0_4_load_6 | 11 | 0.014404 | 0.0036101 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_546-5_0_4_load_7 | 12 | 0.015307 | 0.0038362 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_546-5_0_4_load_11 | 15 | 0.0063271 | 0.0015857 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_546-5_0_4_load_18 | 16 | 0.0082785 | 0.0020748 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_546-5_0_4_load_14 | 17 | 0.008442 | 0.0021158 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_546-5_0_4_load_9 | 18 | 0.015958 | 0.0039993 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_546-5_0_4_load_54 | 20 | 0.0017012 | 0.00042635 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_546-5_0_4_load_24 | 21 | 0.0050576 | 0.0012676 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_546-5_0_4_load_16 | 23 | 0.01508 | 0.0037795 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_546-5_0_4_load_17 | 24 | 0.0087236 | 0.0021863 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_546-5_0_4_load_19 | 25 | 0.011522 | 0.0028878 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_546-5_0_4_load_58 | 26 | 0.0061258 | 0.0015353 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_546-5_0_4_load_20 | 27 | 0.0079915 | 0.0020029 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_546-5_0_4_load_59 | 28 | 0.0020398 | 0.00051122 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_546-5_0_4_load_25 | 29 | 0.0058174 | 0.001458 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_546-5_0_4_load_21 | 30 | 0.0023436 | 0.00058737 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_546-5_0_4_load_63 | 31 | 0.0077084 | 0.0019319 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_546-5_0_4_load_55 | 32 | 0.0013751 | 0.00034464 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_546-5_0_4_load_53 | 33 | 0.002465 | 0.00061778 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_546-5_0_4_load_26 | 34 | 0.0053157 | 0.0013323 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_546-5_0_4_load_27 | 35 | 0.012707 | 0.0031846 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_546-5_0_4_load_44 | 39 | 0.020037 | 0.0050218 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_546-5_0_4_load_35 | 40 | 0.0039545 | 0.00099108 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_546-5_0_4_load_32 | 41 | 0.025036 | 0.0062747 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_546-5_0_4_load_49 | 42 | 0.005107 | 0.0012799 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_546-5_0_4_load_33 | 43 | 0.0060719 | 0.0015218 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_546-5_0_4_load_34 | 44 | 0.0063297 | 0.0015864 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_546-5_0_4_load_40 | 47 | 0.03359 | 0.0084184 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_546-5_0_4_load_37 | 48 | 0.0090702 | 0.0022732 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_546-5_0_4_load_39 | 49 | 0.0073538 | 0.001843 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_546-5_0_4_load_43 | 50 | 0.024034 | 0.0060236 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_546-5_0_4_load_45 | 52 | 0.0053238 | 0.0013343 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_546-5_0_4_load_46 | 53 | 0.0044271 | 0.0011095 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_546-5_0_4_load_48 | 54 | 0.0053013 | 0.0013286 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_546-5_0_4_load_62 | 58 | 0.0066322 | 0.0016622 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_546-5_0_4_line_0 |  | 0 | 1 | 0.026859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_546-5_0_4_line_1 |  | 1 | 2 | 0.028527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_546-5_0_4_line_2 |  | 2 | 3 | 0.024573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_546-5_0_4_line_3 |  | 3 | 4 | 0.018919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_546-5_0_4_line_4 |  | 3 | 5 | 0.041616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_546-5_0_4_line_5 |  | 4 | 8 | 0.014115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_546-5_0_4_line_6 |  | 5 | 9 | 0.006409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_546-5_0_4_line_7 |  | 5 | 10 | 0.02144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_546-5_0_4_line_8 |  | 6 | 7 | 0.048897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_546-5_0_4_line_9 |  | 7 | 36 | 0.10296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_546-5_0_4_line_10 |  | 8 | 48 | 0.026315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_546-5_0_4_line_11 |  | 8 | 40 | 0.022177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_546-5_0_4_line_12 |  | 9 | 19 | 0.018056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_546-5_0_4_line_13 |  | 9 | 20 | 0.036919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_546-5_0_4_line_14 |  | 10 | 18 | 0.0032563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_546-5_0_4_line_15 |  | 11 | 12 | 0.0020735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_546-5_0_4_line_16 |  | 12 | 13 | 0.037741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_546-5_0_4_line_17 |  | 13 | 14 | 0.01342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_546-5_0_4_line_18 |  | 13 | 15 | 0.0016224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_546-5_0_4_line_19 |  | 14 | 16 | 0.014526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_546-5_0_4_line_20 |  | 14 | 17 | 0.0067386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_546-5_0_4_line_21 |  | 15 | 18 | 0.021115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_546-5_0_4_line_22 |  | 16 | 21 | 0.021569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_546-5_0_4_line_23 |  | 17 | 22 | 0.018562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_546-5_0_4_line_24 |  | 19 | 31 | 0.006867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_546-5_0_4_line_25 |  | 20 | 32 | 0.022329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_546-5_0_4_line_26 |  | 21 | 29 | 0.0067951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_546-5_0_4_line_27 |  | 22 | 23 | 0.03228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_546-5_0_4_line_28 |  | 22 | 24 | 0.014195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_546-5_0_4_line_29 |  | 23 | 25 | 0.028504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_546-5_0_4_line_30 |  | 24 | 26 | 0.019631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_546-5_0_4_line_31 |  | 25 | 27 | 0.030374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_546-5_0_4_line_32 |  | 26 | 28 | 0.011746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_546-5_0_4_line_33 |  | 27 | 30 | 0.0066808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_546-5_0_4_line_34 |  | 29 | 33 | 0.012857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_546-5_0_4_line_35 |  | 34 | 35 | 0.012987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_546-5_0_4_line_36 |  | 34 | 36 | 0.022599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_546-5_0_4_line_37 |  | 35 | 37 | 0.072424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_546-5_0_4_line_38 |  | 36 | 38 | 0.003995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_546-5_0_4_line_39 |  | 37 | 39 | 0.051995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_546-5_0_4_line_40 |  | 38 | 40 | 0.018767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_546-5_0_4_line_41 |  | 38 | 41 | 0.027255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_546-5_0_4_line_42 |  | 39 | 42 | 0.069774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_546-5_0_4_line_43 |  | 41 | 43 | 0.0016832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_546-5_0_4_line_44 |  | 42 | 51 | 0.026696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_546-5_0_4_line_45 |  | 43 | 44 | 0.014628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_546-5_0_4_line_46 |  | 44 | 45 | 0.012483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_546-5_0_4_line_47 |  | 45 | 46 | 0.055748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_546-5_0_4_line_48 |  | 45 | 47 | 0.026936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_546-5_0_4_line_49 |  | 46 | 50 | 0.028639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_546-5_0_4_line_50 |  | 48 | 49 | 0.015071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_546-5_0_4_line_51 |  | 51 | 52 | 0.0033935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_546-5_0_4_line_52 |  | 52 | 53 | 0.037177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_546-5_0_4_line_53 |  | 53 | 54 | 0.029522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_546-5_0_4_line_54 |  | 54 | 55 | 0.023555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_546-5_0_4_line_55 |  | 55 | 56 | 0.074049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_546-5_0_4_line_56 |  | 56 | 57 | 0.11605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_546-5_0_4_line_57 |  | 57 | 58 | 0.055345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_546-5_0_4_trafo_38 | 0.63 MVA 20/0.4 kV | 59 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2601685.9925 | 1205712.4115 | 2601662.7753 | 1205698.9072
1 | 2601662.7753 | 1205698.9072 | 2601658.5553 | 1205696.4526 | 2601638.8707 | 1205683.3526
2 | 2601618.4137 | 1205669.7386 | 2601638.8707 | 1205683.3526
3 | 2601618.4137 | 1205669.7386 | 2601608.1736 | 1205685.6471
4 | 2601585.2531 | 1205644.4719 | 2601610.901 | 1205664.0447 | 2601618.4137 | 1205669.7386
5 | 2601600.5339 | 1205697.5158 | 2601608.1736 | 1205685.6471
6 | 2601585.2531 | 1205644.4719 | 2601579.7933 | 1205641.0909
7 | 2601585.2531 | 1205644.4719 | 2601598.4135 | 1205627.5459
8 | 2601582.9461 | 1205804.4809 | 2601626.261 | 1205827.1696
9 | 2601575.4422 | 1205734.7965 | 2601543.8982 | 1205785.0716 | 2601582.9461 | 1205804.4809
10 | 2601600.5339 | 1205697.5158 | 2601623.3413 | 1205710.6423
11 | 2601600.5339 | 1205697.5158 | 2601588.2328 | 1205715.969
12 | 2601579.7933 | 1205641.0909 | 2601575.9971 | 1205645.1255 | 2601565.2567 | 1205651.6152
13 | 2601579.7933 | 1205641.0909 | 2601554.9811 | 1205613.7534
14 | 2601600.4123 | 1205624.9752 | 2601598.4135 | 1205627.5459
15 | 2601646.5964 | 1205630.4043 | 2601644.918 | 1205629.1867
16 | 2601614.3686 | 1205607.0256 | 2601644.918 | 1205629.1867
17 | 2601622.2735 | 1205596.1661 | 2601614.3686 | 1205607.0256
18 | 2601614.3686 | 1205607.0256 | 2601613.3728 | 1205608.3063
19 | 2601622.2735 | 1205596.1661 | 2601610.8999 | 1205587.1304
20 | 2601622.2735 | 1205596.1661 | 2601626.4922 | 1205590.9116
21 | 2601600.4123 | 1205624.9752 | 2601613.3728 | 1205608.3063
22 | 2601610.8999 | 1205587.1304 | 2601594.012 | 1205573.7137
23 | 2601638.1133 | 1205576.4373 | 2601626.4922 | 1205590.9116
24 | 2601565.2567 | 1205651.6152 | 2601566.7913 | 1205658.3081
25 | 2601554.9811 | 1205613.7534 | 2601539.9741 | 1205597.2189
26 | 2601594.012 | 1205573.7137 | 2601588.6915 | 1205569.4869
27 | 2601638.1133 | 1205576.4373 | 2601663.6174 | 1205596.2253
28 | 2601638.1133 | 1205576.4373 | 2601644.5421 | 1205567.9899 | 2601647.2191 | 1205565.6139
29 | 2601663.6174 | 1205596.2253 | 2601686.1382 | 1205613.6986
30 | 2601647.2191 | 1205565.6139 | 2601650.4149 | 1205562.7775 | 2601656.4398 | 1205557.8987 | 2601663.2704 | 1205554.5542 | 2601663.2704 | 1205554.5542
31 | 2601686.1382 | 1205613.6986 | 2601710.1357 | 1205632.3177
32 | 2601663.2704 | 1205554.5542 | 2601671.2718 | 1205553.2223 | 2601674.8827 | 1205553.6336
33 | 2601715.4141 | 1205636.413 | 2601710.1357 | 1205632.3177
34 | 2601588.6915 | 1205569.4869 | 2601578.6248 | 1205561.4893
35 | 2601559.0553 | 1205734.0758 | 2601551.5705 | 1205729.2875 | 2601549.7158 | 1205725.6295 | 2601549.7158 | 1205725.6295
36 | 2601575.4422 | 1205734.7965 | 2601567.0778 | 1205729.0913 | 2601562.3835 | 1205736.2051 | 2601559.0553 | 1205734.0758
37 | 2601477.4037 | 1205729.6587 | 2601549.7158 | 1205725.6295
38 | 2601575.4422 | 1205734.7965 | 2601577.8234 | 1205731.5842
39 | 2601476.4196 | 1205677.7523 | 2601478.2088 | 1205701.8103 | 2601477.4037 | 1205729.6587
40 | 2601577.8234 | 1205731.5842 | 2601588.2328 | 1205715.969
41 | 2601577.8234 | 1205731.5842 | 2601602.2509 | 1205743.6729
42 | 2601476.4196 | 1205677.7523 | 2601453.8923 | 1205678.592 | 2601447.4195 | 1205681.7144 | 2601440.353 | 1205686.4153 | 2601436.9141 | 1205692.1844 | 2601433.6733 | 1205696.1969 | 2601428.9655 | 1205696.3849 | 2601416.9088 | 1205687.5081
43 | 2601602.2509 | 1205743.6729 | 2601603.7595 | 1205744.4194
44 | 2601393.0954 | 1205677.3775 | 2601399.8631 | 1205682.3373 | 2601405.5282 | 1205686.1406 | 2601416.7914 | 1205687.4216 | 2601416.9088 | 1205687.5081
45 | 2601616.8698 | 1205750.9074 | 2601603.7595 | 1205744.4194
46 | 2601628.0575 | 1205756.444 | 2601616.8698 | 1205750.9074
47 | 2601628.0575 | 1205756.444 | 2601677.8346 | 1205781.8266
48 | 2601628.0575 | 1205756.444 | 2601615.5249 | 1205780.2865
49 | 2601677.8346 | 1205781.8266 | 2601670.6234 | 1205787.3277 | 2601667.4514 | 1205789.8838 | 2601665.4732 | 1205793.0072 | 2601660.1344 | 1205803.5284
50 | 2601623.3413 | 1205710.6423 | 2601636.4037 | 1205718.1602
51 | 2601393.0954 | 1205677.3775 | 2601394.8974 | 1205674.502
52 | 2601394.8974 | 1205674.502 | 2601412.5645 | 1205646.3094 | 2601414.6651 | 1205643.0163
53 | 2601414.6651 | 1205643.0163 | 2601430.5421 | 1205618.1267
54 | 2601443.2101 | 1205598.2679 | 2601430.5421 | 1205618.1267
55 | 2601443.2101 | 1205598.2679 | 2601452.6365 | 1205584.1513 | 2601467.6778 | 1205561.6425 | 2601472.9577 | 1205554.5954 | 2601483.2952 | 1205547.4717 | 2601489.4495 | 1205541.4032
56 | 2601489.4495 | 1205541.4032 | 2601486.9743 | 1205523.7819 | 2601498.0794 | 1205519.7157 | 2601578.9646 | 1205489.2523
57 | 2601578.9646 | 1205489.2523 | 2601592.4247 | 1205526.3537 | 2601594.8722 | 1205532.0463 | 2601602.4153 | 1205538.1516

## bus_geodata
| x | y | coords
0 | 2601685.9925 | 1205712.4115
1 | 2601662.7753 | 1205698.9072
2 | 2601638.8707 | 1205683.3526
3 | 2601618.4137 | 1205669.7386
4 | 2601608.1736 | 1205685.6471
5 | 2601585.2531 | 1205644.4719
6 | 2601626.261 | 1205827.1696
7 | 2601582.9461 | 1205804.4809
8 | 2601600.5339 | 1205697.5158
9 | 2601579.7933 | 1205641.0909
10 | 2601598.4135 | 1205627.5459
11 | 2601646.5964 | 1205630.4043
12 | 2601644.918 | 1205629.1867
13 | 2601614.3686 | 1205607.0256
14 | 2601622.2735 | 1205596.1661
15 | 2601613.3728 | 1205608.3063
16 | 2601610.8999 | 1205587.1304
17 | 2601626.4922 | 1205590.9116
18 | 2601600.4123 | 1205624.9752
19 | 2601565.2567 | 1205651.6152
20 | 2601554.9811 | 1205613.7534
21 | 2601594.012 | 1205573.7137
22 | 2601638.1133 | 1205576.4373
23 | 2601663.6174 | 1205596.2253
24 | 2601647.2191 | 1205565.6139
25 | 2601686.1382 | 1205613.6986
26 | 2601663.2704 | 1205554.5542
27 | 2601710.1357 | 1205632.3177
28 | 2601674.8827 | 1205553.6336
29 | 2601588.6915 | 1205569.4869
30 | 2601715.4141 | 1205636.413
31 | 2601566.7913 | 1205658.3081
32 | 2601539.9741 | 1205597.2189
33 | 2601578.6248 | 1205561.4893
34 | 2601559.0553 | 1205734.0758
35 | 2601549.7158 | 1205725.6295
36 | 2601575.4422 | 1205734.7965
37 | 2601477.4037 | 1205729.6587
38 | 2601577.8234 | 1205731.5842
39 | 2601476.4196 | 1205677.7523
40 | 2601588.2328 | 1205715.969
41 | 2601602.2509 | 1205743.6729
42 | 2601416.9088 | 1205687.5081
43 | 2601603.7595 | 1205744.4195
44 | 2601616.8698 | 1205750.9074
45 | 2601628.0575 | 1205756.444
46 | 2601677.8346 | 1205781.8266
47 | 2601615.5249 | 1205780.2865
48 | 2601623.3413 | 1205710.6423
49 | 2601636.4037 | 1205718.1602
50 | 2601660.1344 | 1205803.5284
51 | 2601393.0954 | 1205677.3775
52 | 2601394.8974 | 1205674.502
53 | 2601414.6651 | 1205643.0163
54 | 2601430.5421 | 1205618.1267
55 | 2601443.2101 | 1205598.2679
56 | 2601489.4495 | 1205541.4032
57 | 2601578.9646 | 1205489.2523
58 | 2601602.4153 | 1205538.1516
59 | 2601600.5339 | 1205697.5158

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1