## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5495-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5495-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5495-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5495-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5495-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5495-3_0_4_node_47 | 0.4 | n |  | TRUE
6 | bus_LV_5495-3_0_4_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_5495-3_0_4_node_48 | 0.4 | n |  | TRUE
8 | bus_LV_5495-3_0_4_node_34 | 0.4 | n |  | TRUE
9 | bus_LV_5495-3_0_4_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_5495-3_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_5495-3_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_5495-3_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_5495-3_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_5495-3_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_5495-3_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_5495-3_0_4_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_5495-3_0_4_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_5495-3_0_4_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_5495-3_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_5495-3_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_5495-3_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_5495-3_0_4_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_5495-3_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_5495-3_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_5495-3_0_4_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_5495-3_0_4_node_44 | 0.4 | n |  | TRUE
27 | bus_LV_5495-3_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_5495-3_0_4_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_5495-3_0_4_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_5495-3_0_4_node_46 | 0.4 | n |  | TRUE
31 | bus_LV_5495-3_0_4_node_43 | 0.4 | n |  | TRUE
32 | bus_LV_5495-3_0_4_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_5495-3_0_4_node_52 | 0.4 | n |  | TRUE
34 | bus_LV_5495-3_0_4_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_5495-3_0_4_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_5495-3_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_5495-3_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_5495-3_0_4_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_5495-3_0_4_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_5495-3_0_4_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_5495-3_0_4_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_5495-3_0_4_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_5495-3_0_4_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_5495-3_0_4_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_5495-3_0_4_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_5495-3_0_4_node_53 | 0.4 | n |  | TRUE
47 | bus_LV_5495-3_0_4_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_5495-3_0_4_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_5495-3_0_4_node_45 | 0.4 | n |  | TRUE
50 | bus_MV_315_1_node_59 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5495-3_0_4_load_0 | 0 | 0.016718 | 0.0041898 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5495-3_0_4_load_1 | 1 | 0.061225 | 0.015345 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5495-3_0_4_load_2 | 2 | 0.0022638 | 0.00056737 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5495-3_0_4_load_3 | 3 | 0.019491 | 0.004885 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5495-3_0_4_load_4 | 4 | 0.0045833 | 0.0011487 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5495-3_0_4_load_47 | 5 | 0.067048 | 0.016804 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5495-3_0_4_load_34 | 8 | 0.0038534 | 0.00096574 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5495-3_0_4_load_5 | 10 | 0.010906 | 0.0027333 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5495-3_0_4_load_6 | 11 | 0.0021392 | 0.00053613 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5495-3_0_4_load_7 | 12 | 0.029477 | 0.0073876 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5495-3_0_4_load_13 | 15 | 0.0021332 | 0.00053464 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5495-3_0_4_load_18 | 16 | 0.0030199 | 0.00075687 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5495-3_0_4_load_50 | 17 | 0.069404 | 0.017394 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5495-3_0_4_load_22 | 18 | 0.0038635 | 0.00096829 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5495-3_0_4_load_10 | 19 | 0.002768 | 0.00069373 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5495-3_0_4_load_11 | 20 | 0.0024071 | 0.00060328 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5495-3_0_4_load_16 | 21 | 0.00085316 | 0.00021382 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5495-3_0_4_load_49 | 22 | 0.080715 | 0.020229 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5495-3_0_4_load_17 | 24 | 0.00092677 | 0.00023227 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5495-3_0_4_load_15 | 27 | 0.006413 | 0.0016072 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5495-3_0_4_load_31 | 28 | 0.0013456 | 0.00033724 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5495-3_0_4_load_28 | 29 | 0.0048423 | 0.0012136 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5495-3_0_4_load_43 | 31 | 0.0011376 | 0.00028512 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5495-3_0_4_load_20 | 32 | 0.0012832 | 0.00032159 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5495-3_0_4_load_32 | 34 | 0.0057423 | 0.0014392 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5495-3_0_4_load_19 | 35 | 0.0019985 | 0.00050088 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5495-3_0_4_load_21 | 36 | 0.0014811 | 0.00037119 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5495-3_0_4_load_23 | 37 | 0.001898 | 0.00047568 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5495-3_0_4_load_40 | 38 | 0.00041112 | 0.00010304 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5495-3_0_4_load_24 | 39 | 0.0031039 | 0.00077791 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5495-3_0_4_load_27 | 41 | 0.0067815 | 0.0016996 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5495-3_0_4_load_39 | 42 | 0.0019107 | 0.00047887 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5495-3_0_4_load_37 | 43 | 0.0028275 | 0.00070863 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5495-3_0_4_load_42 | 44 | 0.0038231 | 0.00095815 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5495-3_0_4_load_38 | 45 | 0.0023207 | 0.00058161 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5495-3_0_4_load_53 | 46 | 0.0073319 | 0.0018375 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5495-3_0_4_load_35 | 47 | 0.0029313 | 0.00073464 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5495-3_0_4_load_36 | 48 | 0.0006729 | 0.00016864 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5495-3_0_4_load_45 | 49 | 0.0014469 | 0.00036262 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5495-3_0_4_line_0 |  | 0 | 1 | 0.0031971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5495-3_0_4_line_1 |  | 0 | 2 | 0.01445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5495-3_0_4_line_2 |  | 1 | 3 | 0.0182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5495-3_0_4_line_3 |  | 2 | 4 | 0.02519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5495-3_0_4_line_4 |  | 3 | 5 | 0.0083697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5495-3_0_4_line_5 |  | 4 | 6 | 0.063697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5495-3_0_4_line_6 |  | 5 | 7 | 0.016725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_5495-3_0_4_line_7 |  | 6 | 8 | 0.04627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5495-3_0_4_line_8 |  | 6 | 9 | 0.034452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5495-3_0_4_line_9 |  | 7 | 22 | 0.020668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5495-3_0_4_line_10 |  | 7 | 17 | 0.021507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_5495-3_0_4_line_11 |  | 8 | 33 | 0.018507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5495-3_0_4_line_12 |  | 9 | 34 | 0.018874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5495-3_0_4_line_13 |  | 10 | 11 | 0.017814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5495-3_0_4_line_14 |  | 10 | 12 | 0.02009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5495-3_0_4_line_15 |  | 11 | 13 | 0.022181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5495-3_0_4_line_16 |  | 12 | 14 | 0.018377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_5495-3_0_4_line_17 |  | 13 | 15 | 0.0088494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5495-3_0_4_line_18 |  | 14 | 16 | 0.016754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5495-3_0_4_line_19 |  | 14 | 17 | 0.010586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_5495-3_0_4_line_20 |  | 15 | 18 | 0.0081886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5495-3_0_4_line_21 |  | 16 | 21 | 0.010037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5495-3_0_4_line_22 |  | 18 | 32 | 0.0025022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5495-3_0_4_line_23 |  | 19 | 20 | 0.012103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5495-3_0_4_line_24 |  | 20 | 23 | 0.021114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5495-3_0_4_line_25 |  | 21 | 27 | 0.0058057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5495-3_0_4_line_26 |  | 23 | 24 | 0.010397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5495-3_0_4_line_27 |  | 23 | 25 | 0.018241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5495-3_0_4_line_28 |  | 23 | 26 | 0.056697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5495-3_0_4_line_29 |  | 24 | 27 | 0.0027831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5495-3_0_4_line_30 |  | 25 | 28 | 0.04612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5495-3_0_4_line_31 |  | 25 | 29 | 0.018365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5495-3_0_4_line_32 |  | 26 | 30 | 0.008114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5495-3_0_4_line_33 |  | 26 | 31 | 0.049658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5495-3_0_4_line_34 |  | 28 | 44 | 0.0027932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5495-3_0_4_line_35 |  | 30 | 41 | 0.026607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5495-3_0_4_line_36 |  | 31 | 49 | 0.0030678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5495-3_0_4_line_37 |  | 32 | 35 | 0.040722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5495-3_0_4_line_38 |  | 33 | 46 | 0.07893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5495-3_0_4_line_39 |  | 35 | 36 | 0.0065604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5495-3_0_4_line_40 |  | 36 | 37 | 0.014103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5495-3_0_4_line_41 |  | 37 | 38 | 0.024984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5495-3_0_4_line_42 |  | 39 | 40 | 0.047699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5495-3_0_4_line_43 |  | 40 | 41 | 0.032305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5495-3_0_4_line_44 |  | 42 | 43 | 0.030346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5495-3_0_4_line_45 |  | 43 | 47 | 0.02396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5495-3_0_4_line_46 |  | 44 | 45 | 0.0092242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5495-3_0_4_line_47 |  | 45 | 48 | 0.0096833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5495-3_0_4_line_48 |  | 47 | 48 | 0.016859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5495-3_0_4_trafo_7 | 0.63 MVA 20/0.4 kV | 50 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2530270.1915 | 1162989.3498 | 2530269.6244 | 1162986.2034
1 | 2530270.1915 | 1162989.3498 | 2530272.059 | 1162999.7104 | 2530273.0111 | 1163003.5152
2 | 2530269.6244 | 1162986.2034 | 2530266.3959 | 1162968.292
3 | 2530273.0111 | 1163003.5152 | 2530279.126 | 1163027.952
4 | 2530264.9112 | 1162960.055 | 2530266.3959 | 1162968.292
5 | 2530284.0256 | 1163090.7226 | 2530286.128 | 1163071.2316 | 2530286.1671 | 1163058.1127 | 2530282.2058 | 1163040.2598 | 2530279.126 | 1163027.952
6 | 2530262.6494 | 1162943.5103 | 2530263.0184 | 1162949.5539 | 2530264.9112 | 1162960.055
7 | 2530284.0256 | 1163090.7226 | 2530287.8284 | 1163091.6456 | 2530328.7864 | 1163102.4425
8 | 2530274.8641 | 1163119.1227 | 2530280.1172 | 1163119.5953 | 2530282.9022 | 1163104.7991 | 2530284.0256 | 1163090.7226
9 | 2530262.6494 | 1162943.5103 | 2530242.9229 | 1162946.1744 | 2530242.2265 | 1162945.8645
10 | 2530262.6494 | 1162943.5103 | 2530278.7301 | 1162936.2973 | 2530282.6057 | 1162936.5267
11 | 2530346.6819 | 1163107.16 | 2530328.7864 | 1163102.4425
12 | 2530274.8641 | 1163119.1227 | 2530269.404 | 1163118.6303 | 2530256.1924 | 1163120.819
13 | 2530320.6167 | 1162964.0443 | 2530321.6595 | 1162965.1261 | 2530336.4264 | 1162972.0542
14 | 2530320.6167 | 1162964.0443 | 2530306.6741 | 1162949.5802
15 | 2530356.5071 | 1162981.4753 | 2530336.4264 | 1162972.0542
16 | 2530293.1731 | 1162937.1522 | 2530300.9089 | 1162943.5994 | 2530306.6741 | 1162949.5802
17 | 2530356.5071 | 1162981.4753 | 2530359.7491 | 1162983.5834 | 2530363.405 | 1162986.9684
18 | 2530293.1731 | 1162937.1522 | 2530309.1272 | 1162932.037
19 | 2530293.1731 | 1162937.1522 | 2530282.6057 | 1162936.5267
20 | 2530363.405 | 1162986.9684 | 2530369.4134 | 1162992.5317
21 | 2530318.6845 | 1162928.9726 | 2530309.1272 | 1162932.037
22 | 2530371.2495 | 1162994.2317 | 2530369.4134 | 1162992.5317
23 | 2530351.4254 | 1162952.5119 | 2530349.181 | 1162944.3284 | 2530348.2149 | 1162940.8423
24 | 2530337.0612 | 1162924.5134 | 2530345.1671 | 1162929.8446 | 2530348.2149 | 1162940.8423
25 | 2530318.6845 | 1162928.9726 | 2530324.213 | 1162927.2001
26 | 2530337.0612 | 1162924.5134 | 2530329.6182 | 1162925.467 | 2530326.8632 | 1162926.3503
27 | 2530337.0612 | 1162924.5134 | 2530354.7739 | 1162919.9498
28 | 2530337.0612 | 1162924.5134 | 2530354.3061 | 1162889.5492 | 2530368.003 | 1162878.2506
29 | 2530326.8632 | 1162926.3503 | 2530324.213 | 1162927.2001
30 | 2530354.7739 | 1162919.9498 | 2530365.3767 | 1162941.072 | 2530387.7718 | 1162939.0513
31 | 2530354.7739 | 1162919.9498 | 2530372.3301 | 1162914.5591
32 | 2530368.003 | 1162878.2506 | 2530374.2321 | 1162873.031
33 | 2530368.003 | 1162878.2506 | 2530359.2786 | 1162874.4164 | 2530331.1542 | 1162868.3949 | 2530321.7632 | 1162874.7984
34 | 2530390.5537 | 1162938.8003 | 2530387.7718 | 1162939.0513
35 | 2530374.2321 | 1162873.031 | 2530394.7719 | 1162856.1177
36 | 2530319.2285 | 1162876.5268 | 2530321.7632 | 1162874.7984
37 | 2530371.2495 | 1162994.2317 | 2530391.399 | 1163012.8883 | 2530397.5827 | 1163016.3185 | 2530402.9948 | 1163019.3228
38 | 2530346.6819 | 1163107.16 | 2530349.1062 | 1163028.2875
39 | 2530409.0018 | 1163021.9202 | 2530404.8999 | 1163020.3804 | 2530402.9948 | 1163019.3228
40 | 2530422.3582 | 1163026.3703 | 2530418.3726 | 1163025.4381 | 2530409.0018 | 1163021.9202
41 | 2530422.3582 | 1163026.3703 | 2530433.951 | 1163029.0818 | 2530447.0277 | 1163029.2725
42 | 2530419.71 | 1162835.5827 | 2530426.05 | 1162882.858
43 | 2530419.71 | 1162835.5827 | 2530394.7719 | 1162856.1177
44 | 2530449.317 | 1162928.421 | 2530479.0818 | 1162922.5126
45 | 2530425.816 | 1162933.086 | 2530449.317 | 1162928.421
46 | 2530390.5537 | 1162938.8003 | 2530399.7406 | 1162937.9715
47 | 2530409.2793 | 1162936.3686 | 2530402.4243 | 1162937.7293 | 2530399.7406 | 1162937.9715
48 | 2530425.816 | 1162933.086 | 2530409.2793 | 1162936.3686

## bus_geodata
| x | y | coords
0 | 2530270.1915 | 1162989.3498
1 | 2530269.6244 | 1162986.2034
2 | 2530273.0111 | 1163003.5152
3 | 2530266.3959 | 1162968.292
4 | 2530279.126 | 1163027.952
5 | 2530264.9112 | 1162960.055
6 | 2530284.0256 | 1163090.7226
7 | 2530262.6494 | 1162943.5103
8 | 2530328.7864 | 1163102.4425
9 | 2530274.8641 | 1163119.1227
10 | 2530320.6167 | 1162964.0443
11 | 2530336.4264 | 1162972.0542
12 | 2530306.6741 | 1162949.5802
13 | 2530356.5071 | 1162981.4753
14 | 2530293.1731 | 1162937.1522
15 | 2530363.405 | 1162986.9684
16 | 2530309.1272 | 1162932.037
17 | 2530282.6057 | 1162936.5267
18 | 2530369.4134 | 1162992.5317
19 | 2530351.4254 | 1162952.5119
20 | 2530348.2149 | 1162940.8423
21 | 2530318.6845 | 1162928.9726
22 | 2530242.2265 | 1162945.8645
23 | 2530337.0612 | 1162924.5134
24 | 2530326.8632 | 1162926.3503
25 | 2530354.7739 | 1162919.9498
26 | 2530368.003 | 1162878.2506
27 | 2530324.213 | 1162927.2001
28 | 2530387.7718 | 1162939.0513
29 | 2530372.3301 | 1162914.5591
30 | 2530374.2321 | 1162873.031
31 | 2530321.7632 | 1162874.7984
32 | 2530371.2495 | 1162994.2317
33 | 2530346.6819 | 1163107.16
34 | 2530256.1924 | 1163120.819
35 | 2530402.9948 | 1163019.3228
36 | 2530409.0018 | 1163021.9202
37 | 2530422.3582 | 1163026.3703
38 | 2530447.0277 | 1163029.2725
39 | 2530426.05 | 1162882.858
40 | 2530419.71 | 1162835.5827
41 | 2530394.7719 | 1162856.1177
42 | 2530479.0818 | 1162922.5126
43 | 2530449.317 | 1162928.421
44 | 2530390.5537 | 1162938.8003
45 | 2530399.7406 | 1162937.9715
46 | 2530349.1062 | 1163028.2875
47 | 2530425.816 | 1162933.086
48 | 2530409.2793 | 1162936.3686
49 | 2530319.2285 | 1162876.5268
50 | 2530306.6741 | 1162949.5802

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1