## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_55-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_55-7_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_55-7_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_55-7_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_55-7_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_55-7_0_4_node_49 | 0.4 | n |  | TRUE
6 | bus_LV_55-7_0_4_node_38 | 0.4 | n |  | TRUE
7 | bus_LV_55-7_0_4_node_48 | 0.4 | n |  | TRUE
8 | bus_LV_55-7_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_55-7_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_55-7_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_55-7_0_4_node_37 | 0.4 | n |  | TRUE
12 | bus_LV_55-7_0_4_node_36 | 0.4 | n |  | TRUE
13 | bus_LV_55-7_0_4_node_34 | 0.4 | n |  | TRUE
14 | bus_LV_55-7_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_55-7_0_4_node_46 | 0.4 | n |  | TRUE
16 | bus_LV_55-7_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_55-7_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_55-7_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_55-7_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_55-7_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_55-7_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_55-7_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_55-7_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_55-7_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_55-7_0_4_node_77 | 0.4 | n |  | TRUE
26 | bus_LV_55-7_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_55-7_0_4_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_55-7_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_55-7_0_4_node_54 | 0.4 | n |  | TRUE
30 | bus_LV_55-7_0_4_node_76 | 0.4 | n |  | TRUE
31 | bus_LV_55-7_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_55-7_0_4_node_53 | 0.4 | n |  | TRUE
33 | bus_LV_55-7_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_55-7_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_55-7_0_4_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_55-7_0_4_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_55-7_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_55-7_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_55-7_0_4_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_55-7_0_4_node_67 | 0.4 | n |  | TRUE
41 | bus_LV_55-7_0_4_node_68 | 0.4 | n |  | TRUE
42 | bus_LV_55-7_0_4_node_66 | 0.4 | n |  | TRUE
43 | bus_LV_55-7_0_4_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_55-7_0_4_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_55-7_0_4_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_55-7_0_4_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_55-7_0_4_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_55-7_0_4_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_55-7_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_55-7_0_4_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_55-7_0_4_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_55-7_0_4_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_55-7_0_4_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_55-7_0_4_node_69 | 0.4 | n |  | TRUE
55 | bus_LV_55-7_0_4_node_44 | 0.4 | n |  | TRUE
56 | bus_LV_55-7_0_4_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_55-7_0_4_node_70 | 0.4 | n |  | TRUE
58 | bus_LV_55-7_0_4_node_75 | 0.4 | n |  | TRUE
59 | bus_LV_55-7_0_4_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_55-7_0_4_node_64 | 0.4 | n |  | TRUE
61 | bus_LV_55-7_0_4_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_55-7_0_4_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_55-7_0_4_node_55 | 0.4 | n |  | TRUE
64 | bus_LV_55-7_0_4_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_55-7_0_4_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_55-7_0_4_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_55-7_0_4_node_59 | 0.4 | n |  | TRUE
68 | bus_LV_55-7_0_4_node_62 | 0.4 | n |  | TRUE
69 | bus_LV_55-7_0_4_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_55-7_0_4_node_74 | 0.4 | n |  | TRUE
71 | bus_LV_55-7_0_4_node_72 | 0.4 | n |  | TRUE
72 | bus_LV_55-7_0_4_node_71 | 0.4 | n |  | TRUE
73 | bus_LV_55-7_0_4_node_65 | 0.4 | n |  | TRUE
74 | bus_LV_55-7_0_4_node_73 | 0.4 | n |  | TRUE
75 | bus_MV_383_0_node_31 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_55-7_0_4_load_0 | 0 | 0.0017471 | 0.00043787 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_55-7_0_4_load_1 | 1 | 0.0052229 | 0.001309 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_55-7_0_4_load_4 | 4 | 0.0030662 | 0.00076847 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_55-7_0_4_load_49 | 5 | 0.013949 | 0.003496 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_55-7_0_4_load_38 | 6 | 0.017533 | 0.0043943 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_55-7_0_4_load_48 | 7 | 0.01085 | 0.0027193 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_55-7_0_4_load_6 | 8 | 0.0046661 | 0.0011694 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_55-7_0_4_load_5 | 9 | 0.0016621 | 0.00041656 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_55-7_0_4_load_37 | 11 | 0.055099 | 0.013809 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_55-7_0_4_load_36 | 12 | 0.0073379 | 0.0018391 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_55-7_0_4_load_34 | 13 | 0.011189 | 0.0028042 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_55-7_0_4_load_7 | 14 | 0.0013794 | 0.00034572 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_55-7_0_4_load_46 | 15 | 0.00417 | 0.0010451 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_55-7_0_4_load_10 | 17 | 0.0022451 | 0.00056267 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_55-7_0_4_load_11 | 18 | 0.0014651 | 0.0003672 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_55-7_0_4_load_12 | 19 | 0.0030519 | 0.00076487 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_55-7_0_4_load_13 | 20 | 0.005055 | 0.0012669 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_55-7_0_4_load_15 | 22 | 0.0028844 | 0.0007229 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_55-7_0_4_load_16 | 23 | 0.015501 | 0.0038848 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_55-7_0_4_load_17 | 24 | 0.012179 | 0.0030524 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_55-7_0_4_load_77 | 25 | 0.0018018 | 0.00045158 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_55-7_0_4_load_19 | 26 | 0.0040425 | 0.0010131 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_55-7_0_4_load_18 | 28 | 0.011107 | 0.0027836 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_55-7_0_4_load_54 | 29 | 0.0028404 | 0.00071187 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_55-7_0_4_load_76 | 30 | 0.0022436 | 0.0005623 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_55-7_0_4_load_20 | 31 | 0.012407 | 0.0031096 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_55-7_0_4_load_53 | 32 | 0.0082986 | 0.0020798 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_55-7_0_4_load_28 | 33 | 0.0042324 | 0.0010607 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_55-7_0_4_load_26 | 34 | 0.0036074 | 0.00090411 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_55-7_0_4_load_21 | 35 | 0.0062812 | 0.0015742 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_55-7_0_4_load_22 | 36 | 0.0048178 | 0.0012075 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_55-7_0_4_load_23 | 37 | 0.0043237 | 0.0010836 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_55-7_0_4_load_24 | 38 | 0.0039366 | 0.00098661 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_55-7_0_4_load_25 | 39 | 0.0017247 | 0.00043226 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_55-7_0_4_load_67 | 40 | 0.0038131 | 0.00095564 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_55-7_0_4_load_68 | 41 | 0.0018728 | 0.00046936 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_55-7_0_4_load_66 | 42 | 0.0041569 | 0.0010418 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_55-7_0_4_load_29 | 43 | 0.0038152 | 0.00095617 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_55-7_0_4_load_27 | 44 | 0.0032157 | 0.00080594 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_55-7_0_4_load_30 | 45 | 0.0089997 | 0.0022555 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_55-7_0_4_load_31 | 46 | 0.0035498 | 0.00088966 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_55-7_0_4_load_33 | 47 | 0.019338 | 0.0048465 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_55-7_0_4_load_39 | 48 | 0.011905 | 0.0029837 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_55-7_0_4_load_47 | 50 | 0.0042305 | 0.0010603 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_55-7_0_4_load_41 | 51 | 0.010887 | 0.0027285 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_55-7_0_4_load_42 | 52 | 0.018331 | 0.0045943 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_55-7_0_4_load_69 | 54 | 0.0045856 | 0.0011492 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_55-7_0_4_load_44 | 55 | 0.0052482 | 0.0013153 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_55-7_0_4_load_45 | 56 | 0.0048835 | 0.0012239 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_55-7_0_4_load_70 | 57 | 0.004924 | 0.0012341 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_55-7_0_4_load_75 | 58 | 0.0037433 | 0.00093817 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_55-7_0_4_load_51 | 59 | 0.0020927 | 0.00052447 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_55-7_0_4_load_64 | 60 | 0.0031364 | 0.00078607 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_55-7_0_4_load_50 | 61 | 0.022994 | 0.0057628 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_55-7_0_4_load_52 | 62 | 0.0016805 | 0.00042118 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_55-7_0_4_load_55 | 63 | 0.006849 | 0.0017165 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_55-7_0_4_load_56 | 64 | 0.0037445 | 0.00093846 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_55-7_0_4_load_58 | 66 | 0.0055056 | 0.0013798 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_55-7_0_4_load_59 | 67 | 0.005694 | 0.001427 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_55-7_0_4_load_62 | 68 | 0.0037318 | 0.00093528 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_55-7_0_4_load_74 | 70 | 0.0036237 | 0.00090819 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_55-7_0_4_load_71 | 72 | 0.0057123 | 0.0014316 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_55-7_0_4_load_65 | 73 | 0.0023488 | 0.00058866 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_55-7_0_4_load_73 | 74 | 0.0043291 | 0.001085 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 59 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_55-7_0_4_line_0 |  | 0 | 1 | 0.010121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_55-7_0_4_line_1 |  | 0 | 2 | 0.020896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_55-7_0_4_line_2 |  | 1 | 3 | 0.0044085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_55-7_0_4_line_3 |  | 2 | 4 | 0.043505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_55-7_0_4_line_4 |  | 3 | 8 | 0.077694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_55-7_0_4_line_5 |  | 3 | 9 | 0.019994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_55-7_0_4_line_6 |  | 5 | 6 | 0.0050122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_55-7_0_4_line_7 |  | 5 | 7 | 0.020334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_55-7_0_4_line_8 |  | 6 | 11 | 0.014992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_55-7_0_4_line_9 |  | 7 | 50 | 0.0061083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_55-7_0_4_line_10 |  | 8 | 10 | 0.029221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_55-7_0_4_line_11 |  | 10 | 13 | 0.12127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_55-7_0_4_line_12 |  | 10 | 14 | 0.032286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_55-7_0_4_line_13 |  | 11 | 12 | 0.02025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_55-7_0_4_line_14 |  | 12 | 27 | 0.010212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_55-7_0_4_line_15 |  | 13 | 15 | 0.0063158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_55-7_0_4_line_16 |  | 14 | 16 | 0.0027779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_55-7_0_4_line_17 |  | 15 | 50 | 0.0034182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_55-7_0_4_line_18 |  | 16 | 17 | 0.013398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_55-7_0_4_line_19 |  | 17 | 18 | 0.019126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_55-7_0_4_line_20 |  | 19 | 20 | 0.01081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_55-7_0_4_line_21 |  | 19 | 21 | 0.026318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_55-7_0_4_line_22 |  | 20 | 22 | 0.0076016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_55-7_0_4_line_23 |  | 21 | 23 | 0.028121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_55-7_0_4_line_24 |  | 21 | 24 | 0.017859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_55-7_0_4_line_25 |  | 22 | 25 | 0.0076439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_55-7_0_4_line_26 |  | 23 | 26 | 0.03602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_55-7_0_4_line_27 |  | 24 | 27 | 0.019281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_55-7_0_4_line_28 |  | 25 | 30 | 0.0082981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_55-7_0_4_line_29 |  | 26 | 31 | 0.010934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_55-7_0_4_line_30 |  | 28 | 29 | 0.0094694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_55-7_0_4_line_31 |  | 29 | 32 | 0.0071315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_55-7_0_4_line_32 |  | 30 | 73 | 0.0094523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_55-7_0_4_line_33 |  | 31 | 33 | 0.010961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_55-7_0_4_line_34 |  | 32 | 62 | 0.00015836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_55-7_0_4_line_35 |  | 33 | 34 | 0.0014737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_55-7_0_4_line_36 |  | 34 | 44 | 0.00421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_55-7_0_4_line_37 |  | 35 | 36 | 0.0026831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_55-7_0_4_line_38 |  | 35 | 37 | 0.0048247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_55-7_0_4_line_39 |  | 36 | 38 | 0.0067462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_55-7_0_4_line_40 |  | 37 | 39 | 0.0046034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_55-7_0_4_line_41 |  | 38 | 40 | 0.005854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_55-7_0_4_line_42 |  | 39 | 41 | 0.002739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_55-7_0_4_line_43 |  | 40 | 42 | 0.0059554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_55-7_0_4_line_44 |  | 41 | 43 | 0.0042941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_55-7_0_4_line_45 |  | 43 | 44 | 0.0053322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_55-7_0_4_line_46 |  | 45 | 46 | 0.010606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_55-7_0_4_line_47 |  | 46 | 47 | 0.013052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_55-7_0_4_line_48 |  | 47 | 48 | 0.014368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_55-7_0_4_line_49 |  | 48 | 49 | 0.0020707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_55-7_0_4_line_50 |  | 49 | 51 | 0.0099208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_55-7_0_4_line_51 |  | 49 | 52 | 0.0045792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_55-7_0_4_line_52 |  | 51 | 53 | 0.0049549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_55-7_0_4_line_53 |  | 52 | 54 | 0.0057447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_55-7_0_4_line_54 |  | 53 | 55 | 0.0082897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_55-7_0_4_line_55 |  | 53 | 56 | 0.015899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_55-7_0_4_line_56 |  | 54 | 57 | 0.0060566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_55-7_0_4_line_57 |  | 55 | 58 | 0.0018007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_55-7_0_4_line_58 |  | 56 | 59 | 0.0093629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_55-7_0_4_line_59 |  | 57 | 74 | 0.0084303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_55-7_0_4_line_60 |  | 58 | 60 | 0.0072809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_55-7_0_4_line_61 |  | 59 | 61 | 0.0036884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_55-7_0_4_line_62 |  | 60 | 69 | 0.0093938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_55-7_0_4_line_63 |  | 61 | 62 | 0.0051401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_55-7_0_4_line_64 |  | 63 | 64 | 0.00057989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_55-7_0_4_line_65 |  | 63 | 65 | 0.010902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_55-7_0_4_line_66 |  | 64 | 66 | 0.0079936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_55-7_0_4_line_67 |  | 65 | 67 | 0.0031176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_55-7_0_4_line_68 |  | 66 | 68 | 0.0071897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_55-7_0_4_line_69 |  | 68 | 69 | 0.010007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_55-7_0_4_line_70 |  | 69 | 73 | 0.017703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_55-7_0_4_line_71 |  | 70 | 71 | 0.012325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_55-7_0_4_line_72 |  | 71 | 72 | 0.027957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_55-7_0_4_line_73 |  | 71 | 74 | 0.0061535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_55-7_0_4_trafo_51 | 0.63 MVA 20/0.4 kV | 75 | 59 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2681621.5311 | 1269804.9796 | 2681623.692 | 1269814.8672
1 | 2681616.0769 | 1269784.9173 | 2681617.9665 | 1269788.6687 | 2681621.5311 | 1269804.9796
2 | 2681624.6333 | 1269819.1741 | 2681623.692 | 1269814.8672
3 | 2681616.0769 | 1269784.9173 | 2681611.5737 | 1269792.2277 | 2681607.0106 | 1269798.97 | 2681600.1902 | 1269805.7034 | 2681593.504 | 1269810.3482 | 2681585.6672 | 1269814.8785
4 | 2681624.6333 | 1269819.1741 | 2681630.9097 | 1269833.2832 | 2681635.8724 | 1269835.7315 | 2681651.3131 | 1269836.312 | 2681662.1776 | 1269835.3391 | 2681668.6683 | 1269832.8602 | 2681671.7699 | 1269828.9555 | 2681676.2148 | 1269817.1631 | 2681680.6379 | 1269815.6452 | 2681681.7469 | 1269815.9311
5 | 2681624.6333 | 1269819.1741 | 2681604.7464 | 1269821.242
6 | 2681682.3676 | 1269970.7195 | 2681677.8204 | 1269972.8278
7 | 2681701.2608 | 1269963.2666 | 2681689.8048 | 1269967.2712 | 2681682.3676 | 1269970.7195
8 | 2681677.8204 | 1269972.8278 | 2681673.6659 | 1269974.754 | 2681664.3767 | 1269979.4582
9 | 2681707.0269 | 1269961.251 | 2681701.2608 | 1269963.2666
10 | 2681694.8275 | 1269838.6709 | 2681693.087 | 1269826.3259 | 2681690.73 | 1269819.9215 | 2681685.8342 | 1269816.9848 | 2681681.7469 | 1269815.9311
11 | 2681716.2157 | 1269958.0389 | 2681694.8275 | 1269838.6709
12 | 2681694.8275 | 1269838.6709 | 2681726.5348 | 1269832.5875
13 | 2681646.5222 | 1269989.008 | 2681658.7678 | 1269982.2986 | 2681664.3767 | 1269979.4582
14 | 2681638.1425 | 1269994.8014 | 2681643.7625 | 1269990.5201 | 2681646.5222 | 1269989.008
15 | 2681716.2157 | 1269958.0389 | 2681710.2537 | 1269960.123
16 | 2681729.2629 | 1269832.0641 | 2681726.5348 | 1269832.5875
17 | 2681710.2537 | 1269960.123 | 2681707.0269 | 1269961.251
18 | 2681729.2629 | 1269832.0641 | 2681726.1089 | 1269820.1776 | 2681725.6054 | 1269819.1992
19 | 2681725.6054 | 1269819.1992 | 2681723.1924 | 1269814.5105 | 2681712.315 | 1269805.9323
20 | 2681692.8779 | 1270021.7392 | 2681690.1105 | 1270022.3973 | 2681682.6527 | 1270022.9947 | 2681682.1694 | 1270022.9917
21 | 2681656.3563 | 1270027.1679 | 2681666.6907 | 1270024.2306 | 2681673.0321 | 1270023.2842 | 2681675.2867 | 1270022.9484 | 2681682.1694 | 1270022.9917
22 | 2681700.2733 | 1270019.9805 | 2681692.8779 | 1270021.7392
23 | 2681656.3563 | 1270027.1679 | 2681650.0796 | 1270034.3202 | 2681649.5599 | 1270037.0708 | 2681650.3154 | 1270040.6619 | 2681656.2478 | 1270051.2487
24 | 2681656.3563 | 1270027.1679 | 2681647.5981 | 1270011.6043
25 | 2681707.5992 | 1270017.8049 | 2681701.2461 | 1270019.7492 | 2681700.2733 | 1270019.9805
26 | 2681685.9477 | 1270056.9154 | 2681667.8529 | 1270062.0659 | 2681663.9982 | 1270061.6678 | 2681661.1543 | 1270060.005 | 2681656.2478 | 1270051.2487
27 | 2681638.1425 | 1269994.8014 | 2681647.5981 | 1270011.6043
28 | 2681715.534 | 1270015.3765 | 2681707.5992 | 1270017.8049
29 | 2681696.4476 | 1270053.8643 | 2681688.0459 | 1270056.3182 | 2681685.9477 | 1270056.9154
30 | 2681683.8427 | 1270002.936 | 2681687.1925 | 1270001.0732 | 2681692.2555 | 1269998.596
31 | 2681698.6614 | 1269995.4618 | 2681692.2555 | 1269998.596
32 | 2681724.5725 | 1270012.6103 | 2681715.534 | 1270015.3765
33 | 2681706.969 | 1270050.7913 | 2681696.4476 | 1270053.8643
34 | 2681698.6614 | 1269995.4618 | 2681698.8036 | 1269995.3922
35 | 2681708.3836 | 1270050.3781 | 2681706.969 | 1270050.7913
36 | 2681708.3836 | 1270050.3781 | 2681712.4247 | 1270049.1978
37 | 2681733.3441 | 1270043.0878 | 2681735.9196 | 1270042.3356
38 | 2681733.3441 | 1270043.0878 | 2681728.7129 | 1270044.4405
39 | 2681742.3952 | 1270040.4443 | 2681735.9196 | 1270042.3356
40 | 2681728.7129 | 1270044.4405 | 2681724.294 | 1270045.7311
41 | 2681748.0145 | 1270038.803 | 2681742.3952 | 1270040.4443
42 | 2681724.294 | 1270045.7311 | 2681721.6649 | 1270046.499
43 | 2681753.731 | 1270037.1334 | 2681748.0145 | 1270038.803
44 | 2681721.6649 | 1270046.499 | 2681717.543 | 1270047.7029
45 | 2681717.543 | 1270047.7029 | 2681712.4247 | 1270049.1978
46 | 2681776.3934 | 1269954.0805 | 2681768.4663 | 1269961.1273
47 | 2681768.4663 | 1269961.1273 | 2681767.7096 | 1269961.8 | 2681758.5831 | 1269969.6517
48 | 2681758.5831 | 1269969.6517 | 2681756.2101 | 1269971.6932 | 2681746.4681 | 1269977.2955
49 | 2681744.673 | 1269978.3278 | 2681746.4681 | 1269977.2955
50 | 2681744.673 | 1269978.3278 | 2681736.3687 | 1269980.826 | 2681735.1993 | 1269981.2642
51 | 2681744.673 | 1269978.3278 | 2681746.961 | 1269978.8376 | 2681749.1949 | 1269978.7637
52 | 2681730.5595 | 1269983.0029 | 2681735.1993 | 1269981.2642
53 | 2681749.1949 | 1269978.7637 | 2681749.5658 | 1269978.7514 | 2681754.4728 | 1269976.5612
54 | 2681730.5595 | 1269983.0029 | 2681733.9483 | 1269990.5683
55 | 2681730.5595 | 1269983.0029 | 2681715.7371 | 1269988.7527
56 | 2681760.0221 | 1269974.1361 | 2681758.6517 | 1269974.6961 | 2681754.4728 | 1269976.5612
57 | 2681734.6844 | 1269992.2117 | 2681733.9483 | 1269990.5683
58 | 2681715.7371 | 1269988.7527 | 2681707.008 | 1269992.1387
59 | 2681767.8259 | 1269970.947 | 2681760.0221 | 1269974.1361
60 | 2681734.6844 | 1269992.2117 | 2681737.6608 | 1269998.8565
61 | 2681703.5692 | 1269993.4727 | 2681707.008 | 1269992.1387
62 | 2681741.501 | 1270007.4294 | 2681737.6608 | 1269998.8565
63 | 2681703.5692 | 1269993.4727 | 2681699.5036 | 1269995.0498 | 2681698.8036 | 1269995.3922
64 | 2681766.4902 | 1270001.1705 | 2681765.9365 | 1270001.3426
65 | 2681776.901 | 1269997.9339 | 2681766.4902 | 1270001.1705
66 | 2681758.2321 | 1270003.4559 | 2681762.0736 | 1270002.5435 | 2681765.9365 | 1270001.3426
67 | 2681776.901 | 1269997.9339 | 2681775.9564 | 1269994.9629
68 | 2681758.2321 | 1270003.4559 | 2681751.2369 | 1270005.1172
69 | 2681741.501 | 1270007.4294 | 2681751.2369 | 1270005.1172
70 | 2681741.501 | 1270007.4294 | 2681724.5725 | 1270012.6103
71 | 2681773.5221 | 1269968.6192 | 2681777.5982 | 1269980.2502
72 | 2681773.5221 | 1269968.6192 | 2681792.8039 | 1269961.8696 | 2681795.0821 | 1269969.045
73 | 2681773.5221 | 1269968.6192 | 2681767.8259 | 1269970.947

## bus_geodata
| x | y | coords
0 | 2681621.5311 | 1269804.9796
1 | 2681623.692 | 1269814.8672
2 | 2681616.0769 | 1269784.9173
3 | 2681624.6333 | 1269819.1741
4 | 2681585.6672 | 1269814.8785
5 | 2681682.3676 | 1269970.7195
6 | 2681677.8204 | 1269972.8278
7 | 2681701.2608 | 1269963.2666
8 | 2681681.7469 | 1269815.9311
9 | 2681604.7464 | 1269821.242
10 | 2681694.8275 | 1269838.6709
11 | 2681664.3767 | 1269979.4582
12 | 2681646.5222 | 1269989.008
13 | 2681716.2157 | 1269958.0389
14 | 2681726.5348 | 1269832.5875
15 | 2681710.2537 | 1269960.123
16 | 2681729.2629 | 1269832.0641
17 | 2681725.6054 | 1269819.1992
18 | 2681712.315 | 1269805.9323
19 | 2681682.1694 | 1270022.9917
20 | 2681692.8779 | 1270021.7392
21 | 2681656.3563 | 1270027.1679
22 | 2681700.2733 | 1270019.9805
23 | 2681656.2478 | 1270051.2487
24 | 2681647.5981 | 1270011.6043
25 | 2681707.5992 | 1270017.8049
26 | 2681685.9477 | 1270056.9154
27 | 2681638.1425 | 1269994.8014
28 | 2681683.8427 | 1270002.936
29 | 2681692.2555 | 1269998.596
30 | 2681715.534 | 1270015.3765
31 | 2681696.4476 | 1270053.8643
32 | 2681698.6614 | 1269995.4618
33 | 2681706.969 | 1270050.7913
34 | 2681708.3836 | 1270050.3781
35 | 2681733.3441 | 1270043.0878
36 | 2681735.9196 | 1270042.3356
37 | 2681728.7129 | 1270044.4405
38 | 2681742.3952 | 1270040.4443
39 | 2681724.294 | 1270045.7311
40 | 2681748.0145 | 1270038.803
41 | 2681721.6649 | 1270046.499
42 | 2681753.731 | 1270037.1334
43 | 2681717.543 | 1270047.7029
44 | 2681712.4247 | 1270049.1978
45 | 2681776.3934 | 1269954.0805
46 | 2681768.4663 | 1269961.1273
47 | 2681758.5831 | 1269969.6517
48 | 2681746.4681 | 1269977.2955
49 | 2681744.673 | 1269978.3278
50 | 2681707.0269 | 1269961.251
51 | 2681735.1993 | 1269981.2642
52 | 2681749.1949 | 1269978.7637
53 | 2681730.5595 | 1269983.0029
54 | 2681754.4728 | 1269976.5612
55 | 2681733.9483 | 1269990.5683
56 | 2681715.7371 | 1269988.7527
57 | 2681760.0221 | 1269974.1361
58 | 2681734.6844 | 1269992.2117
59 | 2681707.008 | 1269992.1387
60 | 2681737.6608 | 1269998.8565
61 | 2681703.5692 | 1269993.4727
62 | 2681698.8036 | 1269995.3922
63 | 2681766.4902 | 1270001.1705
64 | 2681765.9365 | 1270001.3426
65 | 2681776.901 | 1269997.9339
66 | 2681758.2321 | 1270003.4559
67 | 2681775.9564 | 1269994.9629
68 | 2681751.2369 | 1270005.1172
69 | 2681741.501 | 1270007.4294
70 | 2681777.5982 | 1269980.2502
71 | 2681773.5221 | 1269968.6192
72 | 2681795.0821 | 1269969.045
73 | 2681724.5725 | 1270012.6103
74 | 2681767.8259 | 1269970.947
75 | 2681730.5595 | 1269983.0029

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1