## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5514-1_1_5_node_26 | 0.4 | n |  | TRUE
1 | bus_LV_5514-1_1_5_node_27 | 0.4 | n |  | TRUE
2 | bus_LV_5514-1_1_5_node_28 | 0.4 | n |  | TRUE
3 | bus_LV_5514-1_1_5_node_29 | 0.4 | n |  | TRUE
4 | bus_LV_5514-1_1_5_node_30 | 0.4 | n |  | TRUE
5 | bus_LV_5514-1_1_5_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_5514-1_1_5_node_32 | 0.4 | n |  | TRUE
7 | bus_LV_5514-1_1_5_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_5514-1_1_5_node_34 | 0.4 | n |  | TRUE
9 | bus_LV_5514-1_1_5_node_82 | 0.4 | n |  | TRUE
10 | bus_LV_5514-1_1_5_node_83 | 0.4 | n |  | TRUE
11 | bus_LV_5514-1_1_5_node_50 | 0.4 | n |  | TRUE
12 | bus_LV_5514-1_1_5_node_68 | 0.4 | n |  | TRUE
13 | bus_LV_5514-1_1_5_node_47 | 0.4 | n |  | TRUE
14 | bus_LV_5514-1_1_5_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_5514-1_1_5_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_5514-1_1_5_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_5514-1_1_5_node_39 | 0.4 | n |  | TRUE
18 | bus_LV_5514-1_1_5_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_5514-1_1_5_node_41 | 0.4 | n |  | TRUE
20 | bus_LV_5514-1_1_5_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_5514-1_1_5_node_45 | 0.4 | n |  | TRUE
22 | bus_LV_5514-1_1_5_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_5514-1_1_5_node_97 | 0.4 | n |  | TRUE
24 | bus_LV_5514-1_1_5_node_98 | 0.4 | n |  | TRUE
25 | bus_LV_5514-1_1_5_node_48 | 0.4 | n |  | TRUE
26 | bus_LV_5514-1_1_5_node_49 | 0.4 | n |  | TRUE
27 | bus_LV_5514-1_1_5_node_51 | 0.4 | n |  | TRUE
28 | bus_LV_5514-1_1_5_node_52 | 0.4 | n |  | TRUE
29 | bus_LV_5514-1_1_5_node_53 | 0.4 | n |  | TRUE
30 | bus_LV_5514-1_1_5_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_5514-1_1_5_node_55 | 0.4 | n |  | TRUE
32 | bus_LV_5514-1_1_5_node_56 | 0.4 | n |  | TRUE
33 | bus_LV_5514-1_1_5_node_57 | 0.4 | n |  | TRUE
34 | bus_LV_5514-1_1_5_node_58 | 0.4 | n |  | TRUE
35 | bus_LV_5514-1_1_5_node_59 | 0.4 | n |  | TRUE
36 | bus_LV_5514-1_1_5_node_60 | 0.4 | n |  | TRUE
37 | bus_LV_5514-1_1_5_node_62 | 0.4 | n |  | TRUE
38 | bus_LV_5514-1_1_5_node_100 | 0.4 | n |  | TRUE
39 | bus_LV_5514-1_1_5_node_66 | 0.4 | n |  | TRUE
40 | bus_LV_5514-1_1_5_node_61 | 0.4 | n |  | TRUE
41 | bus_LV_5514-1_1_5_node_103 | 0.4 | n |  | TRUE
42 | bus_LV_5514-1_1_5_node_63 | 0.4 | n |  | TRUE
43 | bus_LV_5514-1_1_5_node_99 | 0.4 | n |  | TRUE
44 | bus_LV_5514-1_1_5_node_101 | 0.4 | n |  | TRUE
45 | bus_LV_5514-1_1_5_node_102 | 0.4 | n |  | TRUE
46 | bus_LV_5514-1_1_5_node_104 | 0.4 | n |  | TRUE
47 | bus_LV_5514-1_1_5_node_64 | 0.4 | n |  | TRUE
48 | bus_LV_5514-1_1_5_node_65 | 0.4 | n |  | TRUE
49 | bus_LV_5514-1_1_5_node_84 | 0.4 | n |  | TRUE
50 | bus_LV_5514-1_1_5_node_69 | 0.4 | n |  | TRUE
51 | bus_LV_5514-1_1_5_node_75 | 0.4 | n |  | TRUE
52 | bus_LV_5514-1_1_5_node_85 | 0.4 | n |  | TRUE
53 | bus_LV_5514-1_1_5_node_72 | 0.4 | n |  | TRUE
54 | bus_LV_5514-1_1_5_node_70 | 0.4 | n |  | TRUE
55 | bus_LV_5514-1_1_5_node_71 | 0.4 | n |  | TRUE
56 | bus_LV_5514-1_1_5_node_73 | 0.4 | n |  | TRUE
57 | bus_LV_5514-1_1_5_node_74 | 0.4 | n |  | TRUE
58 | bus_LV_5514-1_1_5_node_76 | 0.4 | n |  | TRUE
59 | bus_LV_5514-1_1_5_node_77 | 0.4 | n |  | TRUE
60 | bus_LV_5514-1_1_5_node_89 | 0.4 | n |  | TRUE
61 | bus_LV_5514-1_1_5_node_78 | 0.4 | n |  | TRUE
62 | bus_LV_5514-1_1_5_node_79 | 0.4 | n |  | TRUE
63 | bus_LV_5514-1_1_5_node_80 | 0.4 | n |  | TRUE
64 | bus_LV_5514-1_1_5_node_81 | 0.4 | n |  | TRUE
65 | bus_LV_5514-1_1_5_node_133 | 0.4 | n |  | TRUE
66 | bus_LV_5514-1_1_5_node_131 | 0.4 | n |  | TRUE
67 | bus_LV_5514-1_1_5_node_86 | 0.4 | n |  | TRUE
68 | bus_LV_5514-1_1_5_node_87 | 0.4 | n |  | TRUE
69 | bus_LV_5514-1_1_5_node_88 | 0.4 | n |  | TRUE
70 | bus_LV_5514-1_1_5_node_105 | 0.4 | n |  | TRUE
71 | bus_LV_5514-1_1_5_node_106 | 0.4 | n |  | TRUE
72 | bus_LV_5514-1_1_5_node_107 | 0.4 | n |  | TRUE
73 | bus_LV_5514-1_1_5_node_108 | 0.4 | n |  | TRUE
74 | bus_LV_5514-1_1_5_node_112 | 0.4 | n |  | TRUE
75 | bus_LV_5514-1_1_5_node_110 | 0.4 | n |  | TRUE
76 | bus_LV_5514-1_1_5_node_109 | 0.4 | n |  | TRUE
77 | bus_LV_5514-1_1_5_node_111 | 0.4 | n |  | TRUE
78 | bus_LV_5514-1_1_5_node_113 | 0.4 | n |  | TRUE
79 | bus_LV_5514-1_1_5_node_114 | 0.4 | n |  | TRUE
80 | bus_LV_5514-1_1_5_node_115 | 0.4 | n |  | TRUE
81 | bus_LV_5514-1_1_5_node_116 | 0.4 | n |  | TRUE
82 | bus_LV_5514-1_1_5_node_117 | 0.4 | n |  | TRUE
83 | bus_LV_5514-1_1_5_node_121 | 0.4 | n |  | TRUE
84 | bus_LV_5514-1_1_5_node_118 | 0.4 | n |  | TRUE
85 | bus_LV_5514-1_1_5_node_119 | 0.4 | n |  | TRUE
86 | bus_LV_5514-1_1_5_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_5514-1_1_5_node_122 | 0.4 | n |  | TRUE
88 | bus_LV_5514-1_1_5_node_123 | 0.4 | n |  | TRUE
89 | bus_LV_5514-1_1_5_node_124 | 0.4 | n |  | TRUE
90 | bus_LV_5514-1_1_5_node_125 | 0.4 | n |  | TRUE
91 | bus_LV_5514-1_1_5_node_126 | 0.4 | n |  | TRUE
92 | bus_LV_5514-1_1_5_node_127 | 0.4 | n |  | TRUE
93 | bus_LV_5514-1_1_5_node_128 | 0.4 | n |  | TRUE
94 | bus_LV_5514-1_1_5_node_138 | 0.4 | n |  | TRUE
95 | bus_LV_5514-1_1_5_node_139 | 0.4 | n |  | TRUE
96 | bus_LV_5514-1_1_5_node_137 | 0.4 | n |  | TRUE
97 | bus_LV_5514-1_1_5_node_140 | 0.4 | n |  | TRUE
98 | bus_LV_5514-1_1_5_node_136 | 0.4 | n |  | TRUE
99 | bus_LV_5514-1_1_5_node_129 | 0.4 | n |  | TRUE
100 | bus_LV_5514-1_1_5_node_130 | 0.4 | n |  | TRUE
101 | bus_LV_5514-1_1_5_node_132 | 0.4 | n |  | TRUE
102 | bus_LV_5514-1_1_5_node_134 | 0.4 | n |  | TRUE
103 | bus_LV_5514-1_1_5_node_135 | 0.4 | n |  | TRUE
104 | bus_MV_448_0_node_14 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5514-1_1_5_load_26 | 0 | 0.0047321 | 0.001186 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5514-1_1_5_load_28 | 2 | 0.0082627 | 0.0020708 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5514-1_1_5_load_29 | 3 | 0.001971 | 0.00049398 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5514-1_1_5_load_30 | 4 | 0.0045001 | 0.0011278 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5514-1_1_5_load_31 | 5 | 0.0020659 | 0.00051777 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5514-1_1_5_load_34 | 8 | 0.0064303 | 0.0016116 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5514-1_1_5_load_82 | 9 | 0.011017 | 0.0027611 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5514-1_1_5_load_83 | 10 | 0.0045615 | 0.0011432 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5514-1_1_5_load_50 | 11 | 0.0049455 | 0.0012395 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5514-1_1_5_load_47 | 13 | 0.0035468 | 0.00088891 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5514-1_1_5_load_36 | 14 | 0.0052133 | 0.0013066 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5514-1_1_5_load_37 | 15 | 0.002653 | 0.0006649 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5514-1_1_5_load_39 | 17 | 0.0011278 | 0.00028265 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5514-1_1_5_load_40 | 18 | 0.0030802 | 0.00077198 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5514-1_1_5_load_41 | 19 | 0.0045233 | 0.0011336 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5514-1_1_5_load_42 | 20 | 0.0025976 | 0.00065103 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5514-1_1_5_load_97 | 23 | 0.0043535 | 0.0010911 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5514-1_1_5_load_48 | 25 | 0.0044303 | 0.0011103 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5514-1_1_5_load_49 | 26 | 0.00095547 | 0.00023946 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5514-1_1_5_load_51 | 27 | 0.00035029 | 8.7792e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5514-1_1_5_load_52 | 28 | 0.0044705 | 0.0011204 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5514-1_1_5_load_53 | 29 | 0.00098502 | 0.00024687 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5514-1_1_5_load_54 | 30 | 0.0041769 | 0.0010468 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5514-1_1_5_load_56 | 32 | 0.00097062 | 0.00024326 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5514-1_1_5_load_57 | 33 | 0.0013583 | 0.00034041 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5514-1_1_5_load_58 | 34 | 0.002869 | 0.00071903 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5514-1_1_5_load_60 | 36 | 0.00088706 | 0.00022232 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5514-1_1_5_load_66 | 39 | 0.00097981 | 0.00024556 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5514-1_1_5_load_103 | 41 | 0.0017671 | 0.00044288 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5514-1_1_5_load_63 | 42 | 0.0036215 | 0.00090764 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5514-1_1_5_load_101 | 44 | 0.0018576 | 0.00046555 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5514-1_1_5_load_102 | 45 | 0.0029594 | 0.00074168 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5514-1_1_5_load_104 | 46 | 0.0017164 | 0.00043018 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5514-1_1_5_load_64 | 47 | 0.015355 | 0.0038482 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5514-1_1_5_load_65 | 48 | 0.0017995 | 0.000451 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5514-1_1_5_load_84 | 49 | 0.0034012 | 0.00085243 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5514-1_1_5_load_69 | 50 | 0.0026232 | 0.00065744 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5514-1_1_5_load_75 | 51 | 0.00068725 | 0.00017224 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5514-1_1_5_load_85 | 52 | 0.0024442 | 0.00061257 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5514-1_1_5_load_70 | 54 | 0.0013268 | 0.00033253 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5514-1_1_5_load_71 | 55 | 0.0017944 | 0.00044973 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5514-1_1_5_load_73 | 56 | 0.0039369 | 0.00098667 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5514-1_1_5_load_74 | 57 | 0.0014006 | 0.00035103 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5514-1_1_5_load_76 | 58 | 0.0015094 | 0.00037828 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5514-1_1_5_load_89 | 60 | 0.0039014 | 0.00097778 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5514-1_1_5_load_79 | 62 | 0.001044 | 0.00026166 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5514-1_1_5_load_80 | 63 | 0.01554 | 0.0038946 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5514-1_1_5_load_81 | 64 | 0.011629 | 0.0029146 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5514-1_1_5_load_133 | 65 | 0.0079195 | 0.0019848 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5514-1_1_5_load_131 | 66 | 0.00091496 | 0.00022931 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5514-1_1_5_load_86 | 67 | 0.00085006 | 0.00021304 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5514-1_1_5_load_87 | 68 | 0.002244 | 0.0005624 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5514-1_1_5_load_88 | 69 | 0.0068542 | 0.0017178 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5514-1_1_5_load_105 | 70 | 0.0033291 | 0.00083435 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5514-1_1_5_load_106 | 71 | 0.0018256 | 0.00045755 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5514-1_1_5_load_107 | 72 | 0.0015136 | 0.00037935 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5514-1_1_5_load_108 | 73 | 0.0010051 | 0.00025191 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5514-1_1_5_load_112 | 74 | 0.0010462 | 0.00026221 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5514-1_1_5_load_110 | 75 | 0.001886 | 0.00047269 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5514-1_1_5_load_109 | 76 | 0.0039525 | 0.0009906 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5514-1_1_5_load_111 | 77 | 0.0017677 | 0.00044302 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5514-1_1_5_load_113 | 78 | 0.0046113 | 0.0011557 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5514-1_1_5_load_114 | 79 | 0.0036329 | 0.0009105 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5514-1_1_5_load_116 | 81 | 0.002847 | 0.00071351 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5514-1_1_5_load_117 | 82 | 0.0011689 | 0.00029295 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5514-1_1_5_load_121 | 83 | 0.0011222 | 0.00028126 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5514-1_1_5_load_119 | 85 | 0.0033435 | 0.00083796 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5514-1_1_5_load_120 | 86 | 0.0018775 | 0.00047055 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5514-1_1_5_load_122 | 87 | 0.0028358 | 0.00071072 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5514-1_1_5_load_123 | 88 | 0.0061561 | 0.0015429 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5514-1_1_5_load_125 | 90 | 0.013363 | 0.0033492 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5514-1_1_5_load_126 | 91 | 0.004833 | 0.0012113 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5514-1_1_5_load_127 | 92 | 0.0025146 | 0.00063022 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5514-1_1_5_load_138 | 94 | 0.0025374 | 0.00063593 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5514-1_1_5_load_139 | 95 | 0.001009 | 0.00025288 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5514-1_1_5_load_137 | 96 | 0.0031605 | 0.00079209 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5514-1_1_5_load_140 | 97 | 0.0050582 | 0.0012677 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5514-1_1_5_load_136 | 98 | 0.0040553 | 0.0010163 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5514-1_1_5_load_129 | 99 | 0.0066566 | 0.0016683 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5514-1_1_5_load_130 | 100 | 0.0019002 | 0.00047624 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5514-1_1_5_load_132 | 101 | 0.0040856 | 0.0010239 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5514-1_1_5_load_134 | 102 | 0.0031458 | 0.00078841 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5514-1_1_5_load_135 | 103 | 0.0011187 | 0.00028038 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 47 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5514-1_1_5_line_0 |  | 0 | 1 | 0.025793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5514-1_1_5_line_1 |  | 1 | 2 | 0.0049209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5514-1_1_5_line_2 |  | 1 | 3 | 0.021154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5514-1_1_5_line_3 |  | 2 | 4 | 0.018991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5514-1_1_5_line_4 |  | 3 | 5 | 0.016131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5514-1_1_5_line_5 |  | 4 | 6 | 0.0193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5514-1_1_5_line_6 |  | 6 | 7 | 0.035788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_5514-1_1_5_line_7 |  | 6 | 8 | 0.014543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_5514-1_1_5_line_8 |  | 7 | 9 | 0.022036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5514-1_1_5_line_9 |  | 7 | 10 | 0.006384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_5514-1_1_5_line_10 |  | 8 | 11 | 0.0087408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_5514-1_1_5_line_11 |  | 10 | 12 | 0.056518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_5514-1_1_5_line_12 |  | 11 | 13 | 0.014743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_5514-1_1_5_line_13 |  | 12 | 49 | 0.017264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5514-1_1_5_line_14 |  | 12 | 48 | 0.028719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_5514-1_1_5_line_15 |  | 13 | 21 | 0.016826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_5514-1_1_5_line_16 |  | 14 | 15 | 0.014065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5514-1_1_5_line_17 |  | 14 | 16 | 0.012935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5514-1_1_5_line_18 |  | 15 | 17 | 0.0016162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5514-1_1_5_line_19 |  | 16 | 18 | 0.027744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5514-1_1_5_line_20 |  | 17 | 19 | 0.0085082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5514-1_1_5_line_21 |  | 18 | 20 | 0.013098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5514-1_1_5_line_22 |  | 20 | 21 | 0.015544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5514-1_1_5_line_23 |  | 21 | 22 | 0.013978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_5514-1_1_5_line_24 |  | 22 | 25 | 0.026381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5514-1_1_5_line_25 |  | 22 | 26 | 0.013259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_5514-1_1_5_line_26 |  | 23 | 24 | 0.042788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5514-1_1_5_line_27 |  | 24 | 43 | 0.007227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5514-1_1_5_line_28 |  | 26 | 27 | 0.0049015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_5514-1_1_5_line_29 |  | 27 | 28 | 0.028873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_5514-1_1_5_line_30 |  | 28 | 29 | 0.0023955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_5514-1_1_5_line_31 |  | 29 | 30 | 0.0049921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_5514-1_1_5_line_32 |  | 30 | 31 | 0.031566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_5514-1_1_5_line_33 |  | 31 | 32 | 0.028528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_5514-1_1_5_line_34 |  | 31 | 33 | 0.037233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5514-1_1_5_line_35 |  | 31 | 34 | 0.016519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5514-1_1_5_line_36 |  | 32 | 35 | 0.030719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_5514-1_1_5_line_37 |  | 33 | 36 | 0.0029532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5514-1_1_5_line_38 |  | 35 | 37 | 0.015733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_5514-1_1_5_line_39 |  | 35 | 38 | 0.11801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5514-1_1_5_line_40 |  | 36 | 39 | 0.031544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5514-1_1_5_line_41 |  | 37 | 42 | 0.051317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5514-1_1_5_line_42 |  | 37 | 40 | 0.028009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_5514-1_1_5_line_43 |  | 38 | 45 | 0.065301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5514-1_1_5_line_44 |  | 38 | 43 | 0.03595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5514-1_1_5_line_45 |  | 40 | 41 | 0.019254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_5514-1_1_5_line_46 |  | 41 | 46 | 0.012055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_5514-1_1_5_line_47 |  | 43 | 44 | 0.026368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5514-1_1_5_line_48 |  | 46 | 70 | 0.01792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_5514-1_1_5_line_49 |  | 47 | 48 | 0.017154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_5514-1_1_5_line_50 |  | 49 | 52 | 0.0078615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5514-1_1_5_line_51 |  | 50 | 51 | 0.0036281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5514-1_1_5_line_52 |  | 51 | 53 | 0.012052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5514-1_1_5_line_53 |  | 52 | 67 | 0.0090948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5514-1_1_5_line_54 |  | 53 | 57 | 0.049788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_5514-1_1_5_line_55 |  | 53 | 54 | 0.02273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_5514-1_1_5_line_56 |  | 54 | 55 | 0.0019887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_5514-1_1_5_line_57 |  | 55 | 56 | 0.022649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_5514-1_1_5_line_58 |  | 56 | 58 | 0.01799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_5514-1_1_5_line_59 |  | 57 | 59 | 0.023322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_5514-1_1_5_line_60 |  | 58 | 60 | 0.0044937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5514-1_1_5_line_61 |  | 59 | 61 | 0.035874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_5514-1_1_5_line_62 |  | 59 | 62 | 0.011364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5514-1_1_5_line_63 |  | 61 | 63 | 0.025756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5514-1_1_5_line_64 |  | 61 | 64 | 0.018192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_5514-1_1_5_line_65 |  | 64 | 65 | 0.035592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_5514-1_1_5_line_66 |  | 65 | 66 | 0.0063254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_5514-1_1_5_line_67 |  | 66 | 99 | 0.015117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_5514-1_1_5_line_68 |  | 67 | 68 | 0.0092552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5514-1_1_5_line_69 |  | 68 | 69 | 0.017923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5514-1_1_5_line_70 |  | 70 | 71 | 0.0029642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_5514-1_1_5_line_71 |  | 71 | 72 | 0.0095672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_5514-1_1_5_line_72 |  | 72 | 73 | 0.0032529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_5514-1_1_5_line_73 |  | 73 | 74 | 0.011388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_5514-1_1_5_line_74 |  | 74 | 75 | 0.0047569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_5514-1_1_5_line_75 |  | 75 | 76 | 0.0031903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_5514-1_1_5_line_76 |  | 76 | 77 | 0.0081192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_5514-1_1_5_line_77 |  | 77 | 78 | 0.028415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_5514-1_1_5_line_78 |  | 78 | 79 | 0.00041106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_5514-1_1_5_line_79 |  | 79 | 80 | 0.022461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_5514-1_1_5_line_80 |  | 80 | 81 | 0.02809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5514-1_1_5_line_81 |  | 80 | 82 | 0.0041186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_5514-1_1_5_line_82 |  | 81 | 83 | 0.0059806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5514-1_1_5_line_83 |  | 82 | 84 | 0.050413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_5514-1_1_5_line_84 |  | 84 | 85 | 0.019538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_5514-1_1_5_line_85 |  | 84 | 86 | 0.017152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5514-1_1_5_line_86 |  | 85 | 87 | 0.018345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_5514-1_1_5_line_87 |  | 86 | 88 | 0.0054393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_5514-1_1_5_line_88 |  | 87 | 89 | 0.037421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_5514-1_1_5_line_89 |  | 89 | 90 | 0.031467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_5514-1_1_5_line_90 |  | 89 | 91 | 0.0073078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_5514-1_1_5_line_91 |  | 90 | 92 | 0.0045154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5514-1_1_5_line_92 |  | 91 | 93 | 0.028289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_5514-1_1_5_line_93 |  | 92 | 94 | 0.025507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5514-1_1_5_line_94 |  | 93 | 95 | 0.037361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_5514-1_1_5_line_95 |  | 93 | 96 | 0.025281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_5514-1_1_5_line_96 |  | 95 | 97 | 0.0050661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_5514-1_1_5_line_97 |  | 96 | 98 | 0.025176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_5514-1_1_5_line_98 |  | 98 | 103 | 0.014834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_5514-1_1_5_line_99 |  | 99 | 100 | 0.024759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_5514-1_1_5_line_100 |  | 100 | 101 | 0.020765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_5514-1_1_5_line_101 |  | 101 | 102 | 0.003005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_5514-1_1_5_line_102 |  | 102 | 103 | 0.0090594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5514-1_1_5_trafo_64 | 0.63 MVA 20/0.4 kV | 104 | 47 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2540200.1138 | 1163304.807 | 2540189.9509 | 1163281.1007
1 | 2540200.1138 | 1163304.807 | 2540201.6999 | 1163309.4653
2 | 2540200.1138 | 1163304.807 | 2540217.2794 | 1163292.4436
3 | 2540201.6999 | 1163309.4653 | 2540207.8211 | 1163327.4428
4 | 2540230.3688 | 1163283.016 | 2540217.2794 | 1163292.4436
5 | 2540214.0418 | 1163345.7128 | 2540207.8211 | 1163327.4428
6 | 2540242.9154 | 1163324.458 | 2540214.0418 | 1163345.7128
7 | 2540214.0418 | 1163345.7128 | 2540206.2634 | 1163358.001
8 | 2540242.9154 | 1163324.458 | 2540255.8855 | 1163342.2942
9 | 2540242.9154 | 1163324.458 | 2540248.0568 | 1163320.6736
10 | 2540201.5883 | 1163365.3865 | 2540206.2634 | 1163358.001
11 | 2540287.6901 | 1163280.7219 | 2540268.6384 | 1163302.1787 | 2540260.0785 | 1163311.8247 | 2540248.0568 | 1163320.6736
12 | 2540201.5883 | 1163365.3865 | 2540198.8158 | 1163369.7664 | 2540194.5552 | 1163378.3234
13 | 2540287.6901 | 1163280.7219 | 2540277.9783 | 1163266.4488
14 | 2540287.6901 | 1163280.7219 | 2540304.9999 | 1163303.638
15 | 2540187.0557 | 1163393.3854 | 2540194.5552 | 1163378.3234
16 | 2540126.0963 | 1163374.8943 | 2540126.0963 | 1163374.8943 | 2540137.6636 | 1163366.8926
17 | 2540131.5981 | 1163386.6014 | 2540126.0963 | 1163374.8943
18 | 2540137.6636 | 1163366.8926 | 2540138.9928 | 1163365.9732
19 | 2540131.5981 | 1163386.6014 | 2540144.6652 | 1163384.9701 | 2540158.9619 | 1163387.8083
20 | 2540145.99 | 1163361.1328 | 2540138.9928 | 1163365.9732
21 | 2540171.8092 | 1163390.3587 | 2540158.9619 | 1163387.8083
22 | 2540187.0557 | 1163393.3854 | 2540171.8092 | 1163390.3587
23 | 2540197.4368 | 1163402.7759 | 2540187.0557 | 1163393.3854
24 | 2540197.4368 | 1163402.7759 | 2540215.9316 | 1163383.9147
25 | 2540197.4368 | 1163402.7759 | 2540207.2658 | 1163411.6745
26 | 2540107.5982 | 1163608.962 | 2540092.2001 | 1163617.965 | 2540068.0901 | 1163624.3871
27 | 2540107.5982 | 1163608.962 | 2540113.5159 | 1163604.7896
28 | 2540210.8994 | 1163414.9642 | 2540207.2658 | 1163411.6745
29 | 2540210.8994 | 1163414.9642 | 2540226.8176 | 1163429.3755 | 2540231.2524 | 1163435.3004
30 | 2540231.2524 | 1163435.3004 | 2540232.6879 | 1163437.2181
31 | 2540235.6793 | 1163441.2146 | 2540232.6879 | 1163437.2181
32 | 2540254.5948 | 1163466.4858 | 2540235.6793 | 1163441.2146
33 | 2540254.5948 | 1163466.4858 | 2540250.088 | 1163494.6552
34 | 2540254.5948 | 1163466.4858 | 2540255.1498 | 1163462.9894 | 2540265.2092 | 1163430.8335
35 | 2540254.5948 | 1163466.4858 | 2540264.099 | 1163479.9968
36 | 2540245.235 | 1163524.9886 | 2540250.088 | 1163494.6552
37 | 2540265.2092 | 1163430.8335 | 2540266.0909 | 1163428.015
38 | 2540245.235 | 1163524.9886 | 2540252.8965 | 1163525.9128 | 2540260.7129 | 1163523.945
39 | 2540245.235 | 1163524.9886 | 2540144.2748 | 1163586.0947
40 | 2540275.5088 | 1163397.9097 | 2540266.0909 | 1163428.015
41 | 2540260.7129 | 1163523.945 | 2540287.8129 | 1163567.5228
42 | 2540284.0584 | 1163508.3709 | 2540260.7129 | 1163523.945
43 | 2540144.2748 | 1163586.0947 | 2540161.2291 | 1163602.5346 | 2540174.0096 | 1163622.1289 | 2540186.5066 | 1163635.5784
44 | 2540144.2748 | 1163586.0947 | 2540121.6242 | 1163599.0833 | 2540113.5159 | 1163604.7896
45 | 2540284.0584 | 1163508.3709 | 2540300.0796 | 1163497.6918
46 | 2540300.0796 | 1163497.6918 | 2540307.3051 | 1163492.8756 | 2540310.2969 | 1163491.3211
47 | 2540113.5159 | 1163604.7896 | 2540112.6677 | 1163611.9019 | 2540115.6613 | 1163617.8975 | 2540124.8097 | 1163626.4212
48 | 2540326.1985 | 1163483.0592 | 2540310.2969 | 1163491.3211
49 | 2540299.8785 | 1163320.0091 | 2540304.9999 | 1163303.638
50 | 2540273.5558 | 1163259.9493 | 2540277.9783 | 1163266.4488
51 | 2540330.6213 | 1163224.8085 | 2540332.4333 | 1163221.6652
52 | 2540338.4523 | 1163211.2236 | 2540332.4333 | 1163221.6652
53 | 2540268.4394 | 1163252.43 | 2540273.5558 | 1163259.9493
54 | 2540338.4523 | 1163211.2236 | 2540364.147 | 1163175.2264 | 2540367.4864 | 1163170.78
55 | 2540338.4523 | 1163211.2236 | 2540323.8902 | 1163193.771
56 | 2540323.8902 | 1163193.771 | 2540322.6162 | 1163192.244
57 | 2540322.6162 | 1163192.244 | 2540308.1056 | 1163174.8532
58 | 2540308.1056 | 1163174.8532 | 2540296.5802 | 1163161.0401
59 | 2540380.9656 | 1163151.7577 | 2540374.3005 | 1163161.7071 | 2540367.4864 | 1163170.78
60 | 2540293.7013 | 1163157.5896 | 2540296.5802 | 1163161.0401
61 | 2540399.3199 | 1163182.6033 | 2540395.3001 | 1163175.8506 | 2540391.6541 | 1163169.7168 | 2540380.9656 | 1163151.7577
62 | 2540380.9656 | 1163151.7577 | 2540386.3208 | 1163144.1114 | 2540387.5578 | 1163142.5028
63 | 2540399.3199 | 1163182.6033 | 2540422.1452 | 1163170.6702
64 | 2540399.3199 | 1163182.6033 | 2540408.3107 | 1163198.4183
65 | 2540425.9008 | 1163229.36 | 2540408.3107 | 1163198.4183
66 | 2540429.027 | 1163234.8589 | 2540425.9008 | 1163229.36
67 | 2540436.4979 | 1163248.0005 | 2540429.027 | 1163234.8589
68 | 2540268.4394 | 1163252.43 | 2540263.2328 | 1163244.7781
69 | 2540253.1503 | 1163229.9602 | 2540263.2328 | 1163244.7781
70 | 2540326.1985 | 1163483.0592 | 2540328.8289 | 1163481.6925
71 | 2540337.3185 | 1163477.2815 | 2540328.8289 | 1163481.6925
72 | 2540337.3185 | 1163477.2815 | 2540340.205 | 1163475.7817
73 | 2540340.205 | 1163475.7817 | 2540350.3104 | 1163470.5313
74 | 2540350.3104 | 1163470.5313 | 2540354.5315 | 1163468.3381
75 | 2540357.3625 | 1163466.8672 | 2540354.5315 | 1163468.3381
76 | 2540364.5672 | 1163463.1239 | 2540357.3625 | 1163466.8672
77 | 2540364.5672 | 1163463.1239 | 2540375.5625 | 1163457.411 | 2540390.8454 | 1163452.592
78 | 2540390.8454 | 1163452.592 | 2540391.2374 | 1163452.4684
79 | 2540412.6583 | 1163445.714 | 2540391.2374 | 1163452.4684
80 | 2540412.6583 | 1163445.714 | 2540421.5592 | 1163464.2135 | 2540425.3738 | 1163470.741
81 | 2540412.6583 | 1163445.714 | 2540416.6191 | 1163444.5846
82 | 2540428.3913 | 1163475.9045 | 2540425.3738 | 1163470.741
83 | 2540461.5225 | 1163422.6831 | 2540446.5765 | 1163433.3483 | 2540427.3622 | 1163441.5213 | 2540416.6191 | 1163444.5846
84 | 2540461.5225 | 1163422.6831 | 2540477.6446 | 1163411.6459
85 | 2540461.5225 | 1163422.6831 | 2540474.8488 | 1163433.4813
86 | 2540477.6446 | 1163411.6459 | 2540492.782 | 1163401.2829
87 | 2540479.0748 | 1163436.9056 | 2540474.8488 | 1163433.4813
88 | 2540523.6599 | 1163380.1438 | 2540492.782 | 1163401.2829
89 | 2540523.6599 | 1163380.1438 | 2540544.2774 | 1163403.9158
90 | 2540523.6599 | 1163380.1438 | 2540519.1556 | 1163374.3892
91 | 2540547.2359 | 1163407.327 | 2540544.2774 | 1163403.9158
92 | 2540501.7192 | 1163352.1127 | 2540519.1556 | 1163374.3892
93 | 2540547.2359 | 1163407.327 | 2540557.6065 | 1163419.2843 | 2540564.3267 | 1163426.2505
94 | 2540501.7192 | 1163352.1127 | 2540522.3414 | 1163331.3748 | 2540527.5541 | 1163325.155
95 | 2540501.7192 | 1163352.1127 | 2540487.695 | 1163331.0783
96 | 2540530.8082 | 1163321.2722 | 2540527.5541 | 1163325.155
97 | 2540487.695 | 1163331.0783 | 2540485.4755 | 1163327.7494 | 2540474.2872 | 1163309.7715
98 | 2540466.4492 | 1163297.177 | 2540474.2872 | 1163309.7715
99 | 2540436.4979 | 1163248.0005 | 2540443.3935 | 1163260.1301 | 2540449.1032 | 1163269.3047
100 | 2540449.1032 | 1163269.3047 | 2540460.0746 | 1163286.9341
101 | 2540461.6624 | 1163289.4855 | 2540460.0746 | 1163286.9341
102 | 2540461.6624 | 1163289.4855 | 2540466.4492 | 1163297.177

## bus_geodata
| x | y | coords
0 | 2540189.9509 | 1163281.1007
1 | 2540200.1138 | 1163304.807
2 | 2540201.6999 | 1163309.4653
3 | 2540217.2794 | 1163292.4436
4 | 2540207.8211 | 1163327.4428
5 | 2540230.3688 | 1163283.016
6 | 2540214.0418 | 1163345.7128
7 | 2540242.9154 | 1163324.458
8 | 2540206.2634 | 1163358.001
9 | 2540255.8855 | 1163342.2942
10 | 2540248.0568 | 1163320.6736
11 | 2540201.5883 | 1163365.3865
12 | 2540287.6901 | 1163280.7219
13 | 2540194.5552 | 1163378.3234
14 | 2540126.0963 | 1163374.8943
15 | 2540137.6636 | 1163366.8926
16 | 2540131.5981 | 1163386.6014
17 | 2540138.9928 | 1163365.9732
18 | 2540158.9619 | 1163387.8083
19 | 2540145.99 | 1163361.1328
20 | 2540171.8092 | 1163390.3587
21 | 2540187.0557 | 1163393.3854
22 | 2540197.4368 | 1163402.7759
23 | 2540068.0901 | 1163624.3871
24 | 2540107.5982 | 1163608.962
25 | 2540215.9316 | 1163383.9147
26 | 2540207.2658 | 1163411.6745
27 | 2540210.8994 | 1163414.9642
28 | 2540231.2524 | 1163435.3004
29 | 2540232.6879 | 1163437.2181
30 | 2540235.6793 | 1163441.2146
31 | 2540254.5948 | 1163466.4858
32 | 2540250.088 | 1163494.6552
33 | 2540265.2092 | 1163430.8335
34 | 2540264.099 | 1163479.9968
35 | 2540245.235 | 1163524.9886
36 | 2540266.0909 | 1163428.015
37 | 2540260.7129 | 1163523.945
38 | 2540144.2748 | 1163586.0947
39 | 2540275.5088 | 1163397.9097
40 | 2540284.0584 | 1163508.3709
41 | 2540300.0796 | 1163497.6918
42 | 2540287.8129 | 1163567.5228
43 | 2540113.5159 | 1163604.7895
44 | 2540124.8097 | 1163626.4212
45 | 2540186.5066 | 1163635.5784
46 | 2540310.2969 | 1163491.3211
47 | 2540299.8785 | 1163320.0091
48 | 2540304.9999 | 1163303.638
49 | 2540277.9783 | 1163266.4488
50 | 2540330.6213 | 1163224.8085
51 | 2540332.4333 | 1163221.6652
52 | 2540273.5558 | 1163259.9493
53 | 2540338.4523 | 1163211.2236
54 | 2540323.8902 | 1163193.771
55 | 2540322.6162 | 1163192.244
56 | 2540308.1056 | 1163174.8532
57 | 2540367.4864 | 1163170.78
58 | 2540296.5802 | 1163161.0401
59 | 2540380.9656 | 1163151.7577
60 | 2540293.7013 | 1163157.5896
61 | 2540399.3199 | 1163182.6033
62 | 2540387.5578 | 1163142.5028
63 | 2540422.1452 | 1163170.6702
64 | 2540408.3107 | 1163198.4183
65 | 2540425.9008 | 1163229.36
66 | 2540429.027 | 1163234.8589
67 | 2540268.4394 | 1163252.43
68 | 2540263.2328 | 1163244.7781
69 | 2540253.1503 | 1163229.9602
70 | 2540326.1985 | 1163483.0592
71 | 2540328.8289 | 1163481.6925
72 | 2540337.3185 | 1163477.2815
73 | 2540340.205 | 1163475.7817
74 | 2540350.3104 | 1163470.5313
75 | 2540354.5315 | 1163468.3381
76 | 2540357.3625 | 1163466.8672
77 | 2540364.5672 | 1163463.1239
78 | 2540390.8454 | 1163452.592
79 | 2540391.2374 | 1163452.4684
80 | 2540412.6583 | 1163445.714
81 | 2540425.3738 | 1163470.741
82 | 2540416.6191 | 1163444.5846
83 | 2540428.3913 | 1163475.9045
84 | 2540461.5225 | 1163422.6831
85 | 2540477.6446 | 1163411.6459
86 | 2540474.8488 | 1163433.4813
87 | 2540492.782 | 1163401.2829
88 | 2540479.0748 | 1163436.9056
89 | 2540523.6599 | 1163380.1438
90 | 2540544.2774 | 1163403.9158
91 | 2540519.1556 | 1163374.3892
92 | 2540547.2359 | 1163407.327
93 | 2540501.7192 | 1163352.1127
94 | 2540564.3267 | 1163426.2505
95 | 2540527.5541 | 1163325.155
96 | 2540487.695 | 1163331.0783
97 | 2540530.8082 | 1163321.2722
98 | 2540474.2872 | 1163309.7715
99 | 2540436.4979 | 1163248.0005
100 | 2540449.1032 | 1163269.3047
101 | 2540460.0746 | 1163286.9341
102 | 2540461.6624 | 1163289.4855
103 | 2540466.4492 | 1163297.177
104 | 2540328.5198 | 1163228.454

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1