## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5551-2_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5551-2_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5551-2_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5551-2_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5551-2_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5551-2_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_5551-2_0_6_node_117 | 0.4 | n |  | TRUE
7 | bus_LV_5551-2_0_6_node_92 | 0.4 | n |  | TRUE
8 | bus_LV_5551-2_0_6_node_86 | 0.4 | n |  | TRUE
9 | bus_LV_5551-2_0_6_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_5551-2_0_6_node_119 | 0.4 | n |  | TRUE
11 | bus_LV_5551-2_0_6_node_90 | 0.4 | n |  | TRUE
12 | bus_LV_5551-2_0_6_node_85 | 0.4 | n |  | TRUE
13 | bus_LV_5551-2_0_6_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_5551-2_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_5551-2_0_6_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_5551-2_0_6_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_5551-2_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_5551-2_0_6_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_5551-2_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_5551-2_0_6_node_97 | 0.4 | n |  | TRUE
21 | bus_LV_5551-2_0_6_node_107 | 0.4 | n |  | TRUE
22 | bus_LV_5551-2_0_6_node_62 | 0.4 | n |  | TRUE
23 | bus_LV_5551-2_0_6_node_60 | 0.4 | n |  | TRUE
24 | bus_LV_5551-2_0_6_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_5551-2_0_6_node_142 | 0.4 | n |  | TRUE
26 | bus_LV_5551-2_0_6_node_99 | 0.4 | n |  | TRUE
27 | bus_LV_5551-2_0_6_node_95 | 0.4 | n |  | TRUE
28 | bus_LV_5551-2_0_6_node_68 | 0.4 | n |  | TRUE
29 | bus_LV_5551-2_0_6_node_72 | 0.4 | n |  | TRUE
30 | bus_LV_5551-2_0_6_node_61 | 0.4 | n |  | TRUE
31 | bus_LV_5551-2_0_6_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_5551-2_0_6_node_140 | 0.4 | n |  | TRUE
33 | bus_LV_5551-2_0_6_node_13 | 0.4 | n |  | TRUE
34 | bus_LV_5551-2_0_6_node_14 | 0.4 | n |  | TRUE
35 | bus_LV_5551-2_0_6_node_15 | 0.4 | n |  | TRUE
36 | bus_LV_5551-2_0_6_node_17 | 0.4 | n |  | TRUE
37 | bus_LV_5551-2_0_6_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_5551-2_0_6_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_5551-2_0_6_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_5551-2_0_6_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_5551-2_0_6_node_46 | 0.4 | n |  | TRUE
42 | bus_LV_5551-2_0_6_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_5551-2_0_6_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_5551-2_0_6_node_116 | 0.4 | n |  | TRUE
45 | bus_LV_5551-2_0_6_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_5551-2_0_6_node_148 | 0.4 | n |  | TRUE
47 | bus_LV_5551-2_0_6_node_164 | 0.4 | n |  | TRUE
48 | bus_LV_5551-2_0_6_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_5551-2_0_6_node_19 | 0.4 | n |  | TRUE
50 | bus_LV_5551-2_0_6_node_20 | 0.4 | n |  | TRUE
51 | bus_LV_5551-2_0_6_node_21 | 0.4 | n |  | TRUE
52 | bus_LV_5551-2_0_6_node_22 | 0.4 | n |  | TRUE
53 | bus_LV_5551-2_0_6_node_115 | 0.4 | n |  | TRUE
54 | bus_LV_5551-2_0_6_node_114 | 0.4 | n |  | TRUE
55 | bus_LV_5551-2_0_6_node_82 | 0.4 | n |  | TRUE
56 | bus_LV_5551-2_0_6_node_29 | 0.4 | n |  | TRUE
57 | bus_LV_5551-2_0_6_node_168 | 0.4 | n |  | TRUE
58 | bus_LV_5551-2_0_6_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_5551-2_0_6_node_83 | 0.4 | n |  | TRUE
60 | bus_LV_5551-2_0_6_node_28 | 0.4 | n |  | TRUE
61 | bus_LV_5551-2_0_6_node_23 | 0.4 | n |  | TRUE
62 | bus_LV_5551-2_0_6_node_24 | 0.4 | n |  | TRUE
63 | bus_LV_5551-2_0_6_node_25 | 0.4 | n |  | TRUE
64 | bus_LV_5551-2_0_6_node_27 | 0.4 | n |  | TRUE
65 | bus_LV_5551-2_0_6_node_121 | 0.4 | n |  | TRUE
66 | bus_LV_5551-2_0_6_node_120 | 0.4 | n |  | TRUE
67 | bus_LV_5551-2_0_6_node_169 | 0.4 | n |  | TRUE
68 | bus_LV_5551-2_0_6_node_81 | 0.4 | n |  | TRUE
69 | bus_LV_5551-2_0_6_node_30 | 0.4 | n |  | TRUE
70 | bus_LV_5551-2_0_6_node_31 | 0.4 | n |  | TRUE
71 | bus_LV_5551-2_0_6_node_32 | 0.4 | n |  | TRUE
72 | bus_LV_5551-2_0_6_node_34 | 0.4 | n |  | TRUE
73 | bus_LV_5551-2_0_6_node_36 | 0.4 | n |  | TRUE
74 | bus_LV_5551-2_0_6_node_41 | 0.4 | n |  | TRUE
75 | bus_LV_5551-2_0_6_node_48 | 0.4 | n |  | TRUE
76 | bus_LV_5551-2_0_6_node_49 | 0.4 | n |  | TRUE
77 | bus_LV_5551-2_0_6_node_147 | 0.4 | n |  | TRUE
78 | bus_LV_5551-2_0_6_node_163 | 0.4 | n |  | TRUE
79 | bus_LV_5551-2_0_6_node_45 | 0.4 | n |  | TRUE
80 | bus_LV_5551-2_0_6_node_43 | 0.4 | n |  | TRUE
81 | bus_LV_5551-2_0_6_node_53 | 0.4 | n |  | TRUE
82 | bus_LV_5551-2_0_6_node_54 | 0.4 | n |  | TRUE
83 | bus_LV_5551-2_0_6_node_136 | 0.4 | n |  | TRUE
84 | bus_LV_5551-2_0_6_node_91 | 0.4 | n |  | TRUE
85 | bus_LV_5551-2_0_6_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_5551-2_0_6_node_110 | 0.4 | n |  | TRUE
87 | bus_LV_5551-2_0_6_node_57 | 0.4 | n |  | TRUE
88 | bus_LV_5551-2_0_6_node_112 | 0.4 | n |  | TRUE
89 | bus_LV_5551-2_0_6_node_111 | 0.4 | n |  | TRUE
90 | bus_LV_5551-2_0_6_node_127 | 0.4 | n |  | TRUE
91 | bus_LV_5551-2_0_6_node_109 | 0.4 | n |  | TRUE
92 | bus_LV_5551-2_0_6_node_113 | 0.4 | n |  | TRUE
93 | bus_LV_5551-2_0_6_node_162 | 0.4 | n |  | TRUE
94 | bus_LV_5551-2_0_6_node_145 | 0.4 | n |  | TRUE
95 | bus_LV_5551-2_0_6_node_63 | 0.4 | n |  | TRUE
96 | bus_LV_5551-2_0_6_node_64 | 0.4 | n |  | TRUE
97 | bus_LV_5551-2_0_6_node_65 | 0.4 | n |  | TRUE
98 | bus_LV_5551-2_0_6_node_66 | 0.4 | n |  | TRUE
99 | bus_LV_5551-2_0_6_node_67 | 0.4 | n |  | TRUE
100 | bus_LV_5551-2_0_6_node_69 | 0.4 | n |  | TRUE
101 | bus_LV_5551-2_0_6_node_143 | 0.4 | n |  | TRUE
102 | bus_LV_5551-2_0_6_node_70 | 0.4 | n |  | TRUE
103 | bus_LV_5551-2_0_6_node_144 | 0.4 | n |  | TRUE
104 | bus_LV_5551-2_0_6_node_141 | 0.4 | n |  | TRUE
105 | bus_LV_5551-2_0_6_node_106 | 0.4 | n |  | TRUE
106 | bus_LV_5551-2_0_6_node_146 | 0.4 | n |  | TRUE
107 | bus_LV_5551-2_0_6_node_80 | 0.4 | n |  | TRUE
108 | bus_LV_5551-2_0_6_node_170 | 0.4 | n |  | TRUE
109 | bus_LV_5551-2_0_6_node_79 | 0.4 | n |  | TRUE
110 | bus_LV_5551-2_0_6_node_165 | 0.4 | n |  | TRUE
111 | bus_LV_5551-2_0_6_node_84 | 0.4 | n |  | TRUE
112 | bus_LV_5551-2_0_6_node_75 | 0.4 | n |  | TRUE
113 | bus_LV_5551-2_0_6_node_76 | 0.4 | n |  | TRUE
114 | bus_LV_5551-2_0_6_node_78 | 0.4 | n |  | TRUE
115 | bus_LV_5551-2_0_6_node_87 | 0.4 | n |  | TRUE
116 | bus_LV_5551-2_0_6_node_88 | 0.4 | n |  | TRUE
117 | bus_LV_5551-2_0_6_node_89 | 0.4 | n |  | TRUE
118 | bus_LV_5551-2_0_6_node_93 | 0.4 | n |  | TRUE
119 | bus_LV_5551-2_0_6_node_137 | 0.4 | n |  | TRUE
120 | bus_LV_5551-2_0_6_node_130 | 0.4 | n |  | TRUE
121 | bus_LV_5551-2_0_6_node_124 | 0.4 | n |  | TRUE
122 | bus_LV_5551-2_0_6_node_138 | 0.4 | n |  | TRUE
123 | bus_LV_5551-2_0_6_node_129 | 0.4 | n |  | TRUE
124 | bus_LV_5551-2_0_6_node_94 | 0.4 | n |  | TRUE
125 | bus_LV_5551-2_0_6_node_96 | 0.4 | n |  | TRUE
126 | bus_LV_5551-2_0_6_node_98 | 0.4 | n |  | TRUE
127 | bus_LV_5551-2_0_6_node_100 | 0.4 | n |  | TRUE
128 | bus_LV_5551-2_0_6_node_101 | 0.4 | n |  | TRUE
129 | bus_LV_5551-2_0_6_node_132 | 0.4 | n |  | TRUE
130 | bus_LV_5551-2_0_6_node_133 | 0.4 | n |  | TRUE
131 | bus_LV_5551-2_0_6_node_102 | 0.4 | n |  | TRUE
132 | bus_LV_5551-2_0_6_node_103 | 0.4 | n |  | TRUE
133 | bus_LV_5551-2_0_6_node_104 | 0.4 | n |  | TRUE
134 | bus_LV_5551-2_0_6_node_105 | 0.4 | n |  | TRUE
135 | bus_LV_5551-2_0_6_node_134 | 0.4 | n |  | TRUE
136 | bus_LV_5551-2_0_6_node_108 | 0.4 | n |  | TRUE
137 | bus_LV_5551-2_0_6_node_139 | 0.4 | n |  | TRUE
138 | bus_LV_5551-2_0_6_node_125 | 0.4 | n |  | TRUE
139 | bus_LV_5551-2_0_6_node_122 | 0.4 | n |  | TRUE
140 | bus_LV_5551-2_0_6_node_123 | 0.4 | n |  | TRUE
141 | bus_LV_5551-2_0_6_node_128 | 0.4 | n |  | TRUE
142 | bus_LV_5551-2_0_6_node_135 | 0.4 | n |  | TRUE
143 | bus_LV_5551-2_0_6_node_126 | 0.4 | n |  | TRUE
144 | bus_LV_5551-2_0_6_node_131 | 0.4 | n |  | TRUE
145 | bus_LV_5551-2_0_6_node_167 | 0.4 | n |  | TRUE
146 | bus_LV_5551-2_0_6_node_149 | 0.4 | n |  | TRUE
147 | bus_LV_5551-2_0_6_node_150 | 0.4 | n |  | TRUE
148 | bus_LV_5551-2_0_6_node_151 | 0.4 | n |  | TRUE
149 | bus_LV_5551-2_0_6_node_153 | 0.4 | n |  | TRUE
150 | bus_LV_5551-2_0_6_node_157 | 0.4 | n |  | TRUE
151 | bus_LV_5551-2_0_6_node_158 | 0.4 | n |  | TRUE
152 | bus_LV_5551-2_0_6_node_156 | 0.4 | n |  | TRUE
153 | bus_LV_5551-2_0_6_node_152 | 0.4 | n |  | TRUE
154 | bus_LV_5551-2_0_6_node_159 | 0.4 | n |  | TRUE
155 | bus_LV_5551-2_0_6_node_160 | 0.4 | n |  | TRUE
156 | bus_LV_5551-2_0_6_node_155 | 0.4 | n |  | TRUE
157 | bus_LV_5551-2_0_6_node_161 | 0.4 | n |  | TRUE
158 | bus_MV_316_0_node_14 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5551-2_0_6_load_0 | 0 | 0.010193 | 0.0025546 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5551-2_0_6_load_1 | 1 | 0.0027136 | 0.00068008 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5551-2_0_6_load_3 | 3 | 0.00062015 | 0.00015543 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5551-2_0_6_load_4 | 4 | 0.014888 | 0.0037313 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5551-2_0_6_load_5 | 5 | 0.038533 | 0.0096574 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5551-2_0_6_load_117 | 6 | 0.0022625 | 0.00056704 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5551-2_0_6_load_86 | 8 | 0.0056688 | 0.0014207 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5551-2_0_6_load_26 | 9 | 0.00039146 | 9.8108e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5551-2_0_6_load_119 | 10 | 0.020523 | 0.0051436 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5551-2_0_6_load_6 | 13 | 0.0037293 | 0.00093465 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5551-2_0_6_load_7 | 15 | 0.00072662 | 0.00018211 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5551-2_0_6_load_10 | 17 | 0.0036175 | 0.00090664 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5551-2_0_6_load_11 | 18 | 0.0010923 | 0.00027375 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5551-2_0_6_load_12 | 19 | 0.0028662 | 0.00071834 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5551-2_0_6_load_60 | 23 | 0.0014795 | 0.00037079 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5551-2_0_6_load_35 | 24 | 0.0013972 | 0.00035017 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5551-2_0_6_load_142 | 25 | 0.0021357 | 0.00053526 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5551-2_0_6_load_99 | 26 | 0.0010886 | 0.00027282 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5551-2_0_6_load_95 | 27 | 0.0018686 | 0.00046833 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5551-2_0_6_load_68 | 28 | 0.0020244 | 0.00050735 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5551-2_0_6_load_61 | 30 | 0.0049567 | 0.0012423 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5551-2_0_6_load_140 | 32 | 0.005599 | 0.0014033 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5551-2_0_6_load_13 | 33 | 0.0028536 | 0.00071519 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5551-2_0_6_load_14 | 34 | 0.00024164 | 6.0561e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5551-2_0_6_load_18 | 37 | 0.0023897 | 0.00059891 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5551-2_0_6_load_37 | 38 | 0.00067921 | 0.00017023 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5551-2_0_6_load_47 | 42 | 0.00051585 | 0.00012928 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5551-2_0_6_load_42 | 43 | 0.0006739 | 0.0001689 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5551-2_0_6_load_116 | 44 | 0.0022515 | 0.00056429 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5551-2_0_6_load_148 | 46 | 0.00094239 | 0.00023619 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5551-2_0_6_load_164 | 47 | 0.00080783 | 0.00020246 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5551-2_0_6_load_19 | 49 | 0.0077102 | 0.0019324 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5551-2_0_6_load_114 | 54 | 0.0014545 | 0.00036454 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5551-2_0_6_load_82 | 55 | 0.0022657 | 0.00056785 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5551-2_0_6_load_29 | 56 | 0.0011852 | 0.00029705 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5551-2_0_6_load_168 | 57 | 0.0051911 | 0.001301 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5551-2_0_6_load_55 | 58 | 0.00072285 | 0.00018116 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5551-2_0_6_load_83 | 59 | 0.0022462 | 0.00056296 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5551-2_0_6_load_28 | 60 | 0.0014968 | 0.00037513 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5551-2_0_6_load_23 | 61 | 0.0015675 | 0.00039286 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5551-2_0_6_load_24 | 62 | 0.00032446 | 8.1317e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5551-2_0_6_load_120 | 66 | 0.00028392 | 7.1158e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5551-2_0_6_load_169 | 67 | 0.00089566 | 0.00022447 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5551-2_0_6_load_30 | 69 | 0.0027322 | 0.00068474 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5551-2_0_6_load_31 | 70 | 0.0025144 | 0.00063018 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5551-2_0_6_load_32 | 71 | 0.0037079 | 0.0009293 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5551-2_0_6_load_34 | 72 | 0.0026023 | 0.00065221 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5551-2_0_6_load_48 | 75 | 0.00030425 | 7.6253e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5551-2_0_6_load_49 | 76 | 0.00049762 | 0.00012472 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5551-2_0_6_load_147 | 77 | 0.0012912 | 0.00032361 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5551-2_0_6_load_163 | 78 | 0.0029504 | 0.00073943 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5551-2_0_6_load_45 | 79 | 0.00030044 | 7.5296e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5551-2_0_6_load_43 | 80 | 0.00046834 | 0.00011738 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5551-2_0_6_load_53 | 81 | 0.0020671 | 0.00051805 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5551-2_0_6_load_136 | 83 | 0.0015289 | 0.00038317 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5551-2_0_6_load_110 | 86 | 0.028062 | 0.0070329 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5551-2_0_6_load_57 | 87 | 0.0028243 | 0.00070783 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5551-2_0_6_load_112 | 88 | 0.0034248 | 0.00085833 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5551-2_0_6_load_111 | 89 | 0.0049557 | 0.001242 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5551-2_0_6_load_127 | 90 | 0.024147 | 0.0060517 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5551-2_0_6_load_109 | 91 | 0.0019037 | 0.00047712 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5551-2_0_6_load_113 | 92 | 0.0012384 | 0.00031037 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5551-2_0_6_load_162 | 93 | 0.0009061 | 0.00022709 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5551-2_0_6_load_145 | 94 | 0.00095819 | 0.00024015 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5551-2_0_6_load_63 | 95 | 0.0047981 | 0.0012025 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5551-2_0_6_load_64 | 96 | 0.0056655 | 0.0014199 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5551-2_0_6_load_66 | 98 | 0.001659 | 0.00041579 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5551-2_0_6_load_67 | 99 | 0.0051356 | 0.0012871 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5551-2_0_6_load_69 | 100 | 0.0014849 | 0.00037215 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5551-2_0_6_load_143 | 101 | 0.0026626 | 0.0006673 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5551-2_0_6_load_70 | 102 | 0.0047587 | 0.0011927 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5551-2_0_6_load_144 | 103 | 0.0012771 | 0.00032007 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5551-2_0_6_load_106 | 105 | 0.0026324 | 0.00065975 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5551-2_0_6_load_146 | 106 | 0.0024889 | 0.00062377 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5551-2_0_6_load_170 | 108 | 0.00078246 | 0.0001961 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5551-2_0_6_load_165 | 110 | 0.00023753 | 5.9531e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5551-2_0_6_load_84 | 111 | 0.0014587 | 0.00036559 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5551-2_0_6_load_75 | 112 | 0.0030595 | 0.00076677 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5551-2_0_6_load_76 | 113 | 0.00071198 | 0.00017844 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5551-2_0_6_load_78 | 114 | 0.014746 | 0.0036957 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5551-2_0_6_load_87 | 115 | 0.0021406 | 0.00053649 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5551-2_0_6_load_88 | 116 | 0.016593 | 0.0041586 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5551-2_0_6_load_89 | 117 | 0.018441 | 0.0046217 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5551-2_0_6_load_93 | 118 | 0.014262 | 0.0035743 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_5551-2_0_6_load_137 | 119 | 0.0083172 | 0.0020845 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_5551-2_0_6_load_130 | 120 | 0.0061986 | 0.0015535 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_5551-2_0_6_load_124 | 121 | 0.0057032 | 0.0014294 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_5551-2_0_6_load_129 | 123 | 0.019827 | 0.0049692 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_5551-2_0_6_load_94 | 124 | 0.0025913 | 0.00064944 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_5551-2_0_6_load_96 | 125 | 0.0016186 | 0.00040567 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_5551-2_0_6_load_98 | 126 | 0.00060669 | 0.00015205 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_5551-2_0_6_load_100 | 127 | 0.0045124 | 0.0011309 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_5551-2_0_6_load_101 | 128 | 0.019484 | 0.0048832 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_5551-2_0_6_load_132 | 129 | 0.01183 | 0.0029648 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_5551-2_0_6_load_102 | 131 | 0.016676 | 0.0041793 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_5551-2_0_6_load_103 | 132 | 0.0034387 | 0.00086181 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_5551-2_0_6_load_104 | 133 | 0.0029905 | 0.00074948 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_5551-2_0_6_load_105 | 134 | 0.0097696 | 0.0024485 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_5551-2_0_6_load_134 | 135 | 0.013368 | 0.0033503 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_5551-2_0_6_load_108 | 136 | 0.0028652 | 0.00071808 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_5551-2_0_6_load_139 | 137 | 0.00089726 | 0.00022488 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_5551-2_0_6_load_125 | 138 | 0.029477 | 0.0073877 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_5551-2_0_6_load_122 | 139 | 0.002882 | 0.0007223 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_5551-2_0_6_load_123 | 140 | 0.00097028 | 0.00024318 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_5551-2_0_6_load_128 | 141 | 0.023103 | 0.0057901 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_5551-2_0_6_load_135 | 142 | 0.013371 | 0.003351 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_5551-2_0_6_load_126 | 143 | 0.021223 | 0.005319 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_5551-2_0_6_load_131 | 144 | 0.0012903 | 0.00032338 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_5551-2_0_6_load_167 | 145 | 0.005522 | 0.0013839 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_5551-2_0_6_load_150 | 147 | 0.0010159 | 0.00025461 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_5551-2_0_6_load_153 | 149 | 0.00095396 | 0.00023908 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_5551-2_0_6_load_156 | 152 | 0.0012363 | 0.00030985 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_5551-2_0_6_load_152 | 153 | 0.0008168 | 0.00020471 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_5551-2_0_6_load_159 | 154 | 0.00066884 | 0.00016763 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_5551-2_0_6_load_160 | 155 | 0.00084167 | 0.00021094 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_5551-2_0_6_load_155 | 156 | 0.0027676 | 0.00069363 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_5551-2_0_6_load_161 | 157 | 0.00043517 | 0.00010906 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 86 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5551-2_0_6_line_0 |  | 0 | 1 | 0.029796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5551-2_0_6_line_1 |  | 0 | 2 | 0.01623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5551-2_0_6_line_2 |  | 1 | 3 | 0.029768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5551-2_0_6_line_3 |  | 2 | 4 | 0.0061525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5551-2_0_6_line_4 |  | 2 | 5 | 0.016633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5551-2_0_6_line_5 |  | 3 | 6 | 0.038328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5551-2_0_6_line_6 |  | 4 | 7 | 0.01819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5551-2_0_6_line_7 |  | 5 | 8 | 0.0023257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5551-2_0_6_line_8 |  | 6 | 9 | 0.02066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5551-2_0_6_line_9 |  | 7 | 10 | 0.013289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_5551-2_0_6_line_10 |  | 7 | 11 | 0.008409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5551-2_0_6_line_11 |  | 8 | 12 | 0.015834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5551-2_0_6_line_12 |  | 9 | 62 | 0.017169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5551-2_0_6_line_13 |  | 10 | 122 | 0.0078956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_5551-2_0_6_line_14 |  | 11 | 118 | 0.0095117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5551-2_0_6_line_15 |  | 11 | 116 | 0.018309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5551-2_0_6_line_16 |  | 12 | 111 | 0.0041982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5551-2_0_6_line_17 |  | 12 | 115 | 0.012919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5551-2_0_6_line_18 |  | 13 | 14 | 0.024194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5551-2_0_6_line_19 |  | 14 | 17 | 0.023929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5551-2_0_6_line_20 |  | 14 | 18 | 0.10746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_5551-2_0_6_line_21 |  | 14 | 19 | 0.022405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_5551-2_0_6_line_22 |  | 15 | 16 | 0.0093834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5551-2_0_6_line_23 |  | 16 | 20 | 0.005242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5551-2_0_6_line_24 |  | 16 | 21 | 0.017799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5551-2_0_6_line_25 |  | 17 | 22 | 0.025403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5551-2_0_6_line_26 |  | 17 | 23 | 0.014421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5551-2_0_6_line_27 |  | 18 | 24 | 0.032348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_5551-2_0_6_line_28 |  | 19 | 25 | 0.017283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_5551-2_0_6_line_29 |  | 20 | 26 | 0.034555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_5551-2_0_6_line_30 |  | 20 | 27 | 0.013657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_5551-2_0_6_line_31 |  | 21 | 28 | 0.019314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5551-2_0_6_line_32 |  | 22 | 29 | 0.094473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5551-2_0_6_line_33 |  | 23 | 30 | 0.027758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5551-2_0_6_line_34 |  | 24 | 31 | 0.020229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_5551-2_0_6_line_35 |  | 25 | 32 | 0.0020854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_5551-2_0_6_line_36 |  | 26 | 91 | 0.0098649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_5551-2_0_6_line_37 |  | 27 | 124 | 0.00077778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_5551-2_0_6_line_38 |  | 29 | 94 | 0.098239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5551-2_0_6_line_39 |  | 31 | 73 | 0.041068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_5551-2_0_6_line_40 |  | 31 | 70 | 0.017634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5551-2_0_6_line_41 |  | 32 | 137 | 0.0084731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_5551-2_0_6_line_42 |  | 33 | 34 | 0.005019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5551-2_0_6_line_43 |  | 33 | 35 | 0.054034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5551-2_0_6_line_44 |  | 35 | 36 | 0.013662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_5551-2_0_6_line_45 |  | 35 | 37 | 0.033934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_5551-2_0_6_line_46 |  | 36 | 38 | 0.10436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_5551-2_0_6_line_47 |  | 37 | 39 | 0.049863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_5551-2_0_6_line_48 |  | 38 | 48 | 0.053148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_5551-2_0_6_line_49 |  | 39 | 45 | 0.19251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_5551-2_0_6_line_50 |  | 39 | 44 | 0.047865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5551-2_0_6_line_51 |  | 40 | 41 | 0.16895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_5551-2_0_6_line_52 |  | 40 | 42 | 0.013235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5551-2_0_6_line_53 |  | 40 | 43 | 0.02979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_5551-2_0_6_line_54 |  | 41 | 58 | 0.033907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_5551-2_0_6_line_55 |  | 43 | 80 | 0.015338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_5551-2_0_6_line_56 |  | 45 | 46 | 0.13642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_5551-2_0_6_line_57 |  | 45 | 47 | 0.12624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5551-2_0_6_line_58 |  | 46 | 77 | 0.008764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_5551-2_0_6_line_59 |  | 47 | 78 | 0.010262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5551-2_0_6_line_60 |  | 48 | 74 | 0.054454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_5551-2_0_6_line_61 |  | 49 | 50 | 0.034036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5551-2_0_6_line_62 |  | 50 | 51 | 0.10777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_5551-2_0_6_line_63 |  | 50 | 52 | 0.064752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_5551-2_0_6_line_64 |  | 51 | 53 | 0.059908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5551-2_0_6_line_65 |  | 51 | 54 | 0.053742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_5551-2_0_6_line_66 |  | 52 | 55 | 0.027731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_5551-2_0_6_line_67 |  | 52 | 56 | 0.090349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5551-2_0_6_line_68 |  | 53 | 57 | 0.05217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5551-2_0_6_line_69 |  | 54 | 58 | 0.011974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_5551-2_0_6_line_70 |  | 55 | 59 | 0.034565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_5551-2_0_6_line_71 |  | 56 | 60 | 0.00106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5551-2_0_6_line_72 |  | 59 | 73 | 0.0046768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_5551-2_0_6_line_73 |  | 60 | 69 | 0.015824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5551-2_0_6_line_74 |  | 61 | 62 | 0.020699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5551-2_0_6_line_75 |  | 61 | 63 | 0.068483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5551-2_0_6_line_76 |  | 63 | 64 | 0.051302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5551-2_0_6_line_77 |  | 64 | 65 | 0.2597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5551-2_0_6_line_78 |  | 64 | 66 | 0.006518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5551-2_0_6_line_79 |  | 65 | 67 | 0.038191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5551-2_0_6_line_80 |  | 65 | 68 | 0.01481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5551-2_0_6_line_81 |  | 68 | 110 | 0.05507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5551-2_0_6_line_82 |  | 70 | 71 | 0.036307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5551-2_0_6_line_83 |  | 71 | 72 | 0.033245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_5551-2_0_6_line_84 |  | 74 | 75 | 0.0048953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_5551-2_0_6_line_85 |  | 74 | 76 | 0.048528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5551-2_0_6_line_86 |  | 75 | 79 | 0.00011187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_5551-2_0_6_line_87 |  | 77 | 146 | 0.043494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_5551-2_0_6_line_88 |  | 78 | 93 | 0.0080383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_5551-2_0_6_line_89 |  | 79 | 80 | 0.022764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_5551-2_0_6_line_90 |  | 81 | 82 | 0.017074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5551-2_0_6_line_91 |  | 82 | 85 | 0.007157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5551-2_0_6_line_92 |  | 83 | 84 | 0.016423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_5551-2_0_6_line_93 |  | 84 | 119 | 0.015785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5551-2_0_6_line_94 |  | 84 | 117 | 0.014926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_5551-2_0_6_line_95 |  | 85 | 86 | 0.026162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_5551-2_0_6_line_96 |  | 86 | 91 | 0.015827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_5551-2_0_6_line_97 |  | 87 | 88 | 0.0050695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_5551-2_0_6_line_98 |  | 88 | 92 | 0.022554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_5551-2_0_6_line_99 |  | 89 | 90 | 0.00014914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_5551-2_0_6_line_100 |  | 90 | 138 | 0.0035384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_5551-2_0_6_line_101 |  | 92 | 139 | 0.0088826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_5551-2_0_6_line_102 |  | 94 | 106 | 0.069166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_5551-2_0_6_line_103 |  | 95 | 96 | 0.021728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_5551-2_0_6_line_104 |  | 95 | 97 | 0.023693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_5551-2_0_6_line_105 |  | 96 | 98 | 0.014778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_5551-2_0_6_line_106 |  | 97 | 99 | 0.018783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_5551-2_0_6_line_107 |  | 97 | 100 | 0.0066911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_5551-2_0_6_line_108 |  | 98 | 101 | 0.0085827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_5551-2_0_6_line_109 |  | 99 | 102 | 0.0059251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_5551-2_0_6_line_110 |  | 100 | 103 | 0.0096861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_5551-2_0_6_line_111 |  | 101 | 104 | 0.00077445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_5551-2_0_6_line_112 |  | 103 | 105 | 0.012199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_5551-2_0_6_line_113 |  | 104 | 137 | 0.0055504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_5551-2_0_6_line_114 |  | 104 | 136 | 0.01573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_5551-2_0_6_line_115 |  | 105 | 133 | 0.0020756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
116 | LV_5551-2_0_6_line_116 |  | 106 | 145 | 0.16383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_5551-2_0_6_line_117 |  | 107 | 108 | 0.019929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_5551-2_0_6_line_118 |  | 107 | 109 | 0.013943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_5551-2_0_6_line_119 |  | 109 | 111 | 0.022136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_5551-2_0_6_line_120 |  | 112 | 113 | 0.025012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_5551-2_0_6_line_121 |  | 113 | 114 | 0.0083272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_5551-2_0_6_line_122 |  | 114 | 115 | 0.014901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_5551-2_0_6_line_123 |  | 116 | 117 | 0.0086327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_5551-2_0_6_line_124 |  | 118 | 120 | 0.023047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_5551-2_0_6_line_125 |  | 119 | 121 | 0.0071695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_5551-2_0_6_line_126 |  | 120 | 123 | 0.014835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_5551-2_0_6_line_127 |  | 121 | 140 | 0.007014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_5551-2_0_6_line_128 |  | 122 | 141 | 0.017749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_5551-2_0_6_line_129 |  | 122 | 142 | 0.0046188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_5551-2_0_6_line_130 |  | 123 | 144 | 0.0010426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_5551-2_0_6_line_131 |  | 124 | 125 | 0.01228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_5551-2_0_6_line_132 |  | 125 | 126 | 0.0087275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
133 | LV_5551-2_0_6_line_133 |  | 126 | 127 | 0.01379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
134 | LV_5551-2_0_6_line_134 |  | 127 | 128 | 0.018643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
135 | LV_5551-2_0_6_line_135 |  | 128 | 129 | 0.010696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
136 | LV_5551-2_0_6_line_136 |  | 129 | 130 | 0.0089947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
137 | LV_5551-2_0_6_line_137 |  | 130 | 142 | 0.021311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
138 | LV_5551-2_0_6_line_138 |  | 130 | 135 | 0.002726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
139 | LV_5551-2_0_6_line_139 |  | 131 | 132 | 0.0037307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
140 | LV_5551-2_0_6_line_140 |  | 131 | 133 | 0.009042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
141 | LV_5551-2_0_6_line_141 |  | 132 | 134 | 0.015051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
142 | LV_5551-2_0_6_line_142 |  | 134 | 135 | 0.0093467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
143 | LV_5551-2_0_6_line_143 |  | 138 | 143 | 0.013947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_5551-2_0_6_line_144 |  | 139 | 140 | 0.009821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_5551-2_0_6_line_145 |  | 141 | 143 | 0.0019573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_5551-2_0_6_line_146 |  | 146 | 147 | 0.026719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_5551-2_0_6_line_147 |  | 146 | 148 | 0.043964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_5551-2_0_6_line_148 |  | 147 | 149 | 0.013044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_5551-2_0_6_line_149 |  | 148 | 150 | 0.066586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_5551-2_0_6_line_150 |  | 148 | 151 | 0.053396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_5551-2_0_6_line_151 |  | 148 | 152 | 0.023902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_5551-2_0_6_line_152 |  | 149 | 153 | 0.02244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_5551-2_0_6_line_153 |  | 150 | 154 | 0.0092445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_5551-2_0_6_line_154 |  | 151 | 155 | 0.03789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_5551-2_0_6_line_155 |  | 152 | 156 | 0.02285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_5551-2_0_6_line_156 |  | 155 | 157 | 0.018508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5551-2_0_6_trafo_110 | 0.63 MVA 20/0.4 kV | 158 | 86 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2541503.7948 | 1187880.9276 | 2541509.0852 | 1187883.7518 | 2541515.8691 | 1187886.2868 | 2541525.771 | 1187888.6024 | 2541531.9839 | 1187890.0851
1 | 2541489.5883 | 1187873.081 | 2541499.7598 | 1187878.7736 | 2541503.7948 | 1187880.9276
2 | 2541559.9053 | 1187899.8415 | 2541551.7831 | 1187895.4073 | 2541543.9394 | 1187892.9382 | 2541531.9839 | 1187890.0851
3 | 2541489.5883 | 1187873.081 | 2541487.3074 | 1187867.3669
4 | 2541489.5883 | 1187873.081 | 2541493.1803 | 1187889.3217 | 2541493.1803 | 1187889.3217
5 | 2541559.9053 | 1187899.8415 | 2541591.2367 | 1187921.9178
6 | 2541480.123 | 1187850.7054 | 2541481.7374 | 1187855.8592 | 2541484.1178 | 1187860.5608 | 2541486.7415 | 1187865.9493 | 2541487.3074 | 1187867.3669
7 | 2541493.1803 | 1187889.3217 | 2541493.7556 | 1187891.5751
8 | 2541591.2367 | 1187921.9178 | 2541593.5818 | 1187923.5702 | 2541604.7039 | 1187932.0886 | 2541607.6539 | 1187934.4557
9 | 2541480.123 | 1187850.7054 | 2541472.3507 | 1187853.1941 | 2541467.608 | 1187855.1453
10 | 2541480.123 | 1187850.7054 | 2541481.552 | 1187847.0561 | 2541483.9637 | 1187843.2636
11 | 2541499.3661 | 1187906.3375 | 2541496.7314 | 1187900.6045 | 2541494.7828 | 1187895.5985 | 2541493.7556 | 1187891.5751
12 | 2541620.9711 | 1187945.2911 | 2541612.1776 | 1187938.0857 | 2541607.6539 | 1187934.4557
13 | 2541460.4791 | 1187858.5245 | 2541464.9045 | 1187856.2576 | 2541467.608 | 1187855.1453
14 | 2541483.9637 | 1187843.2636 | 2541480.4163 | 1187840.1521 | 2541476.4158 | 1187837.512
15 | 2541483.9637 | 1187843.2636 | 2541488.6671 | 1187835.8912 | 2541493.2227 | 1187827.4824
16 | 2541499.3661 | 1187906.3375 | 2541501.8377 | 1187909.7309
17 | 2541499.3661 | 1187906.3375 | 2541487.23 | 1187910.7672
18 | 2541278.2761 | 1187920.2135 | 2541283.7027 | 1187916.5915 | 2541293.1708 | 1187911.2399 | 2541299.2102 | 1187908.1279
19 | 2541278.2761 | 1187920.2135 | 2541260.5299 | 1187936.3192
20 | 2541278.2761 | 1187920.2135 | 2541272.3236 | 1187913.7906 | 2541244.9105 | 1187887.8898 | 2541238.5946 | 1187881.7595 | 2541232.3728 | 1187876.6733 | 2541227.0125 | 1187873.0684 | 2541217.0331 | 1187867.5523 | 2541206.2645 | 1187862.4554 | 2541198.6571 | 1187859.2061 | 2541192.9819 | 1187856.9484
21 | 2541278.2761 | 1187920.2135 | 2541285.0787 | 1187923.0816 | 2541293.4255 | 1187926.2903 | 2541299.2291 | 1187928.1047
22 | 2541357.5679 | 1187878.8893 | 2541351.0013 | 1187879.8432 | 2541348.4027 | 1187880.7367
23 | 2541357.5679 | 1187878.8893 | 2541359.1897 | 1187873.9039
24 | 2541357.5679 | 1187878.8893 | 2541358.7564 | 1187884.1695 | 2541360.6665 | 1187889.1203 | 2541366.0293 | 1187893.7592
25 | 2541241.3168 | 1187952.9842 | 2541249.4225 | 1187946.4119 | 2541260.5299 | 1187936.3192
26 | 2541260.5299 | 1187936.3192 | 2541264.1668 | 1187941.5531 | 2541267.4702 | 1187945.4451 | 2541269.575 | 1187947.5021
27 | 2541164.4252 | 1187841.9061 | 2541165.0688 | 1187842.316 | 2541174.4719 | 1187848.1823 | 2541183.8278 | 1187853.1264 | 2541191.0212 | 1187856.1684 | 2541192.9819 | 1187856.9484
28 | 2541316.0419 | 1187931.9509 | 2541312.6928 | 1187931.4263 | 2541305.7686 | 1187930.1491 | 2541299.2291 | 1187928.1047
29 | 2541359.1897 | 1187873.9039 | 2541365.706 | 1187861.5997 | 2541377.6378 | 1187844.7683
30 | 2541359.1897 | 1187873.9039 | 2541364.8194 | 1187876.2055 | 2541372.3806 | 1187876.657
31 | 2541366.0293 | 1187893.7592 | 2541380.3196 | 1187906.7518
32 | 2541241.3168 | 1187952.9842 | 2541235.2244 | 1187958.7029 | 2541185.3309 | 1188001.9071 | 2541180.1922 | 1187999.1117 | 2541167.8322 | 1187991.9848
33 | 2541292.3562 | 1187961.8655 | 2541287.4986 | 1187961.2795 | 2541283.8385 | 1187959.8925 | 2541278.1924 | 1187955.9235 | 2541269.575 | 1187947.5021
34 | 2541147.5159 | 1187830.8045 | 2541157.2997 | 1187837.3674 | 2541164.4252 | 1187841.9061
35 | 2541318.1022 | 1187932.2736 | 2541316.0419 | 1187931.9509
36 | 2541377.6378 | 1187844.7683 | 2541383.343 | 1187836.7204
37 | 2541372.3806 | 1187876.657 | 2541373.157 | 1187876.7033
38 | 2541167.8322 | 1187991.9848 | 2541158.3478 | 1187998.7487 | 2541124.4626 | 1188038.3493 | 2541119.5661 | 1188045.4238 | 2541117.1388 | 1188054.564 | 2541112.9247 | 1188058.1187 | 2541107.3688 | 1188057.1062 | 2541104.6621 | 1188052.6081
39 | 2541164.871 | 1187793.5681 | 2541147.5159 | 1187830.8045
40 | 2541147.5159 | 1187830.8045 | 2541139.0829 | 1187825.8403 | 2541132.4765 | 1187821.6024
41 | 2541326.5646 | 1187932.701 | 2541318.1022 | 1187932.2736 | 2541318.1022 | 1187932.2736
42 | 2541299.0997 | 1187411.5768 | 2541301.0326 | 1187416.2086
43 | 2541269.451 | 1187367.0867 | 2541280.8685 | 1187378.3364 | 2541288.3573 | 1187389.647 | 2541293.4463 | 1187398.9801 | 2541297.2653 | 1187407.1806 | 2541299.0997 | 1187411.5768
44 | 2541269.451 | 1187367.0867 | 2541275.7405 | 1187354.9513
45 | 2541269.451 | 1187367.0867 | 2541252.5875 | 1187396.5337
46 | 2541275.7405 | 1187354.9513 | 2541285.8106 | 1187359.5328 | 2541308.6083 | 1187368.9364 | 2541372.87 | 1187393.0488
47 | 2541227.8078 | 1187439.8039 | 2541252.5875 | 1187396.5337
48 | 2541422.6302 | 1187411.7199 | 2541372.87 | 1187393.0488
49 | 2541047.7095 | 1187372.5838 | 2541057.2317 | 1187376.5143 | 2541085.7141 | 1187386.7393 | 2541102.4835 | 1187392.922 | 2541117.755 | 1187398.8527 | 2541167.8027 | 1187421.1947 | 2541179.9627 | 1187425.7221 | 2541195.2363 | 1187431.0971 | 2541209.3487 | 1187434.7825 | 2541227.8078 | 1187439.8039
50 | 2541227.8078 | 1187439.8039 | 2541241.9221 | 1187444.4566 | 2541256.0608 | 1187449.2648 | 2541273.0285 | 1187455.4794
51 | 2541389.6028 | 1187534.6022 | 2541384.0534 | 1187545.1848 | 2541371.9822 | 1187573.7639 | 2541361.0922 | 1187599.8744 | 2541349.7354 | 1187626.5898 | 2541338.798 | 1187653.2901 | 2541328.0986 | 1187678.5761 | 2541322.8763 | 1187689.8115
52 | 2541389.6028 | 1187534.6022 | 2541401.0379 | 1187541.2659
53 | 2541389.6028 | 1187534.6022 | 2541391.1261 | 1187528.8951 | 2541397.2218 | 1187505.8032
54 | 2541322.8763 | 1187689.8115 | 2541303.4145 | 1187676.5951 | 2541294.8013 | 1187670.7997
55 | 2541401.1366 | 1187490.9732 | 2541397.2218 | 1187505.8032
56 | 2541047.7095 | 1187372.5838 | 2541031.7762 | 1187364.5475 | 2541012.9272 | 1187352.5267 | 2540934.9896 | 1187296.0988
57 | 2541047.7095 | 1187372.5838 | 2541039.6147 | 1187393.4532 | 2540990.2161 | 1187456.2096 | 2540983.1651 | 1187464.5506 | 2540979.3018 | 1187473.5272 | 2540978.4654 | 1187476.7157
58 | 2540927.8908 | 1187290.9592 | 2540934.9896 | 1187296.0988
59 | 2540978.4654 | 1187476.7157 | 2540977.0593 | 1187482.0764 | 2540977.3794 | 1187486.7853
60 | 2541422.6302 | 1187411.7199 | 2541410.3342 | 1187458.6559 | 2541408.9183 | 1187464.4175
61 | 2541175.6276 | 1187693.6166 | 2541171.842 | 1187694.232 | 2541152.5919 | 1187690.1525 | 2541142.4465 | 1187687.3576
62 | 2541175.6276 | 1187693.6166 | 2541205.8912 | 1187702.0681 | 2541212.816 | 1187686.3244 | 2541216.6372 | 1187678.4712 | 2541233.9083 | 1187642.6922 | 2541240.2781 | 1187634.1136
63 | 2541175.6276 | 1187693.6166 | 2541205.8912 | 1187702.0681 | 2541202.5475 | 1187711.1394 | 2541193.0491 | 1187732.8118
64 | 2541189.8346 | 1187601.5802 | 2541225.1053 | 1187624.1794 | 2541240.2781 | 1187634.1136
65 | 2541240.2781 | 1187634.1136 | 2541284.8666 | 1187664.1151
66 | 2541193.0491 | 1187732.8118 | 2541181.3815 | 1187757.9688
67 | 2541193.0491 | 1187732.8118 | 2541246.2416 | 1187761.8385 | 2541250.3112 | 1187764.5111 | 2541252.0735 | 1187766.8396 | 2541252.3051 | 1187770.217 | 2541251.2129 | 1187774.7414 | 2541244.513 | 1187786.9465
68 | 2541158.1701 | 1187643.0487 | 2541163.2219 | 1187636.2062 | 2541169.3943 | 1187629.2859 | 2541180.5738 | 1187614.8566 | 2541189.8346 | 1187601.5802
69 | 2541294.8013 | 1187670.7997 | 2541284.8666 | 1187664.1151
70 | 2541166.8387 | 1187789.3253 | 2541181.3815 | 1187757.9688
71 | 2541244.513 | 1187786.9465 | 2541244.0029 | 1187787.8757
72 | 2541164.871 | 1187793.5681 | 2541166.8387 | 1187789.3253
73 | 2541236.3885 | 1187801.7469 | 2541244.0029 | 1187787.8757
74 | 2541620.9711 | 1187945.2911 | 2541636.9815 | 1187958.4101
75 | 2541690.708 | 1188000.6433 | 2541684.5646 | 1187997.2791 | 2541681.71 | 1187995.5616 | 2541678.2881 | 1187992.7823 | 2541664.86 | 1187981.6737 | 2541653.259 | 1187971.748 | 2541636.9815 | 1187958.4101
76 | 2541690.708 | 1188000.6433 | 2541697.8254 | 1188004.5428 | 2541700.8774 | 1188006.9477 | 2541703.5768 | 1188009.9564 | 2541704.9507 | 1188013.1559 | 2541705.5989 | 1188017.0407 | 2541705.5313 | 1188022.6223 | 2541704.488 | 1188025.9343 | 2541702.7287 | 1188029.3645 | 2541700.8831 | 1188031.7617 | 2541697.5068 | 1188034.4295 | 2541694.2116 | 1188036.0292 | 2541690.3225 | 1188036.9565
77 | 2541690.3225 | 1188036.9565 | 2541692.7928 | 1188046.9826 | 2541693.3173 | 1188060.0738 | 2541694.6236 | 1188094.6473 | 2541694.7526 | 1188107.8646 | 2541694.3575 | 1188111.9263 | 2541693.0506 | 1188114.8074 | 2541691.4771 | 1188123.1941 | 2541688.2101 | 1188133.9321 | 2541686.1112 | 1188138.5107 | 2541682.4461 | 1188145.1836 | 2541656.9819 | 1188192.0031 | 2541651.5115 | 1188202.0622 | 2541638.3173 | 1188221.8801 | 2541622.6914 | 1188232.4943 | 2541588.4364 | 1188253.174 | 2541587.4691 | 1188254.1063
78 | 2541690.3225 | 1188036.9565 | 2541683.9807 | 1188036.7072 | 2541683.8123 | 1188036.6758
79 | 2541587.4691 | 1188254.1063 | 2541595.2044 | 1188255.6871 | 2541605.8619 | 1188262.787 | 2541616.4874 | 1188276.7578
80 | 2541576.7756 | 1188264.3833 | 2541587.4691 | 1188254.1063
81 | 2541576.7756 | 1188264.3833 | 2541592.9568 | 1188267.6603 | 2541603.4876 | 1188274.2945 | 2541608.0627 | 1188281.8985 | 2541608.9514 | 1188291.6621 | 2541605.5759 | 1188298.2877
82 | 2541100.8875 | 1187803.7174 | 2541102.4612 | 1187804.6335 | 2541115.6145 | 1187811.7079 | 2541131.5897 | 1187821.0336 | 2541132.4765 | 1187821.6024
83 | 2541072.1842 | 1187786.9435 | 2541079.1354 | 1187791.0557 | 2541100.8875 | 1187803.7174
84 | 2541408.9183 | 1187464.4175 | 2541408.3531 | 1187465.1346 | 2541407.6945 | 1187466.4418 | 2541406.9853 | 1187468.8056 | 2541406.9724 | 1187468.8545
85 | 2541408.9183 | 1187464.4175 | 2541409.951 | 1187463.9182 | 2541411.1947 | 1187463.9394 | 2541413.144 | 1187464.3205 | 2541417.6445 | 1187465.7994 | 2541454.4065 | 1187480.0119
86 | 2541406.9724 | 1187468.8545 | 2541406.9439 | 1187468.9627
87 | 2540893.3573 | 1187264.5357 | 2540913.1593 | 1187280.2933 | 2540927.8908 | 1187290.9592
88 | 2540978.5484 | 1187494.7138 | 2540977.6484 | 1187490.7422 | 2540977.3794 | 1187486.7853
89 | 2541401.1366 | 1187490.9732 | 2541404.4108 | 1187478.5697 | 2541406.9439 | 1187468.9627
90 | 2541411.2579 | 1187796.2937 | 2541404.3237 | 1187789.3467 | 2541399.9959 | 1187783.5197
91 | 2541411.2579 | 1187796.2937 | 2541407.626 | 1187802.4662
92 | 2541503.9115 | 1187806.492 | 2541511.3268 | 1187791.8386
93 | 2541503.9115 | 1187806.492 | 2541493.1031 | 1187797.3148 | 2541491.9781 | 1187796.1684
94 | 2541503.9115 | 1187806.492 | 2541497.2765 | 1187819.8618
95 | 2541407.626 | 1187802.4662 | 2541392.4961 | 1187823.8088
96 | 2541383.343 | 1187836.7204 | 2541392.4961 | 1187823.8088
97 | 2541441.3845 | 1187767.4251 | 2541441.3988 | 1187767.4153 | 2541446.3237 | 1187766.2886 | 2541446.3237 | 1187766.2886
98 | 2541446.3237 | 1187766.2886 | 2541451.6651 | 1187767.9595 | 2541463.0278 | 1187772.9621 | 2541467.1121 | 1187774.9489
99 | 2541433.0364 | 1187833.4347 | 2541433.1452 | 1187833.5366
100 | 2541435.7281 | 1187835.955 | 2541433.1452 | 1187833.5366
101 | 2541474.6313 | 1187779.6624 | 2541472.4774 | 1187778.1392 | 2541467.6654 | 1187775.218 | 2541467.1121 | 1187774.9489
102 | 2541104.6621 | 1188052.6081 | 2541042.2739 | 1188082.4695
103 | 2541377.8958 | 1187934.1837 | 2541375.8337 | 1187934.3305 | 2541368.8961 | 1187934.7877 | 2541361.6945 | 1187934.7805 | 2541356.2006 | 1187934.4102
104 | 2541401.5372 | 1187933.011 | 2541391.8562 | 1187932.9948 | 2541383.9908 | 1187933.7501 | 2541377.8958 | 1187934.1837
105 | 2541356.2006 | 1187934.4102 | 2541350.3202 | 1187934.0139 | 2541341.4492 | 1187933.5256
106 | 2541401.5372 | 1187933.011 | 2541400.2671 | 1187936.5143 | 2541399.1599 | 1187940.3051 | 2541398.2349 | 1187946.3287 | 2541396.8233 | 1187951.139
107 | 2541401.5372 | 1187933.011 | 2541406.1375 | 1187928.1522
108 | 2541341.4492 | 1187933.5256 | 2541339.0083 | 1187933.3913 | 2541332.881 | 1187933.0269
109 | 2541396.8233 | 1187951.139 | 2541395.1549 | 1187956.8244
110 | 2541413.0406 | 1187921.3577 | 2541406.2865 | 1187927.9949 | 2541406.1375 | 1187928.1522
111 | 2541332.1079 | 1187932.981 | 2541332.881 | 1187933.0269
112 | 2541421.4064 | 1187912.4875 | 2541416.434 | 1187918.0231 | 2541413.0406 | 1187921.3577
113 | 2541332.1079 | 1187932.981 | 2541326.5646 | 1187932.701
114 | 2541332.1079 | 1187932.981 | 2541332.4558 | 1187931.1209 | 2541333.7459 | 1187928.8737 | 2541337.3035 | 1187924.4807 | 2541341.71 | 1187921.0353
115 | 2541421.4064 | 1187912.4875 | 2541422.7934 | 1187910.9434
116 | 2541042.2739 | 1188082.4695 | 2541050.3033 | 1188246.0983
117 | 2541547.0644 | 1187927.7274 | 2541540.9834 | 1187924.5184 | 2541538.8201 | 1187924.0726 | 2541536.359 | 1187922.8182 | 2541533.9489 | 1187923.6533 | 2541532.4709 | 1187925.4132 | 2541531.0809 | 1187928.373
118 | 2541517.4266 | 1187925.3715 | 2541523.3891 | 1187926.6028 | 2541526.0725 | 1187927.188 | 2541531.0809 | 1187928.373
119 | 2541517.4266 | 1187925.3715 | 2541512.3723 | 1187921.063 | 2541508.81 | 1187917.1957 | 2541503.2092 | 1187911.614 | 2541501.8377 | 1187909.7309
120 | 2541467.6385 | 1187947.6382 | 2541467.212 | 1187943.0398 | 2541468.0633 | 1187935.7162 | 2541469.3054 | 1187927.7884 | 2541469.9101 | 1187922.8289
121 | 2541473.2319 | 1187915.8765 | 2541473.2319 | 1187915.8765 | 2541471.0024 | 1187917.2436 | 2541470.3151 | 1187919.5072 | 2541469.9101 | 1187922.8289
122 | 2541473.2319 | 1187915.8765 | 2541487.23 | 1187910.7672
123 | 2541493.2227 | 1187827.4824 | 2541496.4602 | 1187821.5067 | 2541497.2765 | 1187819.8618
124 | 2541476.4158 | 1187837.512 | 2541476.4158 | 1187837.512 | 2541473.6933 | 1187836.0601 | 2541471.0526 | 1187833.6068 | 2541465.4211 | 1187828.7926 | 2541459.1506 | 1187822.606 | 2541459.0477 | 1187822.5118
125 | 2541491.9781 | 1187796.1684 | 2541486.9564 | 1187791.0513
126 | 2541448.1034 | 1187812.4972 | 2541459.0477 | 1187822.5118
127 | 2541486.9564 | 1187791.0513 | 2541482.0436 | 1187786.0452
128 | 2541460.4791 | 1187858.5245 | 2541451.3445 | 1187849.6645 | 2541450.2883 | 1187847.7626 | 2541448.0811 | 1187845.9635
129 | 2541460.4791 | 1187858.5245 | 2541456.5124 | 1187860.8907
130 | 2541447.3343 | 1187811.7934 | 2541448.1034 | 1187812.4972
131 | 2541373.157 | 1187876.7033 | 2541385.4154 | 1187877.4352
132 | 2541385.4154 | 1187877.4352 | 2541390.4061 | 1187877.7332 | 2541393.1287 | 1187876.8616 | 2541393.6039 | 1187876.1339
133 | 2541393.6039 | 1187876.1339 | 2541394.1809 | 1187875.2504 | 2541395.003 | 1187873.508 | 2541396.3606 | 1187871.1378 | 2541398.5413 | 1187870.2492 | 2541404.2051 | 1187871.0626
134 | 2541422.7768 | 1187872.1855 | 2541411.0778 | 1187872.0495 | 2541404.2051 | 1187871.0626
135 | 2541433.3859 | 1187873.2496 | 2541431.6139 | 1187872.7598 | 2541424.0483 | 1187872.2003 | 2541422.7768 | 1187872.1855
136 | 2541441.9224 | 1187876.0718 | 2541435.6146 | 1187873.8656 | 2541433.3859 | 1187873.2496
137 | 2541441.9224 | 1187876.0718 | 2541442.4536 | 1187875.0104 | 2541445.9282 | 1187869.9179 | 2541449.924 | 1187865.8542 | 2541455.1548 | 1187861.7006 | 2541456.5124 | 1187860.8907
138 | 2541441.9224 | 1187876.0718 | 2541440.7095 | 1187878.5131
139 | 2541428.0129 | 1187903.5808 | 2541430.0699 | 1187900.4684 | 2541430.0699 | 1187900.4684
140 | 2541428.0129 | 1187903.5808 | 2541424.1313 | 1187909.4539 | 2541422.7934 | 1187910.9434
141 | 2541436.589 | 1187886.9023 | 2541430.0699 | 1187900.4684
142 | 2541440.7095 | 1187878.5131 | 2541437.9873 | 1187883.9926 | 2541436.589 | 1187886.9023
143 | 2541435.7281 | 1187835.955 | 2541436.8553 | 1187837.0104 | 2541442.2827 | 1187841.2374 | 2541446.5639 | 1187844.7269
144 | 2541474.6313 | 1187779.6624 | 2541478.3849 | 1187782.317 | 2541482.0436 | 1187786.0452
145 | 2541446.5639 | 1187844.7269 | 2541448.0811 | 1187845.9635
146 | 2540893.3573 | 1187264.5357 | 2540882.605 | 1187288.9957
147 | 2540862.7932 | 1187232.9423 | 2540868.4781 | 1187238.4225 | 2540893.3573 | 1187264.5357
148 | 2540882.605 | 1187288.9957 | 2540877.356 | 1187300.9367
149 | 2540862.7932 | 1187232.9423 | 2540845.902 | 1187215.2995 | 2540826.5503 | 1187252.7567
150 | 2540823.9398 | 1187196.4061 | 2540845.902 | 1187215.2995 | 2540862.7932 | 1187232.9423
151 | 2540862.7932 | 1187232.9423 | 2540853.8102 | 1187255.0916
152 | 2540868.3256 | 1187321.4799 | 2540877.356 | 1187300.9367
153 | 2540826.5503 | 1187252.7567 | 2540818.4826 | 1187248.2432
154 | 2540823.9398 | 1187196.4061 | 2540803.4067 | 1187228.2497
155 | 2540840.4287 | 1187265.196 | 2540848.4562 | 1187268.2931 | 2540853.8102 | 1187255.0916
156 | 2540807.1909 | 1187243.1985 | 2540803.5933 | 1187238.9428 | 2540799.8643 | 1187233.7435 | 2540803.4067 | 1187228.2497

## bus_geodata
| x | y | coords
0 | 2541503.7948 | 1187880.9276
1 | 2541531.9839 | 1187890.0851
2 | 2541489.5883 | 1187873.081
3 | 2541559.9053 | 1187899.8415
4 | 2541487.3074 | 1187867.3669
5 | 2541493.1803 | 1187889.3217
6 | 2541591.2367 | 1187921.9178
7 | 2541480.123 | 1187850.7054
8 | 2541493.7556 | 1187891.5751
9 | 2541607.6539 | 1187934.4557
10 | 2541467.608 | 1187855.1453
11 | 2541483.9637 | 1187843.2636
12 | 2541499.3661 | 1187906.3375
13 | 2541299.2102 | 1187908.1279
14 | 2541278.2761 | 1187920.2135
15 | 2541348.4027 | 1187880.7367
16 | 2541357.5679 | 1187878.8893
17 | 2541260.5299 | 1187936.3192
18 | 2541192.9819 | 1187856.9484
19 | 2541299.2291 | 1187928.1047
20 | 2541359.1897 | 1187873.9039
21 | 2541366.0293 | 1187893.7592
22 | 2541241.3168 | 1187952.9842
23 | 2541269.575 | 1187947.5021
24 | 2541164.4252 | 1187841.9061
25 | 2541316.0419 | 1187931.9509
26 | 2541377.6378 | 1187844.7683
27 | 2541372.3806 | 1187876.657
28 | 2541380.3196 | 1187906.7518
29 | 2541167.8322 | 1187991.9848
30 | 2541292.3562 | 1187961.8655
31 | 2541147.5159 | 1187830.8045
32 | 2541318.1022 | 1187932.2736
33 | 2541299.0997 | 1187411.5768
34 | 2541301.0326 | 1187416.2086
35 | 2541269.451 | 1187367.0867
36 | 2541275.7405 | 1187354.9513
37 | 2541252.5875 | 1187396.5337
38 | 2541372.87 | 1187393.0488
39 | 2541227.8078 | 1187439.8039
40 | 2541389.6028 | 1187534.6022
41 | 2541322.8763 | 1187689.8115
42 | 2541401.0379 | 1187541.2659
43 | 2541397.2218 | 1187505.8032
44 | 2541273.0285 | 1187455.4794
45 | 2541047.7095 | 1187372.5838
46 | 2540934.9896 | 1187296.0988
47 | 2540978.4654 | 1187476.7157
48 | 2541422.6302 | 1187411.7199
49 | 2541142.4465 | 1187687.3576
50 | 2541175.6276 | 1187693.6166
51 | 2541240.2781 | 1187634.1136
52 | 2541193.0491 | 1187732.8118
53 | 2541189.8346 | 1187601.5802
54 | 2541284.8666 | 1187664.1151
55 | 2541181.3815 | 1187757.9688
56 | 2541244.513 | 1187786.9465
57 | 2541158.1701 | 1187643.0487
58 | 2541294.8013 | 1187670.7997
59 | 2541166.8387 | 1187789.3253
60 | 2541244.0029 | 1187787.8757
61 | 2541636.9815 | 1187958.4101
62 | 2541620.9711 | 1187945.2911
63 | 2541690.708 | 1188000.6433
64 | 2541690.3225 | 1188036.9565
65 | 2541587.4691 | 1188254.1063
66 | 2541683.8123 | 1188036.6758
67 | 2541616.4874 | 1188276.7578
68 | 2541576.7756 | 1188264.3833
69 | 2541236.3885 | 1187801.7469
70 | 2541132.4765 | 1187821.6024
71 | 2541100.8875 | 1187803.7174
72 | 2541072.1842 | 1187786.9435
73 | 2541164.871 | 1187793.5681
74 | 2541408.9183 | 1187464.4175
75 | 2541406.9724 | 1187468.8545
76 | 2541454.4065 | 1187480.0119
77 | 2540927.8908 | 1187290.9592
78 | 2540977.3794 | 1187486.7853
79 | 2541406.9439 | 1187468.9627
80 | 2541401.1366 | 1187490.9732
81 | 2541399.9959 | 1187783.5197
82 | 2541411.2579 | 1187796.2937
83 | 2541511.3268 | 1187791.8386
84 | 2541503.9115 | 1187806.492
85 | 2541407.626 | 1187802.4662
86 | 2541392.4961 | 1187823.8088
87 | 2541441.3845 | 1187767.4251
88 | 2541446.3237 | 1187766.2886
89 | 2541433.0364 | 1187833.4347
90 | 2541433.1452 | 1187833.5366
91 | 2541383.343 | 1187836.7204
92 | 2541467.1121 | 1187774.9489
93 | 2540978.5484 | 1187494.7138
94 | 2541104.6621 | 1188052.6081
95 | 2541377.8958 | 1187934.1837
96 | 2541356.2006 | 1187934.4102
97 | 2541401.5372 | 1187933.011
98 | 2541341.4492 | 1187933.5256
99 | 2541396.8233 | 1187951.139
100 | 2541406.1375 | 1187928.1522
101 | 2541332.881 | 1187933.0269
102 | 2541395.1549 | 1187956.8244
103 | 2541413.0406 | 1187921.3577
104 | 2541332.1079 | 1187932.981
105 | 2541421.4064 | 1187912.4875
106 | 2541042.2739 | 1188082.4695
107 | 2541531.0809 | 1187928.373
108 | 2541547.0644 | 1187927.7274
109 | 2541517.4266 | 1187925.3715
110 | 2541605.5759 | 1188298.2877
111 | 2541501.8377 | 1187909.7309
112 | 2541467.6385 | 1187947.6382
113 | 2541469.9101 | 1187922.8289
114 | 2541473.2319 | 1187915.8765
115 | 2541487.23 | 1187910.7672
116 | 2541493.2227 | 1187827.4824
117 | 2541497.2765 | 1187819.8618
118 | 2541476.4158 | 1187837.512
119 | 2541491.9781 | 1187796.1684
120 | 2541459.0477 | 1187822.5118
121 | 2541486.9564 | 1187791.0513
122 | 2541460.4791 | 1187858.5245
123 | 2541448.1034 | 1187812.4972
124 | 2541373.157 | 1187876.7033
125 | 2541385.4154 | 1187877.4352
126 | 2541393.6039 | 1187876.1339
127 | 2541404.2051 | 1187871.0626
128 | 2541422.7768 | 1187872.1855
129 | 2541433.3859 | 1187873.2496
130 | 2541441.9224 | 1187876.0718
131 | 2541428.0129 | 1187903.5808
132 | 2541430.0699 | 1187900.4684
133 | 2541422.7934 | 1187910.9434
134 | 2541436.589 | 1187886.9023
135 | 2541440.7095 | 1187878.5131
136 | 2541341.71 | 1187921.0353
137 | 2541326.5646 | 1187932.701
138 | 2541435.7281 | 1187835.955
139 | 2541474.6313 | 1187779.6624
140 | 2541482.0436 | 1187786.0452
141 | 2541448.0811 | 1187845.9635
142 | 2541456.5124 | 1187860.8907
143 | 2541446.5639 | 1187844.7269
144 | 2541447.3343 | 1187811.7934
145 | 2541050.3033 | 1188246.0983
146 | 2540893.3573 | 1187264.5357
147 | 2540882.605 | 1187288.9957
148 | 2540862.7932 | 1187232.9423
149 | 2540877.356 | 1187300.9367
150 | 2540826.5503 | 1187252.7567
151 | 2540823.9398 | 1187196.4061
152 | 2540853.8102 | 1187255.0916
153 | 2540868.3256 | 1187321.4799
154 | 2540818.4826 | 1187248.2432
155 | 2540803.4067 | 1187228.2497
156 | 2540840.4287 | 1187265.196
157 | 2540807.1909 | 1187243.1985
158 | 2541407.626 | 1187802.4662

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1