## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5604-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5604-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5604-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5604-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5604-5_0_4_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_5604-5_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_5604-5_0_4_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_5604-5_0_4_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_5604-5_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_5604-5_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_5604-5_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_5604-5_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_5604-5_0_4_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_5604-5_0_4_node_71 | 0.4 | n |  | TRUE
14 | bus_LV_5604-5_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_5604-5_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_5604-5_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_5604-5_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_5604-5_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_5604-5_0_4_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_5604-5_0_4_node_69 | 0.4 | n |  | TRUE
21 | bus_LV_5604-5_0_4_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_5604-5_0_4_node_68 | 0.4 | n |  | TRUE
23 | bus_LV_5604-5_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_5604-5_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_5604-5_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_5604-5_0_4_node_49 | 0.4 | n |  | TRUE
27 | bus_LV_5604-5_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_5604-5_0_4_node_50 | 0.4 | n |  | TRUE
29 | bus_LV_5604-5_0_4_node_54 | 0.4 | n |  | TRUE
30 | bus_LV_5604-5_0_4_node_51 | 0.4 | n |  | TRUE
31 | bus_LV_5604-5_0_4_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_5604-5_0_4_node_57 | 0.4 | n |  | TRUE
33 | bus_LV_5604-5_0_4_node_62 | 0.4 | n |  | TRUE
34 | bus_LV_5604-5_0_4_node_56 | 0.4 | n |  | TRUE
35 | bus_LV_5604-5_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_5604-5_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_5604-5_0_4_node_98 | 0.4 | n |  | TRUE
38 | bus_LV_5604-5_0_4_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_5604-5_0_4_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_5604-5_0_4_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_5604-5_0_4_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_5604-5_0_4_node_83 | 0.4 | n |  | TRUE
43 | bus_LV_5604-5_0_4_node_84 | 0.4 | n |  | TRUE
44 | bus_LV_5604-5_0_4_node_85 | 0.4 | n |  | TRUE
45 | bus_LV_5604-5_0_4_node_86 | 0.4 | n |  | TRUE
46 | bus_LV_5604-5_0_4_node_90 | 0.4 | n |  | TRUE
47 | bus_LV_5604-5_0_4_node_89 | 0.4 | n |  | TRUE
48 | bus_LV_5604-5_0_4_node_88 | 0.4 | n |  | TRUE
49 | bus_LV_5604-5_0_4_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_5604-5_0_4_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_5604-5_0_4_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_5604-5_0_4_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_5604-5_0_4_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_5604-5_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_5604-5_0_4_node_44 | 0.4 | n |  | TRUE
56 | bus_LV_5604-5_0_4_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_5604-5_0_4_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_5604-5_0_4_node_39 | 0.4 | n |  | TRUE
59 | bus_LV_5604-5_0_4_node_41 | 0.4 | n |  | TRUE
60 | bus_LV_5604-5_0_4_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_5604-5_0_4_node_97 | 0.4 | n |  | TRUE
62 | bus_LV_5604-5_0_4_node_96 | 0.4 | n |  | TRUE
63 | bus_LV_5604-5_0_4_node_55 | 0.4 | n |  | TRUE
64 | bus_LV_5604-5_0_4_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_5604-5_0_4_node_53 | 0.4 | n |  | TRUE
66 | bus_LV_5604-5_0_4_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_5604-5_0_4_node_64 | 0.4 | n |  | TRUE
68 | bus_LV_5604-5_0_4_node_60 | 0.4 | n |  | TRUE
69 | bus_LV_5604-5_0_4_node_59 | 0.4 | n |  | TRUE
70 | bus_LV_5604-5_0_4_node_61 | 0.4 | n |  | TRUE
71 | bus_LV_5604-5_0_4_node_63 | 0.4 | n |  | TRUE
72 | bus_LV_5604-5_0_4_node_65 | 0.4 | n |  | TRUE
73 | bus_LV_5604-5_0_4_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_5604-5_0_4_node_66 | 0.4 | n |  | TRUE
75 | bus_LV_5604-5_0_4_node_67 | 0.4 | n |  | TRUE
76 | bus_LV_5604-5_0_4_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_5604-5_0_4_node_121 | 0.4 | n |  | TRUE
78 | bus_LV_5604-5_0_4_node_87 | 0.4 | n |  | TRUE
79 | bus_LV_5604-5_0_4_node_122 | 0.4 | n |  | TRUE
80 | bus_LV_5604-5_0_4_node_91 | 0.4 | n |  | TRUE
81 | bus_LV_5604-5_0_4_node_92 | 0.4 | n |  | TRUE
82 | bus_LV_5604-5_0_4_node_93 | 0.4 | n |  | TRUE
83 | bus_LV_5604-5_0_4_node_94 | 0.4 | n |  | TRUE
84 | bus_LV_5604-5_0_4_node_95 | 0.4 | n |  | TRUE
85 | bus_LV_5604-5_0_4_node_116 | 0.4 | n |  | TRUE
86 | bus_LV_5604-5_0_4_node_115 | 0.4 | n |  | TRUE
87 | bus_LV_5604-5_0_4_node_117 | 0.4 | n |  | TRUE
88 | bus_LV_5604-5_0_4_node_118 | 0.4 | n |  | TRUE
89 | bus_LV_5604-5_0_4_node_130 | 0.4 | n |  | TRUE
90 | bus_LV_5604-5_0_4_node_119 | 0.4 | n |  | TRUE
91 | bus_LV_5604-5_0_4_node_120 | 0.4 | n |  | TRUE
92 | bus_LV_5604-5_0_4_node_170 | 0.4 | n |  | TRUE
93 | bus_LV_5604-5_0_4_node_173 | 0.4 | n |  | TRUE
94 | bus_LV_5604-5_0_4_node_133 | 0.4 | n |  | TRUE
95 | bus_LV_5604-5_0_4_node_171 | 0.4 | n |  | TRUE
96 | bus_LV_5604-5_0_4_node_169 | 0.4 | n |  | TRUE
97 | bus_LV_5604-5_0_4_node_174 | 0.4 | n |  | TRUE
98 | bus_LV_5604-5_0_4_node_165 | 0.4 | n |  | TRUE
99 | bus_LV_5604-5_0_4_node_166 | 0.4 | n |  | TRUE
100 | bus_LV_5604-5_0_4_node_164 | 0.4 | n |  | TRUE
101 | bus_LV_5604-5_0_4_node_168 | 0.4 | n |  | TRUE
102 | bus_LV_5604-5_0_4_node_167 | 0.4 | n |  | TRUE
103 | bus_LV_5604-5_0_4_node_181 | 0.4 | n |  | TRUE
104 | bus_MV_366_0_node_9 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5604-5_0_4_load_0 | 0 | 0.021433 | 0.0053717 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5604-5_0_4_load_2 | 2 | 0.020543 | 0.0051486 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5604-5_0_4_load_3 | 3 | 0.003255 | 0.00081577 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5604-5_0_4_load_19 | 6 | 0.020419 | 0.0051176 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5604-5_0_4_load_14 | 7 | 0.010603 | 0.0026573 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5604-5_0_4_load_8 | 8 | 0.0078323 | 0.001963 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5604-5_0_4_load_4 | 9 | 0.0050685 | 0.0012703 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5604-5_0_4_load_5 | 10 | 0.013758 | 0.0034481 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5604-5_0_4_load_7 | 11 | 0.0075383 | 0.0018893 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5604-5_0_4_load_20 | 12 | 0.005517 | 0.0013827 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5604-5_0_4_load_71 | 13 | 0.0078108 | 0.0019576 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5604-5_0_4_load_9 | 16 | 0.015749 | 0.003947 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5604-5_0_4_load_10 | 17 | 0.0097028 | 0.0024318 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5604-5_0_4_load_11 | 18 | 0.0096953 | 0.0024299 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5604-5_0_4_load_24 | 21 | 0.0038858 | 0.00097387 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5604-5_0_4_load_18 | 25 | 0.014825 | 0.0037154 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5604-5_0_4_load_49 | 26 | 0.010302 | 0.002582 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5604-5_0_4_load_54 | 29 | 0.012099 | 0.0030324 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5604-5_0_4_load_51 | 30 | 0.012106 | 0.0030341 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5604-5_0_4_load_35 | 31 | 0.011325 | 0.0028384 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5604-5_0_4_load_22 | 35 | 0.0042769 | 0.0010719 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5604-5_0_4_load_23 | 36 | 0.0023677 | 0.00059339 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5604-5_0_4_load_98 | 37 | 0.0021884 | 0.00054848 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5604-5_0_4_load_45 | 39 | 0.005159 | 0.001293 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5604-5_0_4_load_38 | 40 | 0.0037551 | 0.00094111 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5604-5_0_4_load_25 | 41 | 0.00094794 | 0.00023758 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5604-5_0_4_load_83 | 42 | 0.00024758 | 6.2049e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5604-5_0_4_load_84 | 43 | 0.00022247 | 5.5756e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5604-5_0_4_load_86 | 45 | 0.0007783 | 0.00019506 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5604-5_0_4_load_90 | 46 | 0.0015851 | 0.00039727 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5604-5_0_4_load_89 | 47 | 0.0017266 | 0.00043274 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5604-5_0_4_load_88 | 48 | 0.00016744 | 4.1964e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5604-5_0_4_load_31 | 49 | 0.0034193 | 0.00085695 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5604-5_0_4_load_32 | 50 | 0.005512 | 0.0013814 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5604-5_0_4_load_34 | 52 | 0.010825 | 0.0027131 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5604-5_0_4_load_36 | 53 | 0.0052829 | 0.001324 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5604-5_0_4_load_48 | 54 | 0.0029752 | 0.00074566 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5604-5_0_4_load_44 | 55 | 0.0026935 | 0.00067505 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5604-5_0_4_load_43 | 56 | 0.002565 | 0.00064286 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5604-5_0_4_load_37 | 57 | 0.012236 | 0.0030666 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5604-5_0_4_load_41 | 59 | 0.0086611 | 0.0021707 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5604-5_0_4_load_42 | 60 | 0.0056769 | 0.0014228 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5604-5_0_4_load_96 | 62 | 0.0016417 | 0.00041146 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5604-5_0_4_load_55 | 63 | 0.012102 | 0.0030329 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5604-5_0_4_load_52 | 64 | 0.012103 | 0.0030333 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5604-5_0_4_load_53 | 65 | 0.019614 | 0.0049158 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5604-5_0_4_load_58 | 66 | 0.0030371 | 0.00076116 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5604-5_0_4_load_64 | 67 | 0.0022935 | 0.0005748 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5604-5_0_4_load_60 | 68 | 0.0060048 | 0.0015049 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5604-5_0_4_load_59 | 69 | 0.012107 | 0.0030342 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5604-5_0_4_load_61 | 70 | 0.01211 | 0.0030351 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5604-5_0_4_load_63 | 71 | 0.010336 | 0.0025904 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5604-5_0_4_load_65 | 72 | 0.0084988 | 0.00213 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5604-5_0_4_load_72 | 73 | 0.012107 | 0.0030342 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5604-5_0_4_load_66 | 74 | 0.0057082 | 0.0014306 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5604-5_0_4_load_67 | 75 | 0.0073863 | 0.0018512 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5604-5_0_4_load_70 | 76 | 0.0028545 | 0.0007154 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5604-5_0_4_load_87 | 78 | 0.01371 | 0.003436 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5604-5_0_4_load_122 | 79 | 0.0010143 | 0.00025422 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5604-5_0_4_load_91 | 80 | 0.0013294 | 0.00033319 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5604-5_0_4_load_92 | 81 | 0.00094633 | 0.00023717 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5604-5_0_4_load_116 | 85 | 0.001335 | 0.00033459 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5604-5_0_4_load_115 | 86 | 0.0013036 | 0.00032672 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5604-5_0_4_load_117 | 87 | 0.0022931 | 0.00057472 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5604-5_0_4_load_130 | 89 | 0.0007571 | 0.00018975 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5604-5_0_4_load_173 | 93 | 0.0012163 | 0.00030484 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5604-5_0_4_load_171 | 95 | 0.00049612 | 0.00012434 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5604-5_0_4_load_169 | 96 | 0.00022918 | 5.7438e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5604-5_0_4_load_174 | 97 | 0.00041656 | 0.0001044 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5604-5_0_4_load_165 | 98 | 0.00090244 | 0.00022617 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5604-5_0_4_load_164 | 100 | 0.0010059 | 0.00025209 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5604-5_0_4_load_168 | 101 | 0.00032398 | 8.1196e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5604-5_0_4_load_167 | 102 | 0.00017647 | 4.4228e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5604-5_0_4_load_181 | 103 | 0.001682 | 0.00042155 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5604-5_0_4_line_0 |  | 0 | 1 | 0.029432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_5604-5_0_4_line_1 |  | 1 | 2 | 0.037689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_5604-5_0_4_line_2 |  | 1 | 3 | 0.016951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_5604-5_0_4_line_3 |  | 2 | 4 | 0.025613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_5604-5_0_4_line_4 |  | 3 | 5 | 0.002427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_5604-5_0_4_line_5 |  | 4 | 6 | 0.014564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5604-5_0_4_line_6 |  | 4 | 7 | 0.03411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5604-5_0_4_line_7 |  | 5 | 8 | 0.021178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_5604-5_0_4_line_8 |  | 5 | 9 | 0.026828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5604-5_0_4_line_9 |  | 6 | 27 | 0.0035301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5604-5_0_4_line_10 |  | 7 | 23 | 0.016269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5604-5_0_4_line_11 |  | 8 | 13 | 0.044135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_5604-5_0_4_line_12 |  | 9 | 10 | 0.0038284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5604-5_0_4_line_13 |  | 10 | 11 | 0.033688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5604-5_0_4_line_14 |  | 11 | 12 | 0.031748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5604-5_0_4_line_15 |  | 12 | 14 | 0.029627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5604-5_0_4_line_16 |  | 13 | 15 | 0.014068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_5604-5_0_4_line_17 |  | 14 | 19 | 0.01164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5604-5_0_4_line_18 |  | 15 | 20 | 0.044609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_5604-5_0_4_line_19 |  | 15 | 18 | 0.020801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5604-5_0_4_line_20 |  | 16 | 17 | 0.023221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5604-5_0_4_line_21 |  | 16 | 18 | 0.026068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5604-5_0_4_line_22 |  | 19 | 21 | 0.046736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5604-5_0_4_line_23 |  | 20 | 22 | 0.039605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_5604-5_0_4_line_24 |  | 21 | 41 | 0.034354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5604-5_0_4_line_25 |  | 22 | 76 | 0.078335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5604-5_0_4_line_26 |  | 22 | 75 | 0.019987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_5604-5_0_4_line_27 |  | 23 | 24 | 0.021465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5604-5_0_4_line_28 |  | 23 | 25 | 0.046731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5604-5_0_4_line_29 |  | 24 | 26 | 0.022135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5604-5_0_4_line_30 |  | 26 | 31 | 0.022715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5604-5_0_4_line_31 |  | 27 | 35 | 0.029929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5604-5_0_4_line_32 |  | 27 | 36 | 0.02924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5604-5_0_4_line_33 |  | 28 | 29 | 0.018103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5604-5_0_4_line_34 |  | 28 | 30 | 0.014145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5604-5_0_4_line_35 |  | 29 | 63 | 0.0039602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5604-5_0_4_line_36 |  | 30 | 64 | 0.00062045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5604-5_0_4_line_37 |  | 31 | 51 | 0.034529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5604-5_0_4_line_38 |  | 32 | 33 | 0.012885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5604-5_0_4_line_39 |  | 32 | 34 | 0.014898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5604-5_0_4_line_40 |  | 33 | 67 | 0.0089087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5604-5_0_4_line_41 |  | 33 | 68 | 0.014607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5604-5_0_4_line_42 |  | 34 | 66 | 0.016802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5604-5_0_4_line_43 |  | 34 | 63 | 0.0077777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5604-5_0_4_line_44 |  | 36 | 37 | 0.0022731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5604-5_0_4_line_45 |  | 37 | 39 | 0.0087714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5604-5_0_4_line_46 |  | 38 | 39 | 0.010527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5604-5_0_4_line_47 |  | 38 | 40 | 0.010173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5604-5_0_4_line_48 |  | 40 | 57 | 0.011306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5604-5_0_4_line_49 |  | 41 | 42 | 0.040559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5604-5_0_4_line_50 |  | 42 | 43 | 0.0225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5604-5_0_4_line_51 |  | 43 | 44 | 0.07518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5604-5_0_4_line_52 |  | 44 | 45 | 0.11282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5604-5_0_4_line_53 |  | 45 | 46 | 0.02478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5604-5_0_4_line_54 |  | 46 | 47 | 0.032048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5604-5_0_4_line_55 |  | 47 | 48 | 0.051875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5604-5_0_4_line_56 |  | 48 | 78 | 0.019691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5604-5_0_4_line_57 |  | 49 | 50 | 0.042518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5604-5_0_4_line_58 |  | 49 | 51 | 0.025009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5604-5_0_4_line_59 |  | 51 | 52 | 0.036293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5604-5_0_4_line_60 |  | 51 | 53 | 0.030223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5604-5_0_4_line_61 |  | 52 | 54 | 0.12218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5604-5_0_4_line_62 |  | 53 | 55 | 0.0072857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5604-5_0_4_line_63 |  | 55 | 56 | 0.0054589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5604-5_0_4_line_64 |  | 57 | 58 | 0.02385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5604-5_0_4_line_65 |  | 58 | 59 | 0.0097378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5604-5_0_4_line_66 |  | 58 | 60 | 0.026843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5604-5_0_4_line_67 |  | 60 | 61 | 0.015087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5604-5_0_4_line_68 |  | 61 | 62 | 0.028377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5604-5_0_4_line_69 |  | 62 | 83 | 0.02629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5604-5_0_4_line_70 |  | 64 | 65 | 0.018195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5604-5_0_4_line_71 |  | 67 | 73 | 0.030397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5604-5_0_4_line_72 |  | 68 | 69 | 0.0090713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5604-5_0_4_line_73 |  | 69 | 70 | 0.02492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5604-5_0_4_line_74 |  | 70 | 71 | 0.012774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5604-5_0_4_line_75 |  | 71 | 72 | 0.0024679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5604-5_0_4_line_76 |  | 72 | 74 | 0.032197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5604-5_0_4_line_77 |  | 74 | 75 | 0.0099056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_5604-5_0_4_line_78 |  | 76 | 77 | 0.033808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5604-5_0_4_line_79 |  | 77 | 79 | 0.040267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5604-5_0_4_line_80 |  | 79 | 101 | 0.020697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5604-5_0_4_line_81 |  | 80 | 81 | 0.024539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5604-5_0_4_line_82 |  | 80 | 82 | 0.078541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5604-5_0_4_line_83 |  | 81 | 83 | 0.011826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_5604-5_0_4_line_84 |  | 82 | 84 | 0.15037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_5604-5_0_4_line_85 |  | 84 | 85 | 0.074482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5604-5_0_4_line_86 |  | 85 | 86 | 0.045019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_5604-5_0_4_line_87 |  | 87 | 88 | 0.12168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_5604-5_0_4_line_88 |  | 87 | 89 | 0.25949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_5604-5_0_4_line_89 |  | 88 | 90 | 0.002162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_5604-5_0_4_line_90 |  | 88 | 91 | 0.071429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5604-5_0_4_line_91 |  | 90 | 92 | 0.030567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5604-5_0_4_line_92 |  | 90 | 93 | 0.064509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_5604-5_0_4_line_93 |  | 91 | 94 | 0.037563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5604-5_0_4_line_94 |  | 92 | 95 | 0.025833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_5604-5_0_4_line_95 |  | 92 | 96 | 0.027835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_5604-5_0_4_line_96 |  | 93 | 97 | 0.0035462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_5604-5_0_4_line_97 |  | 94 | 98 | 0.051143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_5604-5_0_4_line_98 |  | 94 | 99 | 0.14764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_5604-5_0_4_line_99 |  | 94 | 100 | 0.062299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_5604-5_0_4_line_100 |  | 96 | 101 | 0.011953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_5604-5_0_4_line_101 |  | 98 | 102 | 0.0089961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_5604-5_0_4_line_102 |  | 99 | 103 | 0.046628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5604-5_0_4_trafo_0 | 0.63 MVA 20/0.4 kV | 104 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2548671.0921 | 1154587.6903 | 2548692.208 | 1154586.4871 | 2548700.4896 | 1154586.5412
1 | 2548671.0921 | 1154587.6903 | 2548671.0491 | 1154600.6086 | 2548672.9309 | 1154625.3073
2 | 2548671.0921 | 1154587.6903 | 2548671.1486 | 1154570.7399
3 | 2548674.8768 | 1154650.8468 | 2548672.9309 | 1154625.3073
4 | 2548671.1566 | 1154568.3129 | 2548671.1486 | 1154570.7399
5 | 2548674.8768 | 1154650.8468 | 2548675.9826 | 1154665.369
6 | 2548674.8768 | 1154650.8468 | 2548685.7329 | 1154647.4523 | 2548692.6775 | 1154641.4454 | 2548706.1465 | 1154639.9378
7 | 2548671.1566 | 1154568.3129 | 2548673.1302 | 1154547.2266
8 | 2548671.1566 | 1154568.3129 | 2548666.7148 | 1154567.3837 | 2548658.9148 | 1154565.7606 | 2548652.8017 | 1154563.167 | 2548646.4477 | 1154558.8492
9 | 2548676.2507 | 1154668.889 | 2548675.9826 | 1154665.369
10 | 2548722.3898 | 1154639.0349 | 2548706.5488 | 1154639.8928 | 2548706.1465 | 1154639.9378
11 | 2548677.3734 | 1154503.2973 | 2548676.8433 | 1154507.5545 | 2548673.1302 | 1154547.2266
12 | 2548646.4477 | 1154558.8492 | 2548643.2812 | 1154556.6975
13 | 2548615.4175 | 1154537.7629 | 2548643.2812 | 1154556.6975
14 | 2548615.4175 | 1154537.7629 | 2548589.1587 | 1154519.9191
15 | 2548564.6539 | 1154503.2671 | 2548589.1587 | 1154519.9191
16 | 2548679.1117 | 1154489.3367 | 2548677.3734 | 1154503.2973
17 | 2548564.6539 | 1154503.2671 | 2548558.3576 | 1154498.9966 | 2548555.0012 | 1154496.7241
18 | 2548684.6097 | 1154445.0775 | 2548679.1117 | 1154489.3367
19 | 2548679.1117 | 1154489.3367 | 2548662.5004 | 1154490.7571 | 2548658.5042 | 1154491.7939
20 | 2548610.9586 | 1154504.7823 | 2548633.3358 | 1154498.5781
21 | 2548658.5042 | 1154491.7939 | 2548647.6129 | 1154494.6197 | 2548633.3358 | 1154498.5781
22 | 2548555.0012 | 1154496.7241 | 2548549.9823 | 1154499.1795 | 2548544.6895 | 1154498.3244 | 2548522.796 | 1154494.7545 | 2548509.1932 | 1154494.5612
23 | 2548684.6097 | 1154445.0775 | 2548702.1388 | 1154445.1056 | 2548724.3077 | 1154444.0937
24 | 2548478.123 | 1154484.5156 | 2548491.0794 | 1154494.3038 | 2548509.1932 | 1154494.5612
25 | 2548724.3077 | 1154444.0937 | 2548749.6669 | 1154438.4632 | 2548770.0351 | 1154427.7839 | 2548787.4712 | 1154407.0133 | 2548788.5014 | 1154405.023
26 | 2548724.3077 | 1154444.0937 | 2548736.0354 | 1154460.2788
27 | 2548741.4964 | 1154647.7987 | 2548727.3314 | 1154639.2039 | 2548722.3898 | 1154639.0349
28 | 2548722.3898 | 1154639.0349 | 2548723.401 | 1154637.0808 | 2548723.172 | 1154634.5147 | 2548720.3288 | 1154626.746 | 2548718.0991 | 1154618.9721 | 2548718.058 | 1154614.1588 | 2548721.3091 | 1154608.5947 | 2548728.7694 | 1154602.7836 | 2548732.457 | 1154599.5866
29 | 2548741.4964 | 1154647.7987 | 2548751.12 | 1154654.5868 | 2548757.9515 | 1154662.3728
30 | 2548766.699 | 1154681.9066 | 2548766.388 | 1154671.988 | 2548757.9515 | 1154662.3728
31 | 2548676.2507 | 1154668.889 | 2548686.6257 | 1154667.5441 | 2548692.4063 | 1154669.8515 | 2548693.9726 | 1154672.7174 | 2548695.515 | 1154682.5748
32 | 2548676.2507 | 1154668.889 | 2548681.0667 | 1154697.7301
33 | 2548794.1623 | 1154606.9392 | 2548785.983 | 1154590.7894
34 | 2548794.1623 | 1154606.9392 | 2548801.1015 | 1154619.265
35 | 2548785.983 | 1154590.7894 | 2548784.1937 | 1154587.2565
36 | 2548801.4059 | 1154619.8056 | 2548801.1015 | 1154619.265
37 | 2548769.7881 | 1154715.3596 | 2548765.1 | 1154701.7369 | 2548767.1047 | 1154694.8495 | 2548766.699 | 1154681.9066
38 | 2548772.2897 | 1154567.9941 | 2548766.6294 | 1154556.414
39 | 2548772.2897 | 1154567.9941 | 2548780.6796 | 1154580.3179
40 | 2548766.6294 | 1154556.414 | 2548762.6394 | 1154558.0934 | 2548759.5523 | 1154557.7084 | 2548758.5036 | 1154556.6801
41 | 2548766.6294 | 1154556.414 | 2548763.8499 | 1154550.7236 | 2548764.3408 | 1154542.4639
42 | 2548780.6796 | 1154580.3179 | 2548771.4354 | 1154587.4449 | 2548771.272 | 1154592.5712
43 | 2548780.6796 | 1154580.3179 | 2548784.1937 | 1154587.2565
44 | 2548681.441 | 1154699.9721 | 2548681.0667 | 1154697.7301
45 | 2548681.441 | 1154699.9721 | 2548681.441 | 1154699.9721 | 2548681.8942 | 1154701.8359 | 2548683.4998 | 1154708.4985
46 | 2548685.9661 | 1154718.7323 | 2548683.4998 | 1154708.4985
47 | 2548685.9661 | 1154718.7323 | 2548689.6057 | 1154728.2317
48 | 2548693.6507 | 1154738.7894 | 2548689.6057 | 1154728.2317
49 | 2548478.123 | 1154484.5156 | 2548438.9492 | 1154495.0259
50 | 2548438.9492 | 1154495.0259 | 2548431.6556 | 1154487.7434 | 2548426.1211 | 1154476.8788
51 | 2548414.5749 | 1154404.1571 | 2548413.2198 | 1154414.2963 | 2548412.94 | 1154432.6305 | 2548414.4964 | 1154445.0237 | 2548418.9917 | 1154462.8834 | 2548426.1211 | 1154476.8788
52 | 2548414.5749 | 1154404.1571 | 2548416.8123 | 1154399.3798 | 2548456.0364 | 1154334.2089 | 2548468.543 | 1154315.6918 | 2548475.1182 | 1154309.3562
53 | 2548495.11 | 1154295.6428 | 2548486.0275 | 1154298.8442 | 2548475.1182 | 1154309.3562
54 | 2548526.115 | 1154288.6211 | 2548511.5653 | 1154289.8428 | 2548495.11 | 1154295.6428
55 | 2548577.3666 | 1154294.0547 | 2548562.9795 | 1154290.7473 | 2548538.5494 | 1154287.5771 | 2548526.115 | 1154288.6211
56 | 2548594.0904 | 1154304.3098 | 2548578.6448 | 1154294.3485 | 2548577.3666 | 1154294.0547
57 | 2548788.3019 | 1154732.1733 | 2548819.7772 | 1154760.7582
58 | 2548769.7881 | 1154715.3596 | 2548788.3019 | 1154732.1733
59 | 2548769.7881 | 1154715.3596 | 2548773.9116 | 1154709.5659 | 2548777.2912 | 1154707.3804 | 2548783.1557 | 1154707.8417 | 2548788.432 | 1154711.2874 | 2548799.7402 | 1154717.6444
60 | 2548769.7881 | 1154715.3596 | 2548756.5551 | 1154708.9914 | 2548741.2719 | 1154706.1903
61 | 2548799.7402 | 1154717.6444 | 2548813.0355 | 1154725.1184 | 2548818.6971 | 1154725.1813 | 2548825.877 | 1154723.3748 | 2548830.2739 | 1154719.9466 | 2548833.5262 | 1154715.4165 | 2548835.1403 | 1154711.3006 | 2548835.1797 | 1154704.2188 | 2548833.7892 | 1154697.6716 | 2548795.1578 | 1154646.0037
62 | 2548741.2719 | 1154706.1903 | 2548740.6744 | 1154706.0808 | 2548734.1347 | 1154707.4346
63 | 2548728.7891 | 1154708.5412 | 2548734.1347 | 1154707.4346
64 | 2548702.1835 | 1154761.0605 | 2548693.6507 | 1154738.7894
65 | 2548702.1835 | 1154761.0605 | 2548706.2815 | 1154769.8941
66 | 2548702.1835 | 1154761.0605 | 2548692.828 | 1154766.799 | 2548678.2903 | 1154773.1575
67 | 2548664.4675 | 1154779.2033 | 2548678.2903 | 1154773.1575
68 | 2548664.4675 | 1154779.2033 | 2548638.4703 | 1154790.5797
69 | 2548613.2982 | 1154797.4614 | 2548620.9233 | 1154796.5958 | 2548629.6954 | 1154794.4196 | 2548638.4703 | 1154790.5797
70 | 2548810.3322 | 1154635.661 | 2548801.4059 | 1154619.8056
71 | 2548734.9332 | 1154553.8163 | 2548741.8164 | 1154546.8873 | 2548748.6603 | 1154547.029 | 2548758.5036 | 1154556.6801
72 | 2548764.879 | 1154533.4086 | 2548764.3408 | 1154542.4639
73 | 2548764.879 | 1154533.4086 | 2548765.2989 | 1154526.3429 | 2548766.8042 | 1154508.5651
74 | 2548766.8042 | 1154508.5651 | 2548766.8042 | 1154508.5651 | 2548760.5063 | 1154497.4515
75 | 2548759.2896 | 1154495.3044 | 2548760.5063 | 1154497.4515
76 | 2548759.2896 | 1154495.3044 | 2548751.6634 | 1154481.8468 | 2548741.8475 | 1154468.3
77 | 2548741.8475 | 1154468.3 | 2548736.0354 | 1154460.2788
78 | 2548802.9354 | 1154374.4755 | 2548796.3314 | 1154389.8954 | 2548788.5014 | 1154405.023
79 | 2548802.9354 | 1154374.4755 | 2548806.6586 | 1154365.7836 | 2548817.8862 | 1154337.0911
80 | 2548817.8862 | 1154337.0911 | 2548818.9714 | 1154334.3177 | 2548826.5439 | 1154318.2982
81 | 2548577.4833 | 1154792.5167 | 2548590.7371 | 1154795.5201 | 2548601.5733 | 1154797.0886
82 | 2548500.3023 | 1154779.0081 | 2548513.4384 | 1154779.429 | 2548534.8617 | 1154782.8584 | 2548577.4833 | 1154792.5167
83 | 2548613.2982 | 1154797.4614 | 2548608.1407 | 1154798.0392 | 2548601.5733 | 1154797.0886
84 | 2548357.4475 | 1154810.1506 | 2548385.5456 | 1154793.178 | 2548406.3233 | 1154783.9614 | 2548424.2669 | 1154778.7713 | 2548443.7064 | 1154777.1702 | 2548469.104 | 1154777.9972 | 2548500.3023 | 1154779.0081
85 | 2548357.4475 | 1154810.1506 | 2548324.4459 | 1154770.7136 | 2548310.4259 | 1154755.8263 | 2548308.0988 | 1154754.6474
86 | 2548269.82 | 1154731.8273 | 2548276.829 | 1154739.0844 | 2548291.3727 | 1154746.1741 | 2548308.0988 | 1154754.6474
87 | 2548872.8936 | 1154265.8226 | 2548877.0733 | 1154279.1941 | 2548880.2471 | 1154296.0537 | 2548889.158 | 1154343.4362 | 2548898.6724 | 1154379.7299 | 2548895.9594 | 1154383.6679
88 | 2548895.9594 | 1154383.6679 | 2549109.2715 | 1154531.4286
89 | 2548872.8936 | 1154265.8226 | 2548870.8908 | 1154266.6512
90 | 2548940.6253 | 1154243.2793 | 2548924.4979 | 1154246.6626 | 2548893.2102 | 1154259.8022 | 2548874.7666 | 1154265.0507 | 2548872.8936 | 1154265.8226
91 | 2548870.8908 | 1154266.6512 | 2548861.0676 | 1154270.7258 | 2548845.9124 | 1154283.7617
92 | 2548870.8908 | 1154266.6512 | 2548868.316 | 1154234.5451 | 2548867.6769 | 1154223.4558 | 2548871.8045 | 1154202.6693
93 | 2548940.6253 | 1154243.2793 | 2548952.4615 | 1154239.5545 | 2548964.4949 | 1154236.4729 | 2548970.713 | 1154234.2523 | 2548975.5757 | 1154230.5201
94 | 2548845.9124 | 1154283.7617 | 2548850.4982 | 1154258.3426
95 | 2548845.9124 | 1154283.7617 | 2548844.0085 | 1154285.401 | 2548833.2966 | 1154304.0131 | 2548831.6522 | 1154307.4918
96 | 2548871.8045 | 1154202.6693 | 2548872.4952 | 1154199.191 | 2548872.4952 | 1154199.191
97 | 2548975.5757 | 1154230.5201 | 2548989.6838 | 1154219.6947 | 2549014.4542 | 1154197.3497
98 | 2548975.5757 | 1154230.5201 | 2548970.713 | 1154234.2523 | 2548983.0507 | 1154236.2819 | 2549016.0017 | 1154247.3414 | 2549043.5579 | 1154258.2134 | 2549060.4405 | 1154262.4502 | 2549071.1816 | 1154262.5704 | 2549095.9813 | 1154258.6915 | 2549105.9148 | 1154253.1378
99 | 2548975.5757 | 1154230.5201 | 2548986.0005 | 1154227.719 | 2548997.7538 | 1154230.4874 | 2549010.7526 | 1154234.4792 | 2549016.5152 | 1154234.6304 | 2549023.0795 | 1154232.5291 | 2549034.2024 | 1154225.4693
100 | 2548826.5439 | 1154318.2982 | 2548831.6522 | 1154307.4918
101 | 2549021.1341 | 1154191.3239 | 2549014.4542 | 1154197.3497
102 | 2549105.9148 | 1154253.1378 | 2549094.5922 | 1154245.0517 | 2549072.9797 | 1154220.4107

## bus_geodata
| x | y | coords
0 | 2548700.4896 | 1154586.5412
1 | 2548671.0921 | 1154587.6903
2 | 2548672.9309 | 1154625.3073
3 | 2548671.1486 | 1154570.7399
4 | 2548674.8768 | 1154650.8468
5 | 2548671.1566 | 1154568.3129
6 | 2548675.9826 | 1154665.369
7 | 2548706.1465 | 1154639.9378
8 | 2548673.1302 | 1154547.2266
9 | 2548646.4478 | 1154558.8492
10 | 2548643.2812 | 1154556.6974
11 | 2548615.4175 | 1154537.7629
12 | 2548589.1587 | 1154519.9191
13 | 2548677.3734 | 1154503.2973
14 | 2548564.6539 | 1154503.2671
15 | 2548679.1117 | 1154489.3367
16 | 2548633.3358 | 1154498.5781
17 | 2548610.9586 | 1154504.7823
18 | 2548658.5042 | 1154491.7939
19 | 2548555.0012 | 1154496.7241
20 | 2548684.6097 | 1154445.0775
21 | 2548509.1932 | 1154494.5612
22 | 2548724.3077 | 1154444.0937
23 | 2548722.3898 | 1154639.0349
24 | 2548741.4964 | 1154647.7987
25 | 2548732.457 | 1154599.5866
26 | 2548757.9515 | 1154662.3728
27 | 2548676.2507 | 1154668.889
28 | 2548794.1623 | 1154606.9392
29 | 2548785.983 | 1154590.7894
30 | 2548801.1015 | 1154619.265
31 | 2548766.699 | 1154681.9066
32 | 2548772.2897 | 1154567.9941
33 | 2548766.6294 | 1154556.414
34 | 2548780.6796 | 1154580.3179
35 | 2548695.515 | 1154682.5748
36 | 2548681.0667 | 1154697.7301
37 | 2548681.441 | 1154699.9721
38 | 2548685.9661 | 1154718.7323
39 | 2548683.4998 | 1154708.4985
40 | 2548689.6057 | 1154728.2317
41 | 2548478.123 | 1154484.5156
42 | 2548438.9492 | 1154495.0259
43 | 2548426.1211 | 1154476.8788
44 | 2548414.5749 | 1154404.1571
45 | 2548475.1182 | 1154309.3562
46 | 2548495.11 | 1154295.6428
47 | 2548526.115 | 1154288.6211
48 | 2548577.3666 | 1154294.0547
49 | 2548788.3019 | 1154732.1733
50 | 2548819.7772 | 1154760.7582
51 | 2548769.7881 | 1154715.3596
52 | 2548799.7402 | 1154717.6444
53 | 2548741.2719 | 1154706.1903
54 | 2548795.1578 | 1154646.0037
55 | 2548734.1347 | 1154707.4346
56 | 2548728.7891 | 1154708.5412
57 | 2548693.6507 | 1154738.7894
58 | 2548702.1835 | 1154761.0605
59 | 2548706.2815 | 1154769.8941
60 | 2548678.2903 | 1154773.1575
61 | 2548664.4675 | 1154779.2033
62 | 2548638.4703 | 1154790.5797
63 | 2548784.1937 | 1154587.2565
64 | 2548801.4059 | 1154619.8056
65 | 2548810.3322 | 1154635.661
66 | 2548771.272 | 1154592.5712
67 | 2548758.5036 | 1154556.6801
68 | 2548764.3408 | 1154542.4639
69 | 2548764.879 | 1154533.4086
70 | 2548766.8042 | 1154508.5651
71 | 2548760.5063 | 1154497.4515
72 | 2548759.2896 | 1154495.3044
73 | 2548734.9332 | 1154553.8163
74 | 2548741.8475 | 1154468.3
75 | 2548736.0354 | 1154460.2788
76 | 2548788.5014 | 1154405.023
77 | 2548802.9354 | 1154374.4755
78 | 2548594.0904 | 1154304.3098
79 | 2548817.8862 | 1154337.0911
80 | 2548577.4833 | 1154792.5167
81 | 2548601.5733 | 1154797.0886
82 | 2548500.3023 | 1154779.0081
83 | 2548613.2982 | 1154797.4614
84 | 2548357.4475 | 1154810.1506
85 | 2548308.0988 | 1154754.6474
86 | 2548269.82 | 1154731.8273
87 | 2548895.9594 | 1154383.6679
88 | 2548872.8936 | 1154265.8226
89 | 2549109.2715 | 1154531.4286
90 | 2548870.8908 | 1154266.6512
91 | 2548940.6253 | 1154243.2793
92 | 2548845.9124 | 1154283.7617
93 | 2548871.8045 | 1154202.6693
94 | 2548975.5757 | 1154230.5201
95 | 2548850.4982 | 1154258.3426
96 | 2548831.6522 | 1154307.4918
97 | 2548872.4952 | 1154199.191
98 | 2549014.4542 | 1154197.3497
99 | 2549105.9148 | 1154253.1378
100 | 2549034.2024 | 1154225.4693
101 | 2548826.5439 | 1154318.2982
102 | 2549021.1341 | 1154191.3239
103 | 2549072.9797 | 1154220.4107
104 | 2548705.4797 | 1154586.5738

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1