## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5611-9_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5611-9_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5611-9_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5611-9_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5611-9_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5611-9_0_2_node_73 | 0.4 | n |  | TRUE
6 | bus_LV_5611-9_0_2_node_74 | 0.4 | n |  | TRUE
7 | bus_LV_5611-9_0_2_node_75 | 0.4 | n |  | TRUE
8 | bus_LV_5611-9_0_2_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_5611-9_0_2_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_5611-9_0_2_node_77 | 0.4 | n |  | TRUE
11 | bus_LV_5611-9_0_2_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_5611-9_0_2_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_5611-9_0_2_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_5611-9_0_2_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_5611-9_0_2_node_82 | 0.4 | n |  | TRUE
16 | bus_LV_5611-9_0_2_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_5611-9_0_2_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_5611-9_0_2_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_5611-9_0_2_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_5611-9_0_2_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_5611-9_0_2_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_5611-9_0_2_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_5611-9_0_2_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_5611-9_0_2_node_76 | 0.4 | n |  | TRUE
25 | bus_LV_5611-9_0_2_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_5611-9_0_2_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_5611-9_0_2_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_5611-9_0_2_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_5611-9_0_2_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_5611-9_0_2_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_5611-9_0_2_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_5611-9_0_2_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_5611-9_0_2_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_5611-9_0_2_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_5611-9_0_2_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_5611-9_0_2_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_5611-9_0_2_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_5611-9_0_2_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_5611-9_0_2_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_5611-9_0_2_node_49 | 0.4 | n |  | TRUE
41 | bus_LV_5611-9_0_2_node_50 | 0.4 | n |  | TRUE
42 | bus_LV_5611-9_0_2_node_52 | 0.4 | n |  | TRUE
43 | bus_LV_5611-9_0_2_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_5611-9_0_2_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_5611-9_0_2_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_5611-9_0_2_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_5611-9_0_2_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_5611-9_0_2_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_5611-9_0_2_node_101 | 0.4 | n |  | TRUE
50 | bus_LV_5611-9_0_2_node_83 | 0.4 | n |  | TRUE
51 | bus_LV_5611-9_0_2_node_84 | 0.4 | n |  | TRUE
52 | bus_LV_5611-9_0_2_node_63 | 0.4 | n |  | TRUE
53 | bus_LV_5611-9_0_2_node_64 | 0.4 | n |  | TRUE
54 | bus_LV_5611-9_0_2_node_65 | 0.4 | n |  | TRUE
55 | bus_LV_5611-9_0_2_node_66 | 0.4 | n |  | TRUE
56 | bus_LV_5611-9_0_2_node_67 | 0.4 | n |  | TRUE
57 | bus_LV_5611-9_0_2_node_81 | 0.4 | n |  | TRUE
58 | bus_MV_366_2_node_31 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5611-9_0_2_load_0 | 0 | 0.002701 | 0.00067695 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5611-9_0_2_load_1 | 1 | 0.0012519 | 0.00031376 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5611-9_0_2_load_2 | 2 | 0.002695 | 0.00067544 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5611-9_0_2_load_3 | 3 | 0.0023112 | 0.00057924 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5611-9_0_2_load_4 | 4 | 0.0032574 | 0.00081637 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5611-9_0_2_load_73 | 5 | 0.00065463 | 0.00016407 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5611-9_0_2_load_74 | 6 | 0.00070562 | 0.00017684 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5611-9_0_2_load_75 | 7 | 9.0161e-05 | 2.2596e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5611-9_0_2_load_15 | 8 | 0.0020355 | 0.00051015 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5611-9_0_2_load_6 | 9 | 0.0024487 | 0.00061371 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5611-9_0_2_load_77 | 10 | 0.00028919 | 7.2477e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5611-9_0_2_load_14 | 11 | 0.0021008 | 0.00052651 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5611-9_0_2_load_5 | 12 | 0.0036727 | 0.00092047 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5611-9_0_2_load_7 | 13 | 0.0030921 | 0.00077496 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5611-9_0_2_load_8 | 14 | 0.0029721 | 0.00074488 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5611-9_0_2_load_82 | 15 | 0.0005136 | 0.00012872 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5611-9_0_2_load_18 | 16 | 0.0038479 | 0.00096437 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5611-9_0_2_load_19 | 17 | 0.0035835 | 0.0008981 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5611-9_0_2_load_9 | 18 | 0.003571 | 0.00089497 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5611-9_0_2_load_10 | 19 | 0.0048612 | 0.0012183 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5611-9_0_2_load_11 | 20 | 0.0012916 | 0.00032371 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5611-9_0_2_load_12 | 21 | 0.0027541 | 0.00069025 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5611-9_0_2_load_28 | 23 | 0.002633 | 0.00065989 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5611-9_0_2_load_76 | 24 | 0.00051578 | 0.00012927 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5611-9_0_2_load_25 | 25 | 0.0017414 | 0.00043645 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5611-9_0_2_load_23 | 26 | 0.0010335 | 0.00025901 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5611-9_0_2_load_29 | 27 | 0.004584 | 0.0011488 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5611-9_0_2_load_26 | 28 | 0.0016843 | 0.00042211 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5611-9_0_2_load_24 | 29 | 0.0053074 | 0.0013302 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5611-9_0_2_load_16 | 30 | 0.0024255 | 0.00060788 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5611-9_0_2_load_17 | 31 | 0.0029457 | 0.00073825 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5611-9_0_2_load_21 | 32 | 0.0026723 | 0.00066974 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5611-9_0_2_load_22 | 33 | 0.0042807 | 0.0010728 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5611-9_0_2_load_20 | 34 | 0.0038259 | 0.00095886 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5611-9_0_2_load_32 | 36 | 0.00097901 | 0.00024536 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5611-9_0_2_load_34 | 37 | 0.0039238 | 0.0009834 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5611-9_0_2_load_33 | 38 | 0.0042538 | 0.0010661 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5611-9_0_2_load_27 | 39 | 0.0020254 | 0.00050761 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5611-9_0_2_load_49 | 40 | 0.0025549 | 0.00064031 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5611-9_0_2_load_50 | 41 | 0.00063001 | 0.00015789 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5611-9_0_2_load_52 | 42 | 0.00061679 | 0.00015458 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5611-9_0_2_load_30 | 43 | 0.0024699 | 0.00061901 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5611-9_0_2_load_35 | 44 | 0.0012592 | 0.00031559 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5611-9_0_2_load_36 | 45 | 0.00060791 | 0.00015236 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5611-9_0_2_load_40 | 47 | 0.0011833 | 0.00029657 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5611-9_0_2_load_41 | 48 | 0.0002049 | 5.1353e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5611-9_0_2_load_83 | 50 | 0.00059648 | 0.00014949 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5611-9_0_2_load_84 | 51 | 0.0018311 | 0.00045891 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5611-9_0_2_load_63 | 52 | 0.0023031 | 0.00057721 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5611-9_0_2_load_64 | 53 | 0.0007381 | 0.00018498 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5611-9_0_2_load_65 | 54 | 0.00088448 | 0.00022167 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5611-9_0_2_load_66 | 55 | 0.0014906 | 0.00037357 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5611-9_0_2_load_67 | 56 | 0.00030404 | 7.6201e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5611-9_0_2_load_81 | 57 | 0.00080375 | 0.00020144 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5611-9_0_2_line_0 |  | 0 | 1 | 0.0051155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5611-9_0_2_line_1 |  | 0 | 2 | 0.0095254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5611-9_0_2_line_2 |  | 1 | 3 | 0.006048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5611-9_0_2_line_3 |  | 2 | 4 | 0.0041774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5611-9_0_2_line_4 |  | 3 | 8 | 0.021415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5611-9_0_2_line_5 |  | 4 | 9 | 0.027192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5611-9_0_2_line_6 |  | 5 | 6 | 0.1607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5611-9_0_2_line_7 |  | 5 | 7 | 0.016151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5611-9_0_2_line_8 |  | 6 | 24 | 0.14357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5611-9_0_2_line_9 |  | 6 | 21 | 0.35367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5611-9_0_2_line_10 |  | 7 | 10 | 0.026867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5611-9_0_2_line_11 |  | 8 | 11 | 0.0061818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5611-9_0_2_line_12 |  | 9 | 12 | 0.00024871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5611-9_0_2_line_13 |  | 10 | 15 | 0.033282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5611-9_0_2_line_14 |  | 11 | 30 | 0.026505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5611-9_0_2_line_15 |  | 12 | 13 | 0.0018203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5611-9_0_2_line_16 |  | 13 | 14 | 0.020499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5611-9_0_2_line_17 |  | 14 | 16 | 0.016272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5611-9_0_2_line_18 |  | 15 | 49 | 0.22592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5611-9_0_2_line_19 |  | 16 | 17 | 0.0094156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5611-9_0_2_line_20 |  | 17 | 34 | 0.0028319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5611-9_0_2_line_21 |  | 18 | 19 | 0.019488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5611-9_0_2_line_22 |  | 18 | 20 | 0.015096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5611-9_0_2_line_23 |  | 19 | 21 | 0.015853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5611-9_0_2_line_24 |  | 20 | 22 | 0.013464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5611-9_0_2_line_25 |  | 21 | 23 | 0.028398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5611-9_0_2_line_26 |  | 22 | 25 | 0.026646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5611-9_0_2_line_27 |  | 22 | 26 | 0.027525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5611-9_0_2_line_28 |  | 23 | 27 | 0.0095179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5611-9_0_2_line_29 |  | 25 | 28 | 0.016595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5611-9_0_2_line_30 |  | 26 | 29 | 0.0075923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5611-9_0_2_line_31 |  | 27 | 43 | 0.013504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5611-9_0_2_line_32 |  | 28 | 39 | 0.015351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5611-9_0_2_line_33 |  | 30 | 31 | 0.006252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5611-9_0_2_line_34 |  | 31 | 32 | 4.0695e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5611-9_0_2_line_35 |  | 32 | 33 | 0.029855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5611-9_0_2_line_36 |  | 33 | 37 | 0.01118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5611-9_0_2_line_37 |  | 34 | 35 | 0.036105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5611-9_0_2_line_38 |  | 35 | 36 | 0.072181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5611-9_0_2_line_39 |  | 36 | 44 | 0.0031205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5611-9_0_2_line_40 |  | 37 | 38 | 0.011058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5611-9_0_2_line_41 |  | 38 | 43 | 0.0096169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5611-9_0_2_line_42 |  | 39 | 40 | 0.15389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5611-9_0_2_line_43 |  | 40 | 41 | 0.0084003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5611-9_0_2_line_44 |  | 40 | 42 | 0.20849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5611-9_0_2_line_45 |  | 42 | 50 | 0.0098239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5611-9_0_2_line_46 |  | 45 | 46 | 0.0024651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5611-9_0_2_line_47 |  | 46 | 47 | 0.052097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5611-9_0_2_line_48 |  | 46 | 48 | 0.0038917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5611-9_0_2_line_49 |  | 48 | 49 | 0.25478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5611-9_0_2_line_50 |  | 50 | 51 | 0.042771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5611-9_0_2_line_51 |  | 51 | 56 | 0.030174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5611-9_0_2_line_52 |  | 52 | 53 | 2.6571e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5611-9_0_2_line_53 |  | 52 | 54 | 0.046508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5611-9_0_2_line_54 |  | 53 | 55 | 0.023336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5611-9_0_2_line_55 |  | 54 | 56 | 0.028893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5611-9_0_2_line_56 |  | 55 | 57 | 0.037797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5611-9_0_2_trafo_30 | 0.63 MVA 20/0.4 kV | 58 | 43 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2543930.7691 | 1156193.7615 | 2543932.7252 | 1156198.4883
1 | 2543930.7691 | 1156193.7615 | 2543927.1268 | 1156184.96
2 | 2543935.0378 | 1156204.0766 | 2543932.7252 | 1156198.4883
3 | 2543927.1268 | 1156184.96 | 2543925.5294 | 1156181.1001
4 | 2543935.0378 | 1156204.0766 | 2543943.2267 | 1156223.8645
5 | 2543915.1316 | 1156155.9743 | 2543925.5294 | 1156181.1001
6 | 2544275.2283 | 1156071.662 | 2544303.1984 | 1156147.4874 | 2544320.8877 | 1156197.5501 | 2544326.1372 | 1156223.8156
7 | 2544275.2283 | 1156071.662 | 2544269.6386 | 1156056.5087
8 | 2544369.9104 | 1156359.9716 | 2544366.6151 | 1156356.0889 | 2544362.3414 | 1156344.2666 | 2544330.6991 | 1156246.641 | 2544326.1372 | 1156223.8156
9 | 2544326.1372 | 1156223.8156 | 2544001.5791 | 1156364.3366
10 | 2544269.6386 | 1156056.5087 | 2544260.3404 | 1156031.3018
11 | 2543945.5936 | 1156229.5752 | 2543944.6338 | 1156227.2649 | 2543943.2267 | 1156223.8645
12 | 2543915.0365 | 1156155.7445 | 2543915.1316 | 1156155.9743
13 | 2544260.3404 | 1156031.3018 | 2544256.6169 | 1156021.2076 | 2544255.5799 | 1156009.4665 | 2544257.7985 | 1155998.9625
14 | 2543955.7624 | 1156254.0522 | 2543945.5936 | 1156229.5752
15 | 2543915.0365 | 1156155.7445 | 2543914.3404 | 1156154.0625
16 | 2543914.3404 | 1156154.0625 | 2543906.5019 | 1156135.1212
17 | 2543906.5019 | 1156135.1212 | 2543900.28 | 1156120.0863
18 | 2544257.7985 | 1155998.9625 | 2544444.0551 | 1155871.1024
19 | 2543896.6797 | 1156111.3862 | 2543900.28 | 1156120.0863
20 | 2543895.5968 | 1156108.7696 | 2543896.6797 | 1156111.3862
21 | 2544012.7338 | 1156397.675 | 2544010.7452 | 1156386.4001 | 2544007.661 | 1156378.9761
22 | 2544009.4129 | 1156412.3284 | 2544012.8828 | 1156398.52 | 2544012.7338 | 1156397.675
23 | 2544007.661 | 1156378.9761 | 2544001.5791 | 1156364.3366
24 | 2544006.1317 | 1156425.3861 | 2544009.4129 | 1156412.3284
25 | 2543990.6844 | 1156338.112 | 2544001.5791 | 1156364.3366
26 | 2544006.1317 | 1156425.3861 | 2544016.7165 | 1156434.6258 | 2544028.8092 | 1156438.1504
27 | 2544006.1317 | 1156425.3861 | 2543983.2022 | 1156440.6125
28 | 2543990.6844 | 1156338.112 | 2543987.0328 | 1156329.3225
29 | 2544028.8092 | 1156438.1504 | 2544044.7412 | 1156442.7941
30 | 2543976.8774 | 1156444.8125 | 2543983.2022 | 1156440.6125
31 | 2543981.8518 | 1156316.8514 | 2543987.0328 | 1156329.3225
32 | 2544059.4789 | 1156447.0896 | 2544044.7412 | 1156442.7941
33 | 2543955.7624 | 1156254.0522 | 2543958.161 | 1156259.8258
34 | 2543958.161 | 1156259.8258 | 2543958.1766 | 1156259.8634
35 | 2543958.1766 | 1156259.8634 | 2543969.6306 | 1156287.434
36 | 2543973.9197 | 1156297.7581 | 2543969.6306 | 1156287.434
37 | 2543880.251 | 1156076.1964 | 2543885.9044 | 1156085.3484 | 2543895.5968 | 1156108.7696
38 | 2543880.251 | 1156076.1964 | 2543856.1105 | 1156111.7298 | 2543844.4842 | 1156138.5403
39 | 2543844.4842 | 1156138.5403 | 2543844.0237 | 1156139.6021 | 2543843.2978 | 1156141.4261
40 | 2543973.9197 | 1156297.7581 | 2543978.1622 | 1156307.9704
41 | 2543981.8518 | 1156316.8514 | 2543978.1622 | 1156307.9704
42 | 2544059.4789 | 1156447.0896 | 2544168.613 | 1156555.5895
43 | 2544168.613 | 1156555.5895 | 2544176.7824 | 1156553.6332
44 | 2544125.2661 | 1156759.5222 | 2544168.613 | 1156555.5895
45 | 2544134.5554 | 1156762.7186 | 2544125.2661 | 1156759.5222
46 | 2544308.082 | 1155651.1439 | 2544307.2178 | 1155648.8353
47 | 2544308.082 | 1155651.1439 | 2544302.8407 | 1155654.1497 | 2544289.5429 | 1155661.7659 | 2544284.1206 | 1155665.0957 | 2544279.0857 | 1155665.5538 | 2544271.3306 | 1155661.3124 | 2544262.7204 | 1155655.3513
48 | 2544308.082 | 1155651.1439 | 2544309.4473 | 1155654.7883
49 | 2544444.0551 | 1155871.1024 | 2544309.4473 | 1155654.7883
50 | 2544134.5554 | 1156762.7186 | 2544174.9987 | 1156776.635
51 | 2544200.284 | 1156791.8982 | 2544197.8433 | 1156789.0744 | 2544192.3733 | 1156783.8668 | 2544186.5765 | 1156780.619 | 2544174.9987 | 1156776.635
52 | 2544248.4452 | 1156849.889 | 2544248.4617 | 1156849.9099
53 | 2544248.4452 | 1156849.889 | 2544228.2609 | 1156824.2662 | 2544219.1779 | 1156813.7576
54 | 2544248.4617 | 1156849.9099 | 2544262.9024 | 1156868.2415
55 | 2544200.284 | 1156791.8982 | 2544219.1779 | 1156813.7576
56 | 2544286.2916 | 1156897.9327 | 2544262.9024 | 1156868.2415

## bus_geodata
| x | y | coords
0 | 2543930.7691 | 1156193.7615
1 | 2543932.7252 | 1156198.4883
2 | 2543927.1268 | 1156184.96
3 | 2543935.0378 | 1156204.0766
4 | 2543925.5294 | 1156181.1001
5 | 2544275.2283 | 1156071.662
6 | 2544326.1372 | 1156223.8156
7 | 2544269.6386 | 1156056.5087
8 | 2543943.2267 | 1156223.8645
9 | 2543915.1316 | 1156155.9743
10 | 2544260.3404 | 1156031.3018
11 | 2543945.5936 | 1156229.5752
12 | 2543915.0365 | 1156155.7445
13 | 2543914.3404 | 1156154.0625
14 | 2543906.5019 | 1156135.1212
15 | 2544257.7985 | 1155998.9625
16 | 2543900.28 | 1156120.0863
17 | 2543896.6797 | 1156111.3862
18 | 2544012.7338 | 1156397.675
19 | 2544007.661 | 1156378.9761
20 | 2544009.4129 | 1156412.3284
21 | 2544001.5791 | 1156364.3366
22 | 2544006.1317 | 1156425.3861
23 | 2543990.6844 | 1156338.112
24 | 2544369.9104 | 1156359.9716
25 | 2544028.8092 | 1156438.1504
26 | 2543983.2022 | 1156440.6125
27 | 2543987.0328 | 1156329.3225
28 | 2544044.7412 | 1156442.7941
29 | 2543976.8774 | 1156444.8125
30 | 2543955.7624 | 1156254.0522
31 | 2543958.161 | 1156259.8258
32 | 2543958.1766 | 1156259.8634
33 | 2543969.6306 | 1156287.434
34 | 2543895.5968 | 1156108.7696
35 | 2543880.251 | 1156076.1964
36 | 2543844.4842 | 1156138.5403
37 | 2543973.9197 | 1156297.7581
38 | 2543978.1622 | 1156307.9704
39 | 2544059.4789 | 1156447.0896
40 | 2544168.613 | 1156555.5895
41 | 2544176.7824 | 1156553.6332
42 | 2544125.2661 | 1156759.5222
43 | 2543981.8518 | 1156316.8514
44 | 2543843.2978 | 1156141.4261
45 | 2544307.2178 | 1155648.8353
46 | 2544308.082 | 1155651.1439
47 | 2544262.7204 | 1155655.3513
48 | 2544309.4473 | 1155654.7883
49 | 2544444.0551 | 1155871.1024
50 | 2544134.5554 | 1156762.7186
51 | 2544174.9987 | 1156776.635
52 | 2544248.4452 | 1156849.889
53 | 2544248.4617 | 1156849.9099
54 | 2544219.1779 | 1156813.7576
55 | 2544262.9024 | 1156868.2415
56 | 2544200.284 | 1156791.8982
57 | 2544286.2916 | 1156897.9327
58 | 2544006.1317 | 1156425.3861

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1