## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5613-10_1_3_node_21 | 0.4 | n |  | TRUE
1 | bus_LV_5613-10_1_3_node_31 | 0.4 | n |  | TRUE
2 | bus_LV_5613-10_1_3_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_5613-10_1_3_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_5613-10_1_3_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_5613-10_1_3_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_5613-10_1_3_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_5613-10_1_3_node_50 | 0.4 | n |  | TRUE
8 | bus_LV_5613-10_1_3_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_5613-10_1_3_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_5613-10_1_3_node_51 | 0.4 | n |  | TRUE
11 | bus_LV_5613-10_1_3_node_52 | 0.4 | n |  | TRUE
12 | bus_LV_5613-10_1_3_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_5613-10_1_3_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_5613-10_1_3_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_5613-10_1_3_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_5613-10_1_3_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_5613-10_1_3_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_5613-10_1_3_node_58 | 0.4 | n |  | TRUE
19 | bus_LV_5613-10_1_3_node_64 | 0.4 | n |  | TRUE
20 | bus_LV_5613-10_1_3_node_68 | 0.4 | n |  | TRUE
21 | bus_LV_5613-10_1_3_node_57 | 0.4 | n |  | TRUE
22 | bus_LV_5613-10_1_3_node_61 | 0.4 | n |  | TRUE
23 | bus_LV_5613-10_1_3_node_65 | 0.4 | n |  | TRUE
24 | bus_LV_5613-10_1_3_node_66 | 0.4 | n |  | TRUE
25 | bus_LV_5613-10_1_3_node_63 | 0.4 | n |  | TRUE
26 | bus_LV_5613-10_1_3_node_56 | 0.4 | n |  | TRUE
27 | bus_LV_5613-10_1_3_node_55 | 0.4 | n |  | TRUE
28 | bus_LV_5613-10_1_3_node_71 | 0.4 | n |  | TRUE
29 | bus_LV_5613-10_1_3_node_72 | 0.4 | n |  | TRUE
30 | bus_LV_5613-10_1_3_node_70 | 0.4 | n |  | TRUE
31 | bus_LV_5613-10_1_3_node_53 | 0.4 | n |  | TRUE
32 | bus_LV_5613-10_1_3_node_54 | 0.4 | n |  | TRUE
33 | bus_LV_5613-10_1_3_node_73 | 0.4 | n |  | TRUE
34 | bus_LV_5613-10_1_3_node_69 | 0.4 | n |  | TRUE
35 | bus_LV_5613-10_1_3_node_59 | 0.4 | n |  | TRUE
36 | bus_LV_5613-10_1_3_node_60 | 0.4 | n |  | TRUE
37 | bus_LV_5613-10_1_3_node_62 | 0.4 | n |  | TRUE
38 | bus_LV_5613-10_1_3_node_74 | 0.4 | n |  | TRUE
39 | bus_LV_5613-10_1_3_node_67 | 0.4 | n |  | TRUE
40 | bus_LV_5613-10_1_3_node_117 | 0.4 | n |  | TRUE
41 | bus_LV_5613-10_1_3_node_105 | 0.4 | n |  | TRUE
42 | bus_LV_5613-10_1_3_node_149 | 0.4 | n |  | TRUE
43 | bus_LV_5613-10_1_3_node_108 | 0.4 | n |  | TRUE
44 | bus_LV_5613-10_1_3_node_112 | 0.4 | n |  | TRUE
45 | bus_LV_5613-10_1_3_node_114 | 0.4 | n |  | TRUE
46 | bus_LV_5613-10_1_3_node_110 | 0.4 | n |  | TRUE
47 | bus_LV_5613-10_1_3_node_169 | 0.4 | n |  | TRUE
48 | bus_LV_5613-10_1_3_node_170 | 0.4 | n |  | TRUE
49 | bus_LV_5613-10_1_3_node_95 | 0.4 | n |  | TRUE
50 | bus_LV_5613-10_1_3_node_144 | 0.4 | n |  | TRUE
51 | bus_LV_5613-10_1_3_node_147 | 0.4 | n |  | TRUE
52 | bus_LV_5613-10_1_3_node_87 | 0.4 | n |  | TRUE
53 | bus_LV_5613-10_1_3_node_88 | 0.4 | n |  | TRUE
54 | bus_LV_5613-10_1_3_node_89 | 0.4 | n |  | TRUE
55 | bus_LV_5613-10_1_3_node_90 | 0.4 | n |  | TRUE
56 | bus_LV_5613-10_1_3_node_91 | 0.4 | n |  | TRUE
57 | bus_LV_5613-10_1_3_node_109 | 0.4 | n |  | TRUE
58 | bus_LV_5613-10_1_3_node_115 | 0.4 | n |  | TRUE
59 | bus_LV_5613-10_1_3_node_157 | 0.4 | n |  | TRUE
60 | bus_LV_5613-10_1_3_node_154 | 0.4 | n |  | TRUE
61 | bus_LV_5613-10_1_3_node_116 | 0.4 | n |  | TRUE
62 | bus_LV_5613-10_1_3_node_96 | 0.4 | n |  | TRUE
63 | bus_LV_5613-10_1_3_node_92 | 0.4 | n |  | TRUE
64 | bus_LV_5613-10_1_3_node_93 | 0.4 | n |  | TRUE
65 | bus_LV_5613-10_1_3_node_94 | 0.4 | n |  | TRUE
66 | bus_LV_5613-10_1_3_node_97 | 0.4 | n |  | TRUE
67 | bus_LV_5613-10_1_3_node_201 | 0.4 | n |  | TRUE
68 | bus_LV_5613-10_1_3_node_198 | 0.4 | n |  | TRUE
69 | bus_LV_5613-10_1_3_node_206 | 0.4 | n |  | TRUE
70 | bus_LV_5613-10_1_3_node_146 | 0.4 | n |  | TRUE
71 | bus_LV_5613-10_1_3_node_202 | 0.4 | n |  | TRUE
72 | bus_LV_5613-10_1_3_node_200 | 0.4 | n |  | TRUE
73 | bus_LV_5613-10_1_3_node_196 | 0.4 | n |  | TRUE
74 | bus_LV_5613-10_1_3_node_155 | 0.4 | n |  | TRUE
75 | bus_LV_5613-10_1_3_node_111 | 0.4 | n |  | TRUE
76 | bus_LV_5613-10_1_3_node_113 | 0.4 | n |  | TRUE
77 | bus_LV_5613-10_1_3_node_142 | 0.4 | n |  | TRUE
78 | bus_LV_5613-10_1_3_node_168 | 0.4 | n |  | TRUE
79 | bus_LV_5613-10_1_3_node_150 | 0.4 | n |  | TRUE
80 | bus_LV_5613-10_1_3_node_143 | 0.4 | n |  | TRUE
81 | bus_LV_5613-10_1_3_node_141 | 0.4 | n |  | TRUE
82 | bus_LV_5613-10_1_3_node_148 | 0.4 | n |  | TRUE
83 | bus_LV_5613-10_1_3_node_118 | 0.4 | n |  | TRUE
84 | bus_LV_5613-10_1_3_node_119 | 0.4 | n |  | TRUE
85 | bus_LV_5613-10_1_3_node_120 | 0.4 | n |  | TRUE
86 | bus_LV_5613-10_1_3_node_128 | 0.4 | n |  | TRUE
87 | bus_LV_5613-10_1_3_node_129 | 0.4 | n |  | TRUE
88 | bus_LV_5613-10_1_3_node_130 | 0.4 | n |  | TRUE
89 | bus_LV_5613-10_1_3_node_131 | 0.4 | n |  | TRUE
90 | bus_LV_5613-10_1_3_node_132 | 0.4 | n |  | TRUE
91 | bus_LV_5613-10_1_3_node_133 | 0.4 | n |  | TRUE
92 | bus_LV_5613-10_1_3_node_145 | 0.4 | n |  | TRUE
93 | bus_LV_5613-10_1_3_node_164 | 0.4 | n |  | TRUE
94 | bus_LV_5613-10_1_3_node_165 | 0.4 | n |  | TRUE
95 | bus_LV_5613-10_1_3_node_166 | 0.4 | n |  | TRUE
96 | bus_LV_5613-10_1_3_node_167 | 0.4 | n |  | TRUE
97 | bus_LV_5613-10_1_3_node_194 | 0.4 | n |  | TRUE
98 | bus_LV_5613-10_1_3_node_193 | 0.4 | n |  | TRUE
99 | bus_LV_5613-10_1_3_node_190 | 0.4 | n |  | TRUE
100 | bus_LV_5613-10_1_3_node_195 | 0.4 | n |  | TRUE
101 | bus_LV_5613-10_1_3_node_217 | 0.4 | n |  | TRUE
102 | bus_LV_5613-10_1_3_node_203 | 0.4 | n |  | TRUE
103 | bus_LV_5613-10_1_3_node_197 | 0.4 | n |  | TRUE
104 | bus_LV_5613-10_1_3_node_199 | 0.4 | n |  | TRUE
105 | bus_LV_5613-10_1_3_node_208 | 0.4 | n |  | TRUE
106 | bus_MV_384_1_node_153 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5613-10_1_3_load_21 | 0 | 0.0011994 | 0.0003006 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5613-10_1_3_load_7 | 2 | 0.0026808 | 0.00067188 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5613-10_1_3_load_11 | 4 | 0.00099146 | 0.00024848 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5613-10_1_3_load_12 | 5 | 0.0047194 | 0.0011828 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5613-10_1_3_load_27 | 6 | 0.0018556 | 0.00046505 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5613-10_1_3_load_28 | 8 | 0.0010147 | 0.00025431 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5613-10_1_3_load_22 | 9 | 0.002884 | 0.00072279 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5613-10_1_3_load_51 | 10 | 0.0069052 | 0.0017306 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5613-10_1_3_load_52 | 11 | 0.0039899 | 0.00099996 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5613-10_1_3_load_30 | 12 | 0.0038207 | 0.00095756 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5613-10_1_3_load_25 | 15 | 0.002723 | 0.00068245 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5613-10_1_3_load_64 | 19 | 0.0027748 | 0.00069544 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5613-10_1_3_load_68 | 20 | 0.0061072 | 0.0015306 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5613-10_1_3_load_56 | 26 | 0.025205 | 0.0063169 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5613-10_1_3_load_70 | 30 | 0.0030465 | 0.00076353 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5613-10_1_3_load_53 | 31 | 0.0031453 | 0.00078829 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5613-10_1_3_load_54 | 32 | 0.0033403 | 0.00083716 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5613-10_1_3_load_73 | 33 | 0.025184 | 0.0063116 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5613-10_1_3_load_69 | 34 | 0.0022696 | 0.00056881 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5613-10_1_3_load_59 | 35 | 0.0098752 | 0.002475 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5613-10_1_3_load_60 | 36 | 0.009873 | 0.0024744 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5613-10_1_3_load_62 | 37 | 0.0026514 | 0.00066449 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5613-10_1_3_load_74 | 38 | 0.0062528 | 0.0015671 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5613-10_1_3_load_67 | 39 | 0.0020923 | 0.00052437 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5613-10_1_3_load_105 | 41 | 0.0096842 | 0.0024271 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5613-10_1_3_load_149 | 42 | 0.003283 | 0.00082279 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5613-10_1_3_load_108 | 43 | 0.010702 | 0.0026821 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5613-10_1_3_load_114 | 45 | 0.0036149 | 0.00090597 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5613-10_1_3_load_110 | 46 | 0.0025059 | 0.00062803 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5613-10_1_3_load_170 | 48 | 0.0016693 | 0.00041836 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5613-10_1_3_load_144 | 50 | 0.0016646 | 0.00041718 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5613-10_1_3_load_87 | 52 | 0.0032476 | 0.00081392 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5613-10_1_3_load_88 | 53 | 0.0031143 | 0.00078052 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5613-10_1_3_load_89 | 54 | 0.0048779 | 0.0012225 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5613-10_1_3_load_90 | 55 | 0.0050737 | 0.0012716 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5613-10_1_3_load_91 | 56 | 0.004411 | 0.0011055 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5613-10_1_3_load_157 | 59 | 0.0034947 | 0.00087585 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5613-10_1_3_load_154 | 60 | 0.0029635 | 0.00074271 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5613-10_1_3_load_116 | 61 | 0.0077946 | 0.0019535 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5613-10_1_3_load_92 | 63 | 0.00098598 | 0.00024711 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5613-10_1_3_load_93 | 64 | 0.0036402 | 0.00091232 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5613-10_1_3_load_201 | 67 | 0.0067386 | 0.0016888 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5613-10_1_3_load_206 | 69 | 0.0033952 | 0.00085091 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5613-10_1_3_load_200 | 72 | 0.0059695 | 0.0014961 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5613-10_1_3_load_196 | 73 | 0.0050014 | 0.0012535 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5613-10_1_3_load_155 | 74 | 0.0049 | 0.0012281 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5613-10_1_3_load_111 | 75 | 0.0031543 | 0.00079054 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5613-10_1_3_load_168 | 78 | 0.0046286 | 0.00116 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5613-10_1_3_load_150 | 79 | 0.0020552 | 0.00051509 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5613-10_1_3_load_143 | 80 | 0.001449 | 0.00036315 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5613-10_1_3_load_141 | 81 | 0.0025572 | 0.00064089 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5613-10_1_3_load_148 | 82 | 0.0044618 | 0.0011182 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5613-10_1_3_load_118 | 83 | 0.0013747 | 0.00034453 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5613-10_1_3_load_119 | 84 | 0.0018398 | 0.00046109 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5613-10_1_3_load_128 | 86 | 0.0012216 | 0.00030616 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5613-10_1_3_load_129 | 87 | 0.0025158 | 0.00063052 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5613-10_1_3_load_131 | 89 | 0.0036616 | 0.00091768 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5613-10_1_3_load_132 | 90 | 0.00060542 | 0.00015173 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5613-10_1_3_load_133 | 91 | 0.0016476 | 0.00041293 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5613-10_1_3_load_145 | 92 | 0.0096703 | 0.0024236 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5613-10_1_3_load_164 | 93 | 0.0012425 | 0.0003114 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5613-10_1_3_load_166 | 95 | 0.011382 | 0.0028526 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5613-10_1_3_load_167 | 96 | 0.0033486 | 0.00083925 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5613-10_1_3_load_190 | 99 | 0.0031344 | 0.00078555 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5613-10_1_3_load_217 | 101 | 0.0029733 | 0.00074518 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5613-10_1_3_load_203 | 102 | 0.002263 | 0.00056717 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5613-10_1_3_load_199 | 104 | 0.0026494 | 0.00066401 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5613-10_1_3_load_208 | 105 | 0.0022145 | 0.00055502 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 91 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5613-10_1_3_line_0 |  | 0 | 1 | 0.020099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5613-10_1_3_line_1 |  | 1 | 12 | 0.096695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5613-10_1_3_line_2 |  | 2 | 3 | 0.013714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5613-10_1_3_line_3 |  | 3 | 4 | 0.0087507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5613-10_1_3_line_4 |  | 3 | 5 | 0.048941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_5613-10_1_3_line_5 |  | 4 | 6 | 0.048982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5613-10_1_3_line_6 |  | 5 | 7 | 0.027129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_5613-10_1_3_line_7 |  | 6 | 8 | 0.048849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5613-10_1_3_line_8 |  | 6 | 9 | 0.064884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5613-10_1_3_line_9 |  | 7 | 10 | 0.060903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_5613-10_1_3_line_10 |  | 7 | 11 | 0.025201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5613-10_1_3_line_11 |  | 8 | 16 | 0.01249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5613-10_1_3_line_12 |  | 10 | 26 | 0.010169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_5613-10_1_3_line_13 |  | 12 | 16 | 0.041803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5613-10_1_3_line_14 |  | 12 | 13 | 0.10212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5613-10_1_3_line_15 |  | 13 | 14 | 0.10359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5613-10_1_3_line_16 |  | 14 | 15 | 0.045333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5613-10_1_3_line_17 |  | 17 | 18 | 0.036994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5613-10_1_3_line_18 |  | 17 | 19 | 0.022866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5613-10_1_3_line_19 |  | 18 | 20 | 0.032223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_5613-10_1_3_line_20 |  | 18 | 21 | 0.024616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_5613-10_1_3_line_21 |  | 19 | 22 | 0.023816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5613-10_1_3_line_22 |  | 20 | 34 | 0.04301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_5613-10_1_3_line_23 |  | 21 | 33 | 0.022136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5613-10_1_3_line_24 |  | 21 | 27 | 0.043249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_5613-10_1_3_line_25 |  | 22 | 35 | 0.044873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5613-10_1_3_line_26 |  | 23 | 24 | 0.029783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5613-10_1_3_line_27 |  | 23 | 25 | 0.004478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5613-10_1_3_line_28 |  | 24 | 40 | 0.008515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5613-10_1_3_line_29 |  | 24 | 41 | 0.047562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5613-10_1_3_line_30 |  | 25 | 39 | 0.05494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5613-10_1_3_line_31 |  | 26 | 27 | 0.041675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_5613-10_1_3_line_32 |  | 27 | 31 | 0.011376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5613-10_1_3_line_33 |  | 28 | 29 | 0.06413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_5613-10_1_3_line_34 |  | 28 | 30 | 0.017482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_5613-10_1_3_line_35 |  | 29 | 47 | 0.018707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_5613-10_1_3_line_36 |  | 29 | 48 | 0.044726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5613-10_1_3_line_37 |  | 30 | 34 | 0.059448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_5613-10_1_3_line_38 |  | 31 | 32 | 0.032335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5613-10_1_3_line_39 |  | 35 | 36 | 0.035695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5613-10_1_3_line_40 |  | 36 | 37 | 0.041132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5613-10_1_3_line_41 |  | 37 | 38 | 0.024609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5613-10_1_3_line_42 |  | 40 | 42 | 0.0078284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5613-10_1_3_line_43 |  | 40 | 43 | 0.054674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5613-10_1_3_line_44 |  | 42 | 82 | 0.011188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5613-10_1_3_line_45 |  | 44 | 45 | 0.0061527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5613-10_1_3_line_46 |  | 44 | 46 | 0.010328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5613-10_1_3_line_47 |  | 45 | 79 | 0.0054504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5613-10_1_3_line_48 |  | 46 | 75 | 0.0057082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5613-10_1_3_line_49 |  | 47 | 49 | 0.010395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_5613-10_1_3_line_50 |  | 47 | 50 | 0.014528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_5613-10_1_3_line_51 |  | 48 | 51 | 0.019265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5613-10_1_3_line_52 |  | 49 | 64 | 0.046137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_5613-10_1_3_line_53 |  | 50 | 85 | 0.038002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_5613-10_1_3_line_54 |  | 51 | 70 | 0.02106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5613-10_1_3_line_55 |  | 52 | 53 | 0.019095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5613-10_1_3_line_56 |  | 52 | 54 | 0.023352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5613-10_1_3_line_57 |  | 53 | 55 | 0.00015188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5613-10_1_3_line_58 |  | 54 | 56 | 0.029196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5613-10_1_3_line_59 |  | 55 | 57 | 0.02506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5613-10_1_3_line_60 |  | 56 | 58 | 0.017048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5613-10_1_3_line_61 |  | 57 | 59 | 0.006616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5613-10_1_3_line_62 |  | 57 | 60 | 0.025005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5613-10_1_3_line_63 |  | 58 | 61 | 0.013066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5613-10_1_3_line_64 |  | 58 | 62 | 0.033269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5613-10_1_3_line_65 |  | 60 | 74 | 0.0016528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5613-10_1_3_line_66 |  | 62 | 67 | 0.033475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5613-10_1_3_line_67 |  | 62 | 65 | 0.061014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5613-10_1_3_line_68 |  | 63 | 64 | 0.011824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_5613-10_1_3_line_69 |  | 63 | 65 | 0.079954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_5613-10_1_3_line_70 |  | 65 | 66 | 0.061979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5613-10_1_3_line_71 |  | 66 | 68 | 0.014615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5613-10_1_3_line_72 |  | 66 | 69 | 0.01515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5613-10_1_3_line_73 |  | 67 | 71 | 0.043586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5613-10_1_3_line_74 |  | 68 | 72 | 0.031339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5613-10_1_3_line_75 |  | 68 | 73 | 0.057993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5613-10_1_3_line_76 |  | 70 | 92 | 0.016423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5613-10_1_3_line_77 |  | 71 | 102 | 0.0051225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5613-10_1_3_line_78 |  | 71 | 97 | 0.011001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5613-10_1_3_line_79 |  | 73 | 103 | 0.015534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5613-10_1_3_line_80 |  | 75 | 76 | 0.039642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5613-10_1_3_line_81 |  | 76 | 77 | 0.045564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5613-10_1_3_line_82 |  | 76 | 78 | 0.063888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5613-10_1_3_line_83 |  | 77 | 80 | 0.0173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_5613-10_1_3_line_84 |  | 77 | 81 | 0.048237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_5613-10_1_3_line_85 |  | 79 | 82 | 0.0045053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5613-10_1_3_line_86 |  | 80 | 90 | 0.0037363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_5613-10_1_3_line_87 |  | 81 | 85 | 0.045116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_5613-10_1_3_line_88 |  | 83 | 84 | 0.00093429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_5613-10_1_3_line_89 |  | 84 | 85 | 0.061604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_5613-10_1_3_line_90 |  | 86 | 87 | 0.0026514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5613-10_1_3_line_91 |  | 86 | 88 | 0.019797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5613-10_1_3_line_92 |  | 87 | 89 | 0.020959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_5613-10_1_3_line_93 |  | 88 | 90 | 0.012118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_5613-10_1_3_line_94 |  | 88 | 91 | 0.002901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_5613-10_1_3_line_95 |  | 93 | 94 | 0.043944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_5613-10_1_3_line_96 |  | 94 | 95 | 0.037683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_5613-10_1_3_line_97 |  | 94 | 96 | 0.015777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_5613-10_1_3_line_98 |  | 95 | 97 | 0.033577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_5613-10_1_3_line_99 |  | 97 | 98 | 0.026174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_5613-10_1_3_line_100 |  | 98 | 100 | 0.056356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_5613-10_1_3_line_101 |  | 98 | 99 | 0.014004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_5613-10_1_3_line_102 |  | 100 | 101 | 0.022479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_5613-10_1_3_line_103 |  | 102 | 105 | 0.01343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_5613-10_1_3_line_104 |  | 103 | 104 | 0.01689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5613-10_1_3_trafo_133 | 0.63 MVA 20/0.4 kV | 106 | 91 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2544936.1012 | 1149564.1667 | 2544951.9533 | 1149562.2651 | 2544956.033 | 1149562.9274
1 | 2544936.1012 | 1149564.1667 | 2544927.6409 | 1149564.2109 | 2544918.2915 | 1149560.2277 | 2544904.0377 | 1149552.2207 | 2544880.7845 | 1149544.9299 | 2544876.0553 | 1149542.4386 | 2544869.8771 | 1149541.8505 | 2544856.8616 | 1149545.8164 | 2544844.7719 | 1149547.4284
2 | 2544691.7119 | 1149513.6158 | 2544686.4672 | 1149510.1844 | 2544679.0206 | 1149510.1075
3 | 2544691.7119 | 1149513.6158 | 2544700.4574 | 1149513.9185
4 | 2544691.7119 | 1149513.6158 | 2544676.2649 | 1149513.6579 | 2544667.5711 | 1149516.695 | 2544649.8026 | 1149524.7739 | 2544645.7941 | 1149527.3512
5 | 2544748.844 | 1149521.0114 | 2544716.3601 | 1149516.4462 | 2544706.6804 | 1149514.134 | 2544700.4574 | 1149513.9185
6 | 2544622.2471 | 1149540.5471 | 2544629.1035 | 1149538.0826 | 2544645.7941 | 1149527.3512
7 | 2544793.6435 | 1149538.5837 | 2544786.8648 | 1149533.263 | 2544777.8826 | 1149528.3206 | 2544753.9293 | 1149521.726 | 2544748.844 | 1149521.0114
8 | 2544748.844 | 1149521.0114 | 2544760.5486 | 1149457.1919
9 | 2544622.2471 | 1149540.5471 | 2544634.7485 | 1149547.469 | 2544664.4252 | 1149568.6182 | 2544672.6099 | 1149574.6573
10 | 2544622.2471 | 1149540.5471 | 2544629.4873 | 1149549.7408 | 2544621.9219 | 1149560.9202
11 | 2544803.4683 | 1149546.2953 | 2544793.6435 | 1149538.5837
12 | 2544680.7923 | 1149580.6947 | 2544672.6099 | 1149574.6573
13 | 2544803.4683 | 1149546.2953 | 2544811.4852 | 1149548.9676 | 2544838.3275 | 1149548.2876 | 2544844.7719 | 1149547.4284
14 | 2544844.7719 | 1149547.4284 | 2544879.5739 | 1149451.4248
15 | 2544787.6213 | 1149415.8494 | 2544806.0432 | 1149425.3742 | 2544824.8827 | 1149436.8964 | 2544836.288 | 1149440.6604 | 2544849.1635 | 1149440.6534 | 2544863.4386 | 1149440.0556 | 2544871.2368 | 1149440.6399 | 2544875.6184 | 1149443.7236 | 2544879.5739 | 1149451.4248
16 | 2544787.6213 | 1149415.8494 | 2544795.5972 | 1149414.8757 | 2544832.8574 | 1149416.5458
17 | 2544783.1457 | 1149664.1443 | 2544764.1671 | 1149652.4457 | 2544752.825 | 1149642.9894
18 | 2544783.1457 | 1149664.1443 | 2544804.8291 | 1149671.404
19 | 2544752.825 | 1149642.9894 | 2544744.9345 | 1149647.3753 | 2544722.3386 | 1149652.6162
20 | 2544747.2161 | 1149629.1558 | 2544743.8735 | 1149629.6756 | 2544740.3279 | 1149630.6643 | 2544752.825 | 1149642.9894
21 | 2544827.4491 | 1149678.8566 | 2544811.1008 | 1149673.5038 | 2544804.8291 | 1149671.404
22 | 2544722.3386 | 1149652.6162 | 2544680.4406 | 1149662.3341
23 | 2544747.2161 | 1149629.1558 | 2544752.1381 | 1149628.399 | 2544759.3833 | 1149628.1435 | 2544768.8749 | 1149630.98
24 | 2544713.8447 | 1149606.0724 | 2544721.284 | 1149611.896 | 2544740.3279 | 1149630.6643 | 2544743.8735 | 1149629.6756 | 2544747.2161 | 1149629.1558
25 | 2544827.4491 | 1149678.8566 | 2544831.3937 | 1149671.9946 | 2544838.8245 | 1149670.2144 | 2544844.2687 | 1149666.129 | 2544846.1488 | 1149658.4966 | 2544849.8137 | 1149656.2951 | 2544860.1649 | 1149656.9879
26 | 2544883.7459 | 1149731.4127 | 2544886.3154 | 1149725.286 | 2544888.5427 | 1149716.1718 | 2544891.9136 | 1149702.8339
27 | 2544891.9136 | 1149702.8339 | 2544888.5848 | 1149699.8294
28 | 2544889.6753 | 1149737.5394 | 2544883.7459 | 1149731.4127
29 | 2544883.7459 | 1149731.4127 | 2544893.5714 | 1149733.7573 | 2544930.2103 | 1149741.5601
30 | 2544888.5848 | 1149699.8294 | 2544893.1393 | 1149694.9963 | 2544899.8245 | 1149697.314 | 2544912.2585 | 1149670.975 | 2544922.7208 | 1149677.0476
31 | 2544713.8447 | 1149606.0724 | 2544692.2379 | 1149589.1399 | 2544680.7923 | 1149580.6947
32 | 2544713.8447 | 1149606.0724 | 2544709.5169 | 1149609.6586 | 2544707.4008 | 1149610.812 | 2544704.3324 | 1149610.2621 | 2544704.1292 | 1149610.1585
33 | 2544605.6018 | 1149742.1295 | 2544605.1319 | 1149736.9644 | 2544604.1234 | 1149730.8371 | 2544601.4559 | 1149717.966 | 2544601.2017 | 1149716.2007 | 2544600.9567 | 1149713.7795 | 2544598.7731 | 1149710.9314 | 2544597.5146 | 1149708.4973 | 2544596.7056 | 1149705.681 | 2544596.5462 | 1149700.0573 | 2544598.58 | 1149694.9803 | 2544600.0641 | 1149691.0645 | 2544603.6347 | 1149686.1401 | 2544606.6411 | 1149682.4661
34 | 2544606.6411 | 1149682.4661 | 2544622.2849 | 1149674.6623
35 | 2544605.6018 | 1149742.1295 | 2544612.4438 | 1149740.6324 | 2544618.6901 | 1149740.2969 | 2544623.6259 | 1149742.7194
36 | 2544605.6018 | 1149742.1295 | 2544605.911 | 1149749.0303 | 2544605.3162 | 1149756.1285 | 2544604.1464 | 1149763.3208 | 2544599.0729 | 1149782.6111 | 2544598.1071 | 1149785.9361
37 | 2544680.4406 | 1149662.3341 | 2544680.1521 | 1149662.401 | 2544622.2849 | 1149674.6623
38 | 2544704.1292 | 1149610.1585 | 2544698.0535 | 1149607.0626 | 2544688.3017 | 1149603.5837 | 2544682.7809 | 1149603.5123 | 2544680.192 | 1149605.8373 | 2544679.3677 | 1149610.5363 | 2544679.8917 | 1149611.8245
39 | 2544895.5493 | 1149660.5893 | 2544895.5493 | 1149660.5893 | 2544885.2932 | 1149658.182 | 2544870.1177 | 1149657.6541 | 2544860.1649 | 1149656.9879
40 | 2544895.5493 | 1149660.5893 | 2544900.89 | 1149656.9273 | 2544916.3753 | 1149658.5974 | 2544922.5557 | 1149658.5964 | 2544924.122 | 1149656.0918 | 2544922.3407 | 1149653.5735 | 2544915.678 | 1149651.9304
41 | 2544891.7845 | 1149646.0383 | 2544915.678 | 1149651.9304
42 | 2544889.6753 | 1149737.5394 | 2544884.0523 | 1149737.2019 | 2544881.9326 | 1149736.6305
43 | 2544889.6753 | 1149737.5394 | 2544897.0389 | 1149741.0071 | 2544900.3175 | 1149743.5562 | 2544904.1554 | 1149746.8228 | 2544906.1042 | 1149752.5524 | 2544907.2074 | 1149765.6937 | 2544909.1982 | 1149773.5018 | 2544912.5811 | 1149782.9599
44 | 2544881.9326 | 1149736.6305 | 2544871.1301 | 1149733.7185
45 | 2544862.5926 | 1149721.9683 | 2544862.9023 | 1149728.1132
46 | 2544862.5926 | 1149721.9683 | 2544852.5998 | 1149719.3588
47 | 2544867.4067 | 1149731.1819 | 2544862.9023 | 1149728.1132
48 | 2544847.0768 | 1149717.9165 | 2544852.5998 | 1149719.3588
49 | 2544618.4655 | 1149751.7495 | 2544623.6259 | 1149742.7194
50 | 2544623.6259 | 1149742.7194 | 2544629.2583 | 1149734.9189 | 2544633.5367 | 1149732.5159
51 | 2544592.7331 | 1149804.4367 | 2544598.1071 | 1149785.9361
52 | 2544618.4655 | 1149751.7495 | 2544623.2516 | 1149764.59 | 2544633.995 | 1149792.3947 | 2544635.2542 | 1149794.6982
53 | 2544669.4623 | 1149720.4857 | 2544653.6805 | 1149724.9666 | 2544638.2328 | 1149729.8781 | 2544633.5367 | 1149732.5159
54 | 2544592.7331 | 1149804.4367 | 2544586.5927 | 1149824.5817
55 | 2544825.5865 | 1149828.197 | 2544837.6984 | 1149826.0851 | 2544844.4695 | 1149825.46
56 | 2544803.2012 | 1149834.8296 | 2544824.8443 | 1149828.3265 | 2544825.5865 | 1149828.197
57 | 2544844.6207 | 1149825.446 | 2544844.4695 | 1149825.46
58 | 2544803.2012 | 1149834.8296 | 2544797.1751 | 1149836.6403 | 2544775.9867 | 1149845.3374
59 | 2544869.6415 | 1149825.0361 | 2544852.9402 | 1149824.6779 | 2544844.6207 | 1149825.446
60 | 2544760.2889 | 1149851.9872 | 2544773.7098 | 1149846.272 | 2544775.9867 | 1149845.3374
61 | 2544869.6415 | 1149825.0361 | 2544870.1184 | 1149818.4393
62 | 2544869.6415 | 1149825.0361 | 2544876.8441 | 1149825.1924 | 2544894.5315 | 1149827.1975
63 | 2544760.2889 | 1149851.9872 | 2544758.5204 | 1149847.5122 | 2544756.7203 | 1149846.2836 | 2544750.6235 | 1149846.1618
64 | 2544729.6003 | 1149865.0427 | 2544760.2889 | 1149851.9872
65 | 2544896.1738 | 1149827.3837 | 2544894.5315 | 1149827.1975
66 | 2544729.6003 | 1149865.0427 | 2544735.469 | 1149871.2476 | 2544744.829 | 1149877.2648 | 2544756.4182 | 1149884.7695
67 | 2544670.38 | 1149879.3949 | 2544677.9132 | 1149877.9248 | 2544688.1023 | 1149876.4192 | 2544703.184 | 1149871.8225 | 2544729.6003 | 1149865.0427
68 | 2544635.2542 | 1149794.6982 | 2544640.9261 | 1149805.0731
69 | 2544670.38 | 1149879.3949 | 2544643.821 | 1149811.4699 | 2544640.937 | 1149805.0931 | 2544640.9261 | 1149805.0731
70 | 2544670.38 | 1149879.3949 | 2544677.9132 | 1149877.9248 | 2544682.2555 | 1149887.6122 | 2544683.7953 | 1149890.5885 | 2544686.962 | 1149893.4943 | 2544695.2108 | 1149898.0542 | 2544719.2983 | 1149909.372
71 | 2544731.4647 | 1149917.5201 | 2544719.2983 | 1149909.372
72 | 2544719.2983 | 1149909.372 | 2544722.7093 | 1149907.9622 | 2544726.2732 | 1149906.4731 | 2544733.5017 | 1149908.8081
73 | 2544792.3917 | 1149909.3117 | 2544783.9312 | 1149902.5858 | 2544756.4182 | 1149884.7695
74 | 2544761.3493 | 1149925.6054 | 2544742.1306 | 1149917.7778 | 2544731.4647 | 1149917.5201
75 | 2544731.4647 | 1149917.5201 | 2544740.8812 | 1149923.8369 | 2544757.1326 | 1149942.0973 | 2544769.3735 | 1149960.6285
76 | 2544586.5927 | 1149824.5817 | 2544577.3777 | 1149820.9981 | 2544571.0577 | 1149819.3346
77 | 2544792.3917 | 1149909.3117 | 2544797.4783 | 1149908.7056
78 | 2544799.2566 | 1149917.8309 | 2544797.011 | 1149914.0718 | 2544792.3917 | 1149909.3117
79 | 2544777.9351 | 1149973.5896 | 2544769.3735 | 1149960.6285
80 | 2544807.8727 | 1149712.4096 | 2544840.7134 | 1149716.2548 | 2544847.0768 | 1149717.9165
81 | 2544807.8727 | 1149712.4096 | 2544762.2011 | 1149710.8726
82 | 2544807.8727 | 1149712.4096 | 2544812.3739 | 1149725.1973 | 2544831.4724 | 1149739.1183 | 2544833.5797 | 1149742.0339 | 2544833.6832 | 1149746.6132 | 2544831.6255 | 1149749.1111 | 2544817.0017 | 1149753.5533
83 | 2544762.2011 | 1149710.8726 | 2544762.3117 | 1149723.7339 | 2544762.6191 | 1149728.1613
84 | 2544762.2011 | 1149710.8726 | 2544723.3958 | 1149712.9635 | 2544714.0757 | 1149713.9824
85 | 2544867.4067 | 1149731.1819 | 2544871.1301 | 1149733.7185 | 2544871.1301 | 1149733.7185
86 | 2544762.8779 | 1149731.8886 | 2544762.6191 | 1149728.1613
87 | 2544669.4623 | 1149720.4857 | 2544684.7816 | 1149717.4654 | 2544696.8588 | 1149715.8646 | 2544714.0757 | 1149713.9824
88 | 2544682.9735 | 1149752.8016 | 2544683.9076 | 1149752.819
89 | 2544669.4623 | 1149720.4857 | 2544677.4611 | 1149723.7027 | 2544683.1074 | 1149724.0843 | 2544690.6353 | 1149725.3602 | 2544695.4432 | 1149728.0619 | 2544696.4041 | 1149733.2002 | 2544694.7514 | 1149750.5024 | 2544690.9506 | 1149752.9497 | 2544683.9076 | 1149752.819
90 | 2544774.4903 | 1149760.7025 | 2544774.2366 | 1149758.0633
91 | 2544772.2194 | 1149738.3729 | 2544772.5458 | 1149740.471 | 2544774.2366 | 1149758.0633
92 | 2544775.4573 | 1149781.6105 | 2544775.5424 | 1149771.6489 | 2544774.4903 | 1149760.7025
93 | 2544772.2194 | 1149738.3729 | 2544765.3271 | 1149736.0794 | 2544762.8779 | 1149731.8886
94 | 2544775.0137 | 1149739.181 | 2544772.2194 | 1149738.3729
95 | 2544861.4486 | 1149906.9213 | 2544871.5783 | 1149864.1604
96 | 2544861.4486 | 1149906.9213 | 2544854.5553 | 1149906.9956 | 2544850.3513 | 1149909.8468 | 2544849.4792 | 1149914.3683 | 2544845.5208 | 1149920.5524 | 2544834.2615 | 1149919.2105 | 2544832.112 | 1149920.3292
97 | 2544875.9571 | 1149910.9571 | 2544872.4726 | 1149907.7095 | 2544861.4486 | 1149906.9213
98 | 2544799.2566 | 1149917.8309 | 2544810.4954 | 1149921.1295 | 2544830.1738 | 1149921.338 | 2544832.112 | 1149920.3292
99 | 2544799.2566 | 1149917.8309 | 2544812.2477 | 1149940.5682
100 | 2544850.3995 | 1149980.3615 | 2544836.4222 | 1149973.1192 | 2544828.3735 | 1149964.4107 | 2544817.0462 | 1149948.962 | 2544812.2477 | 1149940.5682
101 | 2544812.2477 | 1149940.5682 | 2544817.508 | 1149939.0525 | 2544825.2816 | 1149939.5258 | 2544826.0228 | 1149939.5121
102 | 2544829.8892 | 1149981.4947 | 2544846.0931 | 1149984.5922 | 2544850.3995 | 1149980.3615
103 | 2544810.8745 | 1149907.8837 | 2544801.2875 | 1149908.2517 | 2544797.4783 | 1149908.7056
104 | 2544777.9351 | 1149973.5896 | 2544789.5969 | 1149985.8076

## bus_geodata
| x | y | coords
0 | 2544956.033 | 1149562.9274
1 | 2544936.1012 | 1149564.1667
2 | 2544679.0207 | 1149510.1075
3 | 2544691.7119 | 1149513.6158
4 | 2544700.4574 | 1149513.9185
5 | 2544645.7941 | 1149527.3512
6 | 2544748.844 | 1149521.0114
7 | 2544622.2471 | 1149540.5471
8 | 2544793.6435 | 1149538.5837
9 | 2544760.5486 | 1149457.1919
10 | 2544672.6099 | 1149574.6573
11 | 2544621.9219 | 1149560.9202
12 | 2544844.7719 | 1149547.4284
13 | 2544879.5739 | 1149451.4248
14 | 2544787.6213 | 1149415.8494
15 | 2544832.8574 | 1149416.5458
16 | 2544803.4683 | 1149546.2953
17 | 2544783.1457 | 1149664.1443
18 | 2544752.825 | 1149642.9894
19 | 2544804.8291 | 1149671.404
20 | 2544722.3386 | 1149652.6162
21 | 2544747.2161 | 1149629.1558
22 | 2544827.4491 | 1149678.8566
23 | 2544891.9136 | 1149702.8339
24 | 2544883.7459 | 1149731.4127
25 | 2544888.5848 | 1149699.8294
26 | 2544680.7923 | 1149580.6947
27 | 2544713.8447 | 1149606.0724
28 | 2544606.6411 | 1149682.4661
29 | 2544605.6018 | 1149742.1295
30 | 2544622.2849 | 1149674.6623
31 | 2544704.1292 | 1149610.1585
32 | 2544679.8917 | 1149611.8245
33 | 2544768.8749 | 1149630.98
34 | 2544680.4406 | 1149662.3341
35 | 2544860.1649 | 1149656.9879
36 | 2544895.5493 | 1149660.5893
37 | 2544915.678 | 1149651.9304
38 | 2544891.7845 | 1149646.0383
39 | 2544922.7208 | 1149677.0476
40 | 2544889.6753 | 1149737.5394
41 | 2544930.2103 | 1149741.5601
42 | 2544881.9326 | 1149736.6305
43 | 2544912.5811 | 1149782.9599
44 | 2544862.5926 | 1149721.9683
45 | 2544862.9023 | 1149728.1132
46 | 2544852.5998 | 1149719.3588
47 | 2544623.6259 | 1149742.7194
48 | 2544598.1071 | 1149785.9361
49 | 2544618.4655 | 1149751.7495
50 | 2544633.5367 | 1149732.5159
51 | 2544592.7331 | 1149804.4367
52 | 2544825.5865 | 1149828.197
53 | 2544844.4695 | 1149825.46
54 | 2544803.2012 | 1149834.8296
55 | 2544844.6207 | 1149825.446
56 | 2544775.9867 | 1149845.3374
57 | 2544869.6415 | 1149825.0361
58 | 2544760.2889 | 1149851.9872
59 | 2544870.1184 | 1149818.4393
60 | 2544894.5315 | 1149827.1975
61 | 2544750.6235 | 1149846.1618
62 | 2544729.6003 | 1149865.0427
63 | 2544640.9261 | 1149805.0731
64 | 2544635.2542 | 1149794.6982
65 | 2544670.38 | 1149879.3949
66 | 2544719.2983 | 1149909.372
67 | 2544756.4182 | 1149884.7695
68 | 2544731.4647 | 1149917.5201
69 | 2544733.5017 | 1149908.8081
70 | 2544586.5927 | 1149824.5817
71 | 2544792.3917 | 1149909.3117
72 | 2544761.3493 | 1149925.6054
73 | 2544769.3735 | 1149960.6285
74 | 2544896.1738 | 1149827.3837
75 | 2544847.0768 | 1149717.9165
76 | 2544807.8727 | 1149712.4096
77 | 2544762.2011 | 1149710.8726
78 | 2544817.0017 | 1149753.5533
79 | 2544867.4067 | 1149731.1819
80 | 2544762.6191 | 1149728.1613
81 | 2544714.0757 | 1149713.9824
82 | 2544871.1301 | 1149733.7185
83 | 2544682.9735 | 1149752.8016
84 | 2544683.9076 | 1149752.819
85 | 2544669.4623 | 1149720.4857
86 | 2544774.2366 | 1149758.0633
87 | 2544774.4903 | 1149760.7025
88 | 2544772.2194 | 1149738.3729
89 | 2544775.4573 | 1149781.6105
90 | 2544762.8779 | 1149731.8886
91 | 2544775.0137 | 1149739.181
92 | 2544571.0577 | 1149819.3346
93 | 2544871.5783 | 1149864.1604
94 | 2544861.4486 | 1149906.9213
95 | 2544832.112 | 1149920.3292
96 | 2544875.9571 | 1149910.9571
97 | 2544799.2566 | 1149917.8309
98 | 2544812.2477 | 1149940.5682
99 | 2544826.0228 | 1149939.5121
100 | 2544850.3995 | 1149980.3615
101 | 2544829.8892 | 1149981.4947
102 | 2544797.4783 | 1149908.7056
103 | 2544777.9351 | 1149973.5896
104 | 2544789.5969 | 1149985.8076
105 | 2544810.8745 | 1149907.8837
106 | 2544772.2194 | 1149738.3729

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1