## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6455-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6455-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6455-1_0_4_node_84 | 0.4 | n |  | TRUE
3 | bus_LV_6455-1_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_6455-1_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_6455-1_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_6455-1_0_4_node_83 | 0.4 | n |  | TRUE
7 | bus_LV_6455-1_0_4_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_6455-1_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_6455-1_0_4_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_6455-1_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_6455-1_0_4_node_4 | 0.4 | n |  | TRUE
12 | bus_LV_6455-1_0_4_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_6455-1_0_4_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_6455-1_0_4_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_6455-1_0_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_6455-1_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_6455-1_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_6455-1_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_6455-1_0_4_node_54 | 0.4 | n |  | TRUE
20 | bus_LV_6455-1_0_4_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_6455-1_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_6455-1_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_6455-1_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_6455-1_0_4_node_92 | 0.4 | n |  | TRUE
25 | bus_LV_6455-1_0_4_node_50 | 0.4 | n |  | TRUE
26 | bus_LV_6455-1_0_4_node_63 | 0.4 | n |  | TRUE
27 | bus_LV_6455-1_0_4_node_57 | 0.4 | n |  | TRUE
28 | bus_LV_6455-1_0_4_node_58 | 0.4 | n |  | TRUE
29 | bus_LV_6455-1_0_4_node_61 | 0.4 | n |  | TRUE
30 | bus_LV_6455-1_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_6455-1_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_6455-1_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_6455-1_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_6455-1_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_6455-1_0_4_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_6455-1_0_4_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_6455-1_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_6455-1_0_4_node_55 | 0.4 | n |  | TRUE
39 | bus_LV_6455-1_0_4_node_78 | 0.4 | n |  | TRUE
40 | bus_LV_6455-1_0_4_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_6455-1_0_4_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_6455-1_0_4_node_56 | 0.4 | n |  | TRUE
43 | bus_LV_6455-1_0_4_node_79 | 0.4 | n |  | TRUE
44 | bus_LV_6455-1_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_6455-1_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_6455-1_0_4_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_6455-1_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_6455-1_0_4_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_6455-1_0_4_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_6455-1_0_4_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_6455-1_0_4_node_62 | 0.4 | n |  | TRUE
52 | bus_LV_6455-1_0_4_node_60 | 0.4 | n |  | TRUE
53 | bus_LV_6455-1_0_4_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_6455-1_0_4_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_6455-1_0_4_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_6455-1_0_4_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_6455-1_0_4_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_6455-1_0_4_node_93 | 0.4 | n |  | TRUE
59 | bus_LV_6455-1_0_4_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_6455-1_0_4_node_46 | 0.4 | n |  | TRUE
61 | bus_LV_6455-1_0_4_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_6455-1_0_4_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_6455-1_0_4_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_6455-1_0_4_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_6455-1_0_4_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_6455-1_0_4_node_91 | 0.4 | n |  | TRUE
67 | bus_LV_6455-1_0_4_node_59 | 0.4 | n |  | TRUE
68 | bus_LV_6455-1_0_4_node_85 | 0.4 | n |  | TRUE
69 | bus_LV_6455-1_0_4_node_86 | 0.4 | n |  | TRUE
70 | bus_LV_6455-1_0_4_node_81 | 0.4 | n |  | TRUE
71 | bus_LV_6455-1_0_4_node_82 | 0.4 | n |  | TRUE
72 | bus_LV_6455-1_0_4_node_68 | 0.4 | n |  | TRUE
73 | bus_LV_6455-1_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_6455-1_0_4_node_65 | 0.4 | n |  | TRUE
75 | bus_LV_6455-1_0_4_node_66 | 0.4 | n |  | TRUE
76 | bus_LV_6455-1_0_4_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_6455-1_0_4_node_69 | 0.4 | n |  | TRUE
78 | bus_LV_6455-1_0_4_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_6455-1_0_4_node_76 | 0.4 | n |  | TRUE
80 | bus_LV_6455-1_0_4_node_71 | 0.4 | n |  | TRUE
81 | bus_LV_6455-1_0_4_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_6455-1_0_4_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_6455-1_0_4_node_80 | 0.4 | n |  | TRUE
84 | bus_LV_6455-1_0_4_node_73 | 0.4 | n |  | TRUE
85 | bus_LV_6455-1_0_4_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_6455-1_0_4_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_6455-1_0_4_node_89 | 0.4 | n |  | TRUE
88 | bus_LV_6455-1_0_4_node_88 | 0.4 | n |  | TRUE
89 | bus_LV_6455-1_0_4_node_87 | 0.4 | n |  | TRUE
90 | bus_MV_325_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6455-1_0_4_load_0 | 0 | 0.011894 | 0.002981 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6455-1_0_4_load_84 | 2 | 0.0092739 | 0.0023242 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6455-1_0_4_load_3 | 4 | 0.0060772 | 0.0015231 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6455-1_0_4_load_6 | 5 | 0.0061526 | 0.001542 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6455-1_0_4_load_83 | 6 | 0.017427 | 0.0043676 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6455-1_0_4_load_10 | 7 | 0.0019166 | 0.00048035 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6455-1_0_4_load_7 | 8 | 0.0026712 | 0.00066947 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6455-1_0_4_load_8 | 10 | 0.0044403 | 0.0011129 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6455-1_0_4_load_5 | 12 | 0.012821 | 0.0032133 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6455-1_0_4_load_18 | 14 | 0.017441 | 0.0043712 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6455-1_0_4_load_19 | 15 | 0.0085011 | 0.0021306 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6455-1_0_4_load_9 | 16 | 0.008634 | 0.0021639 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6455-1_0_4_load_54 | 19 | 0.0052926 | 0.0013264 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6455-1_0_4_load_53 | 20 | 0.00055968 | 0.00014027 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6455-1_0_4_load_13 | 21 | 0.00099047 | 0.00024824 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6455-1_0_4_load_16 | 23 | 0.0014853 | 0.00037224 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6455-1_0_4_load_92 | 24 | 0.0086379 | 0.0021649 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6455-1_0_4_load_63 | 26 | 0.0058322 | 0.0014617 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6455-1_0_4_load_57 | 27 | 0.01461 | 0.0036616 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6455-1_0_4_load_58 | 28 | 0.0088044 | 0.0022066 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6455-1_0_4_load_20 | 30 | 0.030766 | 0.0077108 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6455-1_0_4_load_21 | 31 | 0.0019121 | 0.00047922 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6455-1_0_4_load_22 | 32 | 0.017073 | 0.004279 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6455-1_0_4_load_25 | 34 | 0.0074759 | 0.0018736 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6455-1_0_4_load_26 | 35 | 0.00279 | 0.00069925 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6455-1_0_4_load_24 | 36 | 0.0047672 | 0.0011948 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6455-1_0_4_load_55 | 38 | 0.0029012 | 0.00072712 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6455-1_0_4_load_34 | 41 | 0.0084755 | 0.0021242 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6455-1_0_4_load_56 | 42 | 0.0021078 | 0.00052825 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6455-1_0_4_load_36 | 44 | 0.0011034 | 0.00027654 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6455-1_0_4_load_28 | 46 | 0.0067101 | 0.0016817 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6455-1_0_4_load_29 | 47 | 0.0041236 | 0.0010335 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6455-1_0_4_load_30 | 48 | 0.0055666 | 0.0013951 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6455-1_0_4_load_31 | 49 | 0.013208 | 0.0033102 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6455-1_0_4_load_32 | 50 | 0.0094337 | 0.0023643 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6455-1_0_4_load_60 | 52 | 0.0043388 | 0.0010874 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6455-1_0_4_load_39 | 53 | 0.0009834 | 0.00024646 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6455-1_0_4_load_40 | 54 | 0.00098315 | 0.0002464 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6455-1_0_4_load_43 | 57 | 0.00098433 | 0.0002467 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6455-1_0_4_load_93 | 58 | 0.0029826 | 0.0007475 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6455-1_0_4_load_46 | 60 | 0.0029856 | 0.00074827 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6455-1_0_4_load_47 | 61 | 0.0014769 | 0.00037015 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6455-1_0_4_load_49 | 62 | 0.0014769 | 0.00037015 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6455-1_0_4_load_51 | 63 | 0.0029848 | 0.00074806 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6455-1_0_4_load_48 | 64 | 0.001476 | 0.00036993 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6455-1_0_4_load_52 | 65 | 0.0029832 | 0.00074767 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6455-1_0_4_load_91 | 66 | 0.0054802 | 0.0013735 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6455-1_0_4_load_59 | 67 | 0.0039473 | 0.00098929 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6455-1_0_4_load_85 | 68 | 0.01399 | 0.0035063 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6455-1_0_4_load_86 | 69 | 0.022117 | 0.0055431 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6455-1_0_4_load_82 | 71 | 0.0088861 | 0.0022271 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6455-1_0_4_load_68 | 72 | 0.0041527 | 0.0010408 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6455-1_0_4_load_64 | 73 | 0.0021125 | 0.00052944 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6455-1_0_4_load_65 | 74 | 0.0017022 | 0.00042662 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6455-1_0_4_load_67 | 76 | 0.0028156 | 0.00070565 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6455-1_0_4_load_69 | 77 | 0.0048322 | 0.0012111 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6455-1_0_4_load_70 | 78 | 0.001967 | 0.00049297 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6455-1_0_4_load_76 | 79 | 0.0054801 | 0.0013734 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6455-1_0_4_load_71 | 80 | 0.0018769 | 0.00047038 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6455-1_0_4_load_72 | 82 | 0.006423 | 0.0016098 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6455-1_0_4_load_80 | 83 | 0.0050121 | 0.0012561 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6455-1_0_4_load_73 | 84 | 0.0038835 | 0.00097328 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6455-1_0_4_load_75 | 85 | 0.0026795 | 0.00067155 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6455-1_0_4_load_77 | 86 | 0.015535 | 0.0038934 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6455-1_0_4_load_89 | 87 | 0.007123 | 0.0017852 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6455-1_0_4_load_88 | 88 | 0.0044255 | 0.0011091 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6455-1_0_4_load_87 | 89 | 0.007295 | 0.0018283 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6455-1_0_4_line_0 |  | 0 | 1 | 0.013339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6455-1_0_4_line_1 |  | 0 | 2 | 0.065246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6455-1_0_4_line_2 |  | 1 | 3 | 0.042586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6455-1_0_4_line_3 |  | 1 | 4 | 0.026858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6455-1_0_4_line_4 |  | 2 | 5 | 0.016934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6455-1_0_4_line_5 |  | 2 | 6 | 0.024314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6455-1_0_4_line_6 |  | 3 | 7 | 0.061504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6455-1_0_4_line_7 |  | 3 | 8 | 0.028677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6455-1_0_4_line_8 |  | 5 | 11 | 0.020716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6455-1_0_4_line_9 |  | 6 | 68 | 0.024881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_6455-1_0_4_line_10 |  | 7 | 9 | 0.020877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6455-1_0_4_line_11 |  | 8 | 10 | 0.03679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6455-1_0_4_line_12 |  | 9 | 17 | 0.043192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6455-1_0_4_line_13 |  | 9 | 18 | 0.10262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6455-1_0_4_line_14 |  | 10 | 16 | 0.0022799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6455-1_0_4_line_15 |  | 11 | 12 | 0.020988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6455-1_0_4_line_16 |  | 13 | 14 | 0.029133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6455-1_0_4_line_17 |  | 13 | 15 | 0.024031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6455-1_0_4_line_18 |  | 15 | 26 | 0.039357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6455-1_0_4_line_19 |  | 17 | 19 | 0.042348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6455-1_0_4_line_20 |  | 17 | 20 | 0.018757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6455-1_0_4_line_21 |  | 18 | 21 | 0.017035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6455-1_0_4_line_22 |  | 19 | 24 | 0.022712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6455-1_0_4_line_23 |  | 20 | 25 | 0.0011369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6455-1_0_4_line_24 |  | 21 | 22 | 0.019105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6455-1_0_4_line_25 |  | 22 | 23 | 0.0044393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6455-1_0_4_line_26 |  | 24 | 66 | 0.019534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6455-1_0_4_line_27 |  | 25 | 65 | 0.029237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6455-1_0_4_line_28 |  | 25 | 64 | 0.014388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6455-1_0_4_line_29 |  | 26 | 29 | 0.029927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6455-1_0_4_line_30 |  | 27 | 28 | 0.041632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6455-1_0_4_line_31 |  | 28 | 67 | 0.01697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_6455-1_0_4_line_32 |  | 29 | 52 | 0.026991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6455-1_0_4_line_33 |  | 30 | 31 | 0.022327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6455-1_0_4_line_34 |  | 30 | 32 | 0.0073201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6455-1_0_4_line_35 |  | 31 | 33 | 0.016152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6455-1_0_4_line_36 |  | 33 | 34 | 0.01668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6455-1_0_4_line_37 |  | 33 | 35 | 0.035865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_6455-1_0_4_line_38 |  | 34 | 38 | 0.024107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6455-1_0_4_line_39 |  | 35 | 39 | 0.014003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_6455-1_0_4_line_40 |  | 36 | 37 | 0.026306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6455-1_0_4_line_41 |  | 37 | 40 | 0.025246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6455-1_0_4_line_42 |  | 37 | 41 | 0.016151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6455-1_0_4_line_43 |  | 38 | 42 | 0.012767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6455-1_0_4_line_44 |  | 39 | 43 | 0.027423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_6455-1_0_4_line_45 |  | 40 | 44 | 0.007314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6455-1_0_4_line_46 |  | 41 | 45 | 0.032888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6455-1_0_4_line_47 |  | 42 | 49 | 0.027466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6455-1_0_4_line_48 |  | 43 | 83 | 0.020721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_6455-1_0_4_line_49 |  | 45 | 50 | 0.050383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6455-1_0_4_line_50 |  | 46 | 47 | 0.013113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6455-1_0_4_line_51 |  | 46 | 48 | 0.035737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6455-1_0_4_line_52 |  | 47 | 49 | 0.014384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6455-1_0_4_line_53 |  | 48 | 50 | 0.0041683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6455-1_0_4_line_54 |  | 49 | 51 | 0.024558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6455-1_0_4_line_55 |  | 51 | 52 | 0.0047561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6455-1_0_4_line_56 |  | 53 | 54 | 0.00024065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6455-1_0_4_line_57 |  | 54 | 55 | 0.014518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6455-1_0_4_line_58 |  | 55 | 56 | 0.003601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6455-1_0_4_line_59 |  | 55 | 57 | 0.023641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6455-1_0_4_line_60 |  | 56 | 58 | 0.029274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6455-1_0_4_line_61 |  | 57 | 59 | 0.0032715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6455-1_0_4_line_62 |  | 59 | 60 | 0.029137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6455-1_0_4_line_63 |  | 59 | 61 | 0.010854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6455-1_0_4_line_64 |  | 61 | 62 | 0.016377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6455-1_0_4_line_65 |  | 62 | 63 | 0.028547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6455-1_0_4_line_66 |  | 62 | 64 | 0.013242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6455-1_0_4_line_67 |  | 67 | 70 | 0.0069904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_6455-1_0_4_line_68 |  | 68 | 69 | 0.019047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_6455-1_0_4_line_69 |  | 69 | 89 | 0.045719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_6455-1_0_4_line_70 |  | 70 | 71 | 0.02344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_6455-1_0_4_line_71 |  | 70 | 72 | 0.0060762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_6455-1_0_4_line_72 |  | 71 | 87 | 0.014548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_6455-1_0_4_line_73 |  | 72 | 75 | 0.034063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_6455-1_0_4_line_74 |  | 73 | 74 | 0.012169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_6455-1_0_4_line_75 |  | 73 | 75 | 0.016041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_6455-1_0_4_line_76 |  | 74 | 76 | 0.02893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_6455-1_0_4_line_77 |  | 75 | 77 | 0.0029223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_6455-1_0_4_line_78 |  | 76 | 78 | 0.014911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_6455-1_0_4_line_79 |  | 77 | 79 | 0.031886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_6455-1_0_4_line_80 |  | 78 | 80 | 0.011198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_6455-1_0_4_line_81 |  | 79 | 81 | 0.024817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_6455-1_0_4_line_82 |  | 80 | 82 | 0.011896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_6455-1_0_4_line_83 |  | 81 | 86 | 0.0072952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_6455-1_0_4_line_84 |  | 81 | 84 | 0.023616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_6455-1_0_4_line_85 |  | 82 | 83 | 0.022993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_6455-1_0_4_line_86 |  | 84 | 85 | 0.022299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_6455-1_0_4_line_87 |  | 87 | 88 | 0.016256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_6455-1_0_4_line_88 |  | 88 | 89 | 0.032919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6455-1_0_4_trafo_58 | 0.63 MVA 20/0.4 kV | 90 | 28 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2572049.804 | 1211493.0768 | 2572046.2935 | 1211505.9451
1 | 2572046.2935 | 1211505.9451 | 2572053.6233 | 1211570.7783
2 | 2572013.7046 | 1211470.3226 | 2572049.804 | 1211493.0768
3 | 2572049.804 | 1211493.0768 | 2572072.8681 | 1211506.8395
4 | 2572069.394 | 1211576.9455 | 2572053.6233 | 1211570.7783
5 | 2572035.0888 | 1211571.378 | 2572037.7861 | 1211564.585 | 2572053.6233 | 1211570.7783
6 | 2572013.7046 | 1211470.3226 | 2571961.6731 | 1211437.5289
7 | 2572013.7046 | 1211470.3226 | 2572005.535 | 1211482.8682 | 2571992.1665 | 1211479.8477
8 | 2572088.6875 | 1211584.4904 | 2572069.394 | 1211576.9455
9 | 2572035.0888 | 1211571.378 | 2572025.9068 | 1211594.5023
10 | 2571944.9711 | 1211425.0987 | 2571953.2487 | 1211432.2193 | 2571961.6731 | 1211437.5289
11 | 2571992.1665 | 1211479.8477 | 2571976.4716 | 1211476.3014 | 2571965.7823 | 1211494.0272
12 | 2571944.9711 | 1211425.0987 | 2571940.5627 | 1211428.0101 | 2571935.5559 | 1211431.3134 | 2571909.2987 | 1211449.4477
13 | 2571944.9711 | 1211425.0987 | 2572009.4227 | 1211345.2385
14 | 2571964.605 | 1211495.9796 | 2571965.7823 | 1211494.0272
15 | 2572088.6875 | 1211584.4904 | 2572086.955 | 1211597.4059 | 2572084.4501 | 1211604.9584
16 | 2572062.175 | 1211671.0752 | 2572034.9406 | 1211660.7296
17 | 2572062.175 | 1211671.0752 | 2572052.6343 | 1211693.1317
18 | 2572052.6343 | 1211693.1317 | 2572044.1964 | 1211712.6389 | 2572034.1499 | 1211727.6987
19 | 2571909.2987 | 1211449.4477 | 2571907.1403 | 1211450.9365 | 2571891.4716 | 1211463.5288 | 2571889.4506 | 1211465.1504 | 2571881.5073 | 1211472.4921 | 2571877.2665 | 1211477.0376
20 | 2571909.2987 | 1211449.4477 | 2571904.0126 | 1211443.4804 | 2571894.3258 | 1211438.7389
21 | 2572009.4227 | 1211345.2385 | 2572000.1471 | 1211330.9498
22 | 2571877.2665 | 1211477.0376 | 2571869.0261 | 1211485.8698 | 2571861.9446 | 1211493.8013
23 | 2571893.3047 | 1211438.2391 | 2571894.3258 | 1211438.7389
24 | 2571989.7446 | 1211314.9251 | 2572000.1471 | 1211330.9498
25 | 2571989.7446 | 1211314.9251 | 2571987.1197 | 1211311.3449
26 | 2571849.152 | 1211508.5618 | 2571857.5228 | 1211498.7538 | 2571861.9446 | 1211493.8013
27 | 2571893.3047 | 1211438.2391 | 2571884.3491 | 1211454.8575 | 2571874.9294 | 1211450.4663
28 | 2571893.3047 | 1211438.2391 | 2571880.3842 | 1211431.909
29 | 2572017.4652 | 1211752.5429 | 2572021.1477 | 1211747.1892 | 2572034.1499 | 1211727.6987
30 | 2571992.5741 | 1211644.6356 | 2571979.9325 | 1211639.8335 | 2571956.0387 | 1211632.1306 | 2571953.1508 | 1211631.3033
31 | 2571936.8375 | 1211626.6296 | 2571953.1508 | 1211631.3033
32 | 2572017.4652 | 1211752.5429 | 2572008.0425 | 1211744.1714 | 2571998.8766 | 1211737.0883 | 2571996.5508 | 1211735.5246
33 | 2571892.3722 | 1211747.0521 | 2571885.2833 | 1211732.5552 | 2571886.8231 | 1211726.5605
34 | 2571892.3722 | 1211747.0521 | 2571892.3722 | 1211747.0521 | 2571898.6612 | 1211750.7981
35 | 2571890.8413 | 1211710.9166 | 2571886.8231 | 1211726.5605
36 | 2571890.8413 | 1211710.9166 | 2571893.8208 | 1211711.1582 | 2571897.3476 | 1211711.4639 | 2571907.4613 | 1211712.3327
37 | 2571890.8413 | 1211710.9166 | 2571873.7633 | 1211709.73 | 2571864.7645 | 1211709.1056 | 2571855.0727 | 1211708.2994
38 | 2571907.4613 | 1211712.3327 | 2571931.4795 | 1211714.3957
39 | 2571841.1184 | 1211707.1387 | 2571855.0727 | 1211708.2994
40 | 2571883.5236 | 1211826.3167 | 2571890.3048 | 1211800.8993
41 | 2571859.0139 | 1211819.9847 | 2571883.5236 | 1211826.3167
42 | 2571883.5236 | 1211826.3167 | 2571899.1686 | 1211830.326
43 | 2571931.4795 | 1211714.3957 | 2571944.1994 | 1211715.4883
44 | 2571841.1184 | 1211707.1387 | 2571836.8771 | 1211706.7808 | 2571813.9218 | 1211703.1208
45 | 2571859.0139 | 1211819.9847 | 2571851.9102 | 1211818.2436
46 | 2571930.3742 | 1211831.8207 | 2571921.5201 | 1211836.0538 | 2571899.1686 | 1211830.326
47 | 2571970.9788 | 1211721.2552 | 2571959.8782 | 1211717.9946 | 2571948.9958 | 1211715.9003 | 2571944.1994 | 1211715.4883
48 | 2571813.9218 | 1211703.1208 | 2571822.4304 | 1211684.2279
49 | 2571930.3742 | 1211831.8207 | 2571947.7429 | 1211784.526
50 | 2571966.02 | 1211734.7578 | 2571961.4994 | 1211747.0673
51 | 2571949.1799 | 1211780.6132 | 2571961.4994 | 1211747.0673
52 | 2571970.9788 | 1211721.2552 | 2571966.02 | 1211734.7578
53 | 2571947.7429 | 1211784.526 | 2571949.1799 | 1211780.6132
54 | 2571992.6037 | 1211732.871 | 2571985.3553 | 1211728.0135 | 2571973.6363 | 1211722.5101 | 2571970.9788 | 1211721.2552
55 | 2571992.6037 | 1211732.871 | 2571996.5508 | 1211735.5246
56 | 2571825.9176 | 1211389.2462 | 2571826.019 | 1211389.028
57 | 2571819.7972 | 1211402.4112 | 2571825.9176 | 1211389.2462
58 | 2571816.5829 | 1211400.77 | 2571819.7972 | 1211402.4112
59 | 2571819.7972 | 1211402.4112 | 2571841.0911 | 1211412.6818
60 | 2571816.5829 | 1211400.77 | 2571808.1555 | 1211418.1642 | 2571799.0111 | 1211414.172
61 | 2571844.0377 | 1211414.103 | 2571841.0911 | 1211412.6818
62 | 2571844.0377 | 1211414.103 | 2571835.5783 | 1211431.175 | 2571826.4399 | 1211426.838
63 | 2571844.0377 | 1211414.103 | 2571853.7851 | 1211418.8781
64 | 2571868.4923 | 1211426.0829 | 2571853.7851 | 1211418.8781
65 | 2571868.4923 | 1211426.0829 | 2571859.7345 | 1211442.7338 | 2571850.931 | 1211438.5064
66 | 2571868.4923 | 1211426.0829 | 2571880.3842 | 1211431.909
67 | 2571930.1175 | 1211624.7043 | 2571936.8375 | 1211626.6296
68 | 2572007.8958 | 1211588.3076 | 2572025.9068 | 1211594.5023 | 2572025.9068 | 1211594.5023
69 | 2571970.1299 | 1211562.5403 | 2572007.8958 | 1211588.3076
70 | 2571930.1175 | 1211624.7043 | 2571937.3963 | 1211602.4231
71 | 2571930.1175 | 1211624.7043 | 2571924.2759 | 1211623.0322
72 | 2571941.9137 | 1211588.5948 | 2571941.9137 | 1211588.5948 | 2571937.3963 | 1211602.4231
73 | 2571891.5284 | 1211613.6582 | 2571924.2759 | 1211623.0322
74 | 2571885.7591 | 1211628.6259 | 2571881.3825 | 1211639.9805
75 | 2571891.5284 | 1211613.6582 | 2571885.7591 | 1211628.6259
76 | 2571881.3825 | 1211639.9805 | 2571870.9776 | 1211666.9745
77 | 2571891.5284 | 1211613.6582 | 2571888.7188 | 1211612.8545
78 | 2571856.9249 | 1211667.0372 | 2571866.3846 | 1211669.3531 | 2571870.9776 | 1211666.9745 | 2571870.9776 | 1211666.9745
79 | 2571888.7188 | 1211612.8545 | 2571876.3119 | 1211609.3054 | 2571864.1049 | 1211605.1052 | 2571858.631 | 1211602.4769
80 | 2571856.9249 | 1211667.0372 | 2571846.048 | 1211664.3743
81 | 2571837.2958 | 1211589.9347 | 2571841.3301 | 1211593.1063 | 2571853.375 | 1211599.9531 | 2571858.631 | 1211602.4769
82 | 2571846.048 | 1211664.3743 | 2571840.324 | 1211662.9729 | 2571834.6501 | 1211664.9342
83 | 2571837.2958 | 1211589.9347 | 2571831.56 | 1211585.4269
84 | 2571837.2958 | 1211589.9347 | 2571819.1917 | 1211605.0994
85 | 2571822.4304 | 1211684.2279 | 2571826.2449 | 1211675.758 | 2571834.6501 | 1211664.9342 | 2571834.6501 | 1211664.9342
86 | 2571802.0974 | 1211619.4183 | 2571819.1917 | 1211605.0994
87 | 2571941.9137 | 1211588.5948 | 2571952.5204 | 1211590.179 | 2571954.4309 | 1211584.9882
88 | 2571970.1299 | 1211562.5403 | 2571963.383 | 1211560.6666 | 2571954.4309 | 1211584.9882

## bus_geodata
| x | y | coords
0 | 2572046.2935 | 1211505.9451
1 | 2572049.804 | 1211493.0768
2 | 2572053.6233 | 1211570.7783
3 | 2572013.7046 | 1211470.3226
4 | 2572072.8681 | 1211506.8395
5 | 2572069.394 | 1211576.9455
6 | 2572035.0888 | 1211571.378
7 | 2571961.6731 | 1211437.5289
8 | 2571992.1665 | 1211479.8477
9 | 2571944.9711 | 1211425.0987
10 | 2571965.7823 | 1211494.0272
11 | 2572088.6875 | 1211584.4904
12 | 2572084.4501 | 1211604.9584
13 | 2572062.175 | 1211671.0752
14 | 2572034.9406 | 1211660.7296
15 | 2572052.6343 | 1211693.1317
16 | 2571964.605 | 1211495.9796
17 | 2571909.2987 | 1211449.4477
18 | 2572009.4227 | 1211345.2385
19 | 2571877.2665 | 1211477.0376
20 | 2571894.3258 | 1211438.7389
21 | 2572000.1471 | 1211330.9498
22 | 2571989.7446 | 1211314.9251
23 | 2571987.1197 | 1211311.3449
24 | 2571861.9446 | 1211493.8013
25 | 2571893.3047 | 1211438.2391
26 | 2572034.1499 | 1211727.6987
27 | 2571992.5741 | 1211644.6356
28 | 2571953.1508 | 1211631.3033
29 | 2572017.4652 | 1211752.5429
30 | 2571892.3722 | 1211747.0521
31 | 2571886.8231 | 1211726.5605
32 | 2571898.6612 | 1211750.7981
33 | 2571890.8413 | 1211710.9166
34 | 2571907.4613 | 1211712.3327
35 | 2571855.0727 | 1211708.2994
36 | 2571890.3048 | 1211800.8993
37 | 2571883.5236 | 1211826.3167
38 | 2571931.4795 | 1211714.3957
39 | 2571841.1184 | 1211707.1387
40 | 2571859.0139 | 1211819.9847
41 | 2571899.1686 | 1211830.326
42 | 2571944.1994 | 1211715.4883
43 | 2571813.9218 | 1211703.1208
44 | 2571851.9102 | 1211818.2436
45 | 2571930.3742 | 1211831.8207
46 | 2571961.4994 | 1211747.0673
47 | 2571966.02 | 1211734.7578
48 | 2571949.1799 | 1211780.6132
49 | 2571970.9788 | 1211721.2552
50 | 2571947.7429 | 1211784.526
51 | 2571992.6037 | 1211732.871
52 | 2571996.5508 | 1211735.5246
53 | 2571826.019 | 1211389.028
54 | 2571825.9176 | 1211389.2462
55 | 2571819.7972 | 1211402.4112
56 | 2571816.5829 | 1211400.77
57 | 2571841.0911 | 1211412.6818
58 | 2571799.0111 | 1211414.172
59 | 2571844.0377 | 1211414.103
60 | 2571826.4399 | 1211426.838
61 | 2571853.7851 | 1211418.8781
62 | 2571868.4923 | 1211426.0829
63 | 2571850.931 | 1211438.5064
64 | 2571880.3842 | 1211431.909
65 | 2571874.9294 | 1211450.4663
66 | 2571849.152 | 1211508.5618
67 | 2571936.8375 | 1211626.6296
68 | 2572025.9068 | 1211594.5023
69 | 2572007.8958 | 1211588.3076
70 | 2571930.1175 | 1211624.7043
71 | 2571937.3963 | 1211602.4231
72 | 2571924.2759 | 1211623.0322
73 | 2571885.7591 | 1211628.6259
74 | 2571881.3825 | 1211639.9805
75 | 2571891.5284 | 1211613.6581
76 | 2571870.9776 | 1211666.9745
77 | 2571888.7188 | 1211612.8545
78 | 2571856.9249 | 1211667.0372
79 | 2571858.631 | 1211602.4769
80 | 2571846.048 | 1211664.3743
81 | 2571837.2957 | 1211589.9347
82 | 2571834.6501 | 1211664.9342
83 | 2571822.4304 | 1211684.2279
84 | 2571819.1917 | 1211605.0994
85 | 2571802.0974 | 1211619.4183
86 | 2571831.56 | 1211585.4269
87 | 2571941.9137 | 1211588.5948
88 | 2571954.4309 | 1211584.9882
89 | 2571970.1299 | 1211562.5403
90 | 2571930.1175 | 1211624.7043

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1