## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_861-16_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_861-16_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_861-16_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_861-16_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_861-16_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_861-16_0_4_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_861-16_0_4_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_861-16_0_4_node_81 | 0.4 | n |  | TRUE
8 | bus_LV_861-16_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_861-16_0_4_node_80 | 0.4 | n |  | TRUE
10 | bus_LV_861-16_0_4_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_861-16_0_4_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_861-16_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_861-16_0_4_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_861-16_0_4_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_861-16_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_861-16_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_861-16_0_4_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_861-16_0_4_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_861-16_0_4_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_861-16_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_861-16_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_861-16_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_861-16_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_861-16_0_4_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_861-16_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_861-16_0_4_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_861-16_0_4_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_861-16_0_4_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_861-16_0_4_node_75 | 0.4 | n |  | TRUE
30 | bus_LV_861-16_0_4_node_79 | 0.4 | n |  | TRUE
31 | bus_LV_861-16_0_4_node_74 | 0.4 | n |  | TRUE
32 | bus_LV_861-16_0_4_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_861-16_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_861-16_0_4_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_861-16_0_4_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_861-16_0_4_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_861-16_0_4_node_68 | 0.4 | n |  | TRUE
38 | bus_LV_861-16_0_4_node_72 | 0.4 | n |  | TRUE
39 | bus_LV_861-16_0_4_node_41 | 0.4 | n |  | TRUE
40 | bus_LV_861-16_0_4_node_73 | 0.4 | n |  | TRUE
41 | bus_LV_861-16_0_4_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_861-16_0_4_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_861-16_0_4_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_861-16_0_4_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_861-16_0_4_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_861-16_0_4_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_861-16_0_4_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_861-16_0_4_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_861-16_0_4_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_861-16_0_4_node_60 | 0.4 | n |  | TRUE
51 | bus_LV_861-16_0_4_node_51 | 0.4 | n |  | TRUE
52 | bus_LV_861-16_0_4_node_66 | 0.4 | n |  | TRUE
53 | bus_LV_861-16_0_4_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_861-16_0_4_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_861-16_0_4_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_861-16_0_4_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_861-16_0_4_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_861-16_0_4_node_67 | 0.4 | n |  | TRUE
59 | bus_LV_861-16_0_4_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_861-16_0_4_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_861-16_0_4_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_861-16_0_4_node_47 | 0.4 | n |  | TRUE
63 | bus_LV_861-16_0_4_node_57 | 0.4 | n |  | TRUE
64 | bus_LV_861-16_0_4_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_861-16_0_4_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_861-16_0_4_node_70 | 0.4 | n |  | TRUE
67 | bus_LV_861-16_0_4_node_69 | 0.4 | n |  | TRUE
68 | bus_LV_861-16_0_4_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_861-16_0_4_node_59 | 0.4 | n |  | TRUE
70 | bus_LV_861-16_0_4_node_61 | 0.4 | n |  | TRUE
71 | bus_LV_861-16_0_4_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_861-16_0_4_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_861-16_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_861-16_0_4_node_65 | 0.4 | n |  | TRUE
75 | bus_LV_861-16_0_4_node_71 | 0.4 | n |  | TRUE
76 | bus_LV_861-16_0_4_node_76 | 0.4 | n |  | TRUE
77 | bus_LV_861-16_0_4_node_77 | 0.4 | n |  | TRUE
78 | bus_MV_121_0_node_169 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_861-16_0_4_load_0 | 0 | 0.015714 | 0.0039384 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_861-16_0_4_load_1 | 1 | 0.014885 | 0.0037304 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_861-16_0_4_load_81 | 7 | 0.032248 | 0.0080821 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_861-16_0_4_load_80 | 9 | 0.016938 | 0.0042451 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_861-16_0_4_load_26 | 10 | 0.014954 | 0.0037479 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_861-16_0_4_load_24 | 11 | 0.015107 | 0.0037863 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_861-16_0_4_load_9 | 12 | 0.021885 | 0.0054848 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_861-16_0_4_load_22 | 14 | 0.017097 | 0.0042849 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_861-16_0_4_load_8 | 16 | 0.019456 | 0.0048761 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_861-16_0_4_load_16 | 17 | 0.010389 | 0.0026038 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_861-16_0_4_load_11 | 20 | 0.016663 | 0.0041762 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_861-16_0_4_load_13 | 21 | 0.017565 | 0.0044023 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_861-16_0_4_load_20 | 23 | 0.014541 | 0.0036444 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_861-16_0_4_load_23 | 24 | 0.018061 | 0.0045265 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_861-16_0_4_load_21 | 25 | 0.014213 | 0.003562 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_861-16_0_4_load_27 | 26 | 0.015216 | 0.0038134 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_861-16_0_4_load_28 | 27 | 0.011259 | 0.0028218 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_861-16_0_4_load_29 | 28 | 0.014668 | 0.0036762 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_861-16_0_4_load_79 | 30 | 0.0034124 | 0.00085522 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_861-16_0_4_load_74 | 31 | 0.044366 | 0.011119 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_861-16_0_4_load_30 | 32 | 0.0025248 | 0.00063277 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_861-16_0_4_load_31 | 33 | 0.0028306 | 0.00070941 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_861-16_0_4_load_32 | 34 | 0.002758 | 0.00069123 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_861-16_0_4_load_33 | 35 | 0.0026353 | 0.00066047 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_861-16_0_4_load_34 | 36 | 0.0025959 | 0.00065061 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_861-16_0_4_load_68 | 37 | 0.0027259 | 0.00068318 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_861-16_0_4_load_72 | 38 | 0.0027937 | 0.00070016 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_861-16_0_4_load_73 | 40 | 0.0025719 | 0.00064459 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_861-16_0_4_load_35 | 41 | 0.0025326 | 0.00063472 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_861-16_0_4_load_36 | 42 | 0.0028082 | 0.00070381 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_861-16_0_4_load_39 | 45 | 0.0028301 | 0.00070929 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_861-16_0_4_load_40 | 46 | 0.0025497 | 0.00063902 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_861-16_0_4_load_48 | 47 | 0.0035206 | 0.00088234 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_861-16_0_4_load_45 | 48 | 0.0025499 | 0.00063906 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_861-16_0_4_load_42 | 49 | 0.0025364 | 0.00063568 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_861-16_0_4_load_60 | 50 | 0.0028096 | 0.00070416 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_861-16_0_4_load_66 | 52 | 0.0025774 | 0.00064597 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_861-16_0_4_load_46 | 53 | 0.0027843 | 0.00069781 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_861-16_0_4_load_43 | 54 | 0.0027771 | 0.00069601 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_861-16_0_4_load_49 | 57 | 0.0027791 | 0.00069652 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_861-16_0_4_load_67 | 58 | 0.0030433 | 0.00076273 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_861-16_0_4_load_44 | 59 | 0.0025834 | 0.00064746 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_861-16_0_4_load_54 | 60 | 0.0028054 | 0.0007031 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_861-16_0_4_load_55 | 61 | 0.0025511 | 0.00063936 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_861-16_0_4_load_47 | 62 | 0.0025746 | 0.00064525 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_861-16_0_4_load_57 | 63 | 0.0028028 | 0.00070244 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_861-16_0_4_load_56 | 64 | 0.002568 | 0.00064361 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_861-16_0_4_load_50 | 65 | 0.0030939 | 0.00077541 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_861-16_0_4_load_70 | 66 | 0.0026942 | 0.00067523 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_861-16_0_4_load_69 | 67 | 0.0026839 | 0.00067264 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_861-16_0_4_load_58 | 68 | 0.0027391 | 0.00068647 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_861-16_0_4_load_59 | 69 | 0.0026101 | 0.00065414 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_861-16_0_4_load_61 | 70 | 0.0026145 | 0.00065525 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_861-16_0_4_load_62 | 71 | 0.0027496 | 0.00068912 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_861-16_0_4_load_63 | 72 | 0.0030002 | 0.00075192 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_861-16_0_4_load_64 | 73 | 0.0026064 | 0.00065323 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_861-16_0_4_load_65 | 74 | 0.0028117 | 0.00070469 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_861-16_0_4_load_71 | 75 | 0.0027558 | 0.00069066 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_861-16_0_4_load_76 | 76 | 0.015377 | 0.0038539 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_861-16_0_4_load_77 | 77 | 0.013357 | 0.0033475 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_861-16_0_4_line_0 |  | 0 | 1 | 0.04037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_861-16_0_4_line_1 |  | 0 | 2 | 0.0063416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_861-16_0_4_line_2 |  | 1 | 3 | 0.034276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_861-16_0_4_line_3 |  | 2 | 4 | 0.060463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_861-16_0_4_line_4 |  | 3 | 5 | 0.00902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_861-16_0_4_line_5 |  | 3 | 6 | 0.014441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_861-16_0_4_line_6 |  | 4 | 7 | 0.017728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_861-16_0_4_line_7 |  | 4 | 8 | 0.043395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_861-16_0_4_line_8 |  | 5 | 9 | 0.020074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_861-16_0_4_line_9 |  | 6 | 10 | 0.013003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_861-16_0_4_line_10 |  | 6 | 11 | 0.0076557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_861-16_0_4_line_11 |  | 8 | 12 | 0.038368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_861-16_0_4_line_12 |  | 10 | 19 | 0.037988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_861-16_0_4_line_13 |  | 11 | 24 | 0.050731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_861-16_0_4_line_14 |  | 12 | 16 | 0.022179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_861-16_0_4_line_15 |  | 13 | 14 | 0.028754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_861-16_0_4_line_16 |  | 13 | 15 | 0.048625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_861-16_0_4_line_17 |  | 14 | 24 | 0.021442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_861-16_0_4_line_18 |  | 15 | 22 | 0.049633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_861-16_0_4_line_19 |  | 15 | 20 | 0.021609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_861-16_0_4_line_20 |  | 17 | 18 | 0.0095991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_861-16_0_4_line_21 |  | 18 | 19 | 0.014416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_861-16_0_4_line_22 |  | 19 | 26 | 0.0054111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_861-16_0_4_line_23 |  | 20 | 21 | 0.024193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_861-16_0_4_line_24 |  | 22 | 23 | 0.021712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_861-16_0_4_line_25 |  | 23 | 25 | 0.02104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_861-16_0_4_line_26 |  | 26 | 27 | 0.014795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_861-16_0_4_line_27 |  | 27 | 28 | 0.0059728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_861-16_0_4_line_28 |  | 28 | 29 | 0.023653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_861-16_0_4_line_29 |  | 29 | 30 | 0.042566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_861-16_0_4_line_30 |  | 29 | 31 | 0.040039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_861-16_0_4_line_31 |  | 30 | 77 | 0.037191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_861-16_0_4_line_32 |  | 31 | 56 | 0.11143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_861-16_0_4_line_33 |  | 32 | 33 | 0.0062512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_861-16_0_4_line_34 |  | 32 | 34 | 0.0118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_861-16_0_4_line_35 |  | 33 | 35 | 0.011834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_861-16_0_4_line_36 |  | 34 | 36 | 0.0062497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_861-16_0_4_line_37 |  | 35 | 37 | 0.0062537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_861-16_0_4_line_38 |  | 36 | 38 | 0.011792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_861-16_0_4_line_39 |  | 37 | 39 | 0.015908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_861-16_0_4_line_40 |  | 38 | 40 | 0.0062561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_861-16_0_4_line_41 |  | 39 | 51 | 0.021315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_861-16_0_4_line_42 |  | 39 | 52 | 0.0089884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_861-16_0_4_line_43 |  | 39 | 43 | 0.025776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_861-16_0_4_line_44 |  | 41 | 42 | 3.3328e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_861-16_0_4_line_45 |  | 41 | 43 | 0.015012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_861-16_0_4_line_46 |  | 42 | 44 | 0.0081852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_861-16_0_4_line_47 |  | 43 | 45 | 0.029194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_861-16_0_4_line_48 |  | 43 | 46 | 0.0091321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_861-16_0_4_line_49 |  | 44 | 47 | 0.015775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_861-16_0_4_line_50 |  | 44 | 48 | 0.013905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_861-16_0_4_line_51 |  | 45 | 49 | 0.006248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_861-16_0_4_line_52 |  | 46 | 50 | 0.0062492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_861-16_0_4_line_53 |  | 48 | 53 | 0.01133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_861-16_0_4_line_54 |  | 49 | 54 | 0.011999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_861-16_0_4_line_55 |  | 51 | 55 | 0.006565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_861-16_0_4_line_56 |  | 51 | 56 | 0.061406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_861-16_0_4_line_57 |  | 51 | 57 | 0.008562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_861-16_0_4_line_58 |  | 52 | 58 | 0.0062517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_861-16_0_4_line_59 |  | 53 | 62 | 0.0062481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_861-16_0_4_line_60 |  | 54 | 59 | 0.0062542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_861-16_0_4_line_61 |  | 55 | 66 | 0.013484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_861-16_0_4_line_62 |  | 57 | 65 | 0.0062543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_861-16_0_4_line_63 |  | 59 | 60 | 0.011524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_861-16_0_4_line_64 |  | 60 | 61 | 0.0062542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_861-16_0_4_line_65 |  | 62 | 63 | 0.012271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_861-16_0_4_line_66 |  | 63 | 64 | 0.0062513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_861-16_0_4_line_67 |  | 64 | 68 | 0.011133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_861-16_0_4_line_68 |  | 66 | 67 | 0.0062536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_861-16_0_4_line_69 |  | 67 | 75 | 0.011749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_861-16_0_4_line_70 |  | 68 | 69 | 0.0062522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_861-16_0_4_line_71 |  | 70 | 71 | 0.0062563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_861-16_0_4_line_72 |  | 70 | 72 | 0.011788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_861-16_0_4_line_73 |  | 71 | 73 | 0.011542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_861-16_0_4_line_74 |  | 72 | 74 | 0.0062501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_861-16_0_4_line_75 |  | 73 | 75 | 0.0062562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_861-16_0_4_line_76 |  | 76 | 77 | 0.024044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_861-16_0_4_trafo_25 | 0.63 MVA 20/0.4 kV | 78 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2604552.9122 | 1194450.5898 | 2604527.91 | 1194439.9163 | 2604525.7577 | 1194434.4451 | 2604528.2384 | 1194427.5732
1 | 2604558.7446 | 1194453.0796 | 2604552.9122 | 1194450.5898
2 | 2604538.2527 | 1194395.3449 | 2604530.6793 | 1194414.894 | 2604531.4308 | 1194418.7299 | 2604528.2384 | 1194427.5732
3 | 2604526.8411 | 1194483.6386 | 2604556.7246 | 1194464.3063 | 2604560.9781 | 1194461.9971 | 2604568.8069 | 1194457.3784 | 2604558.7446 | 1194453.0796
4 | 2604546.777 | 1194398.364 | 2604538.2527 | 1194395.3449
5 | 2604524.7773 | 1194390.0543 | 2604538.2527 | 1194395.3449
6 | 2604526.8411 | 1194483.6386 | 2604523.4696 | 1194478.2888 | 2604512.7288 | 1194474.3565
7 | 2604493.2487 | 1194511.0059 | 2604503.4806 | 1194502.4089 | 2604513.4232 | 1194493.5005 | 2604519.9267 | 1194488.1136 | 2604526.8411 | 1194483.6386
8 | 2604546.777 | 1194398.364 | 2604565.5975 | 1194405.3474
9 | 2604524.7773 | 1194390.0543 | 2604529.5445 | 1194377.9564
10 | 2604524.7773 | 1194390.0543 | 2604522.025 | 1194397.1981
11 | 2604493.2487 | 1194511.0059 | 2604498.4895 | 1194512.9886 | 2604529.1323 | 1194524.5882
12 | 2604551.0972 | 1194347.7516 | 2604545.5581 | 1194357.2302 | 2604542.7522 | 1194359.685 | 2604539.0928 | 1194362.1947 | 2604535.1433 | 1194365.449 | 2604532.6864 | 1194369.9829 | 2604529.5445 | 1194377.9564
13 | 2604485.3565 | 1194426.7727 | 2604485.8447 | 1194425.433 | 2604516.158 | 1194412.4263 | 2604522.025 | 1194397.1981
14 | 2604549.8749 | 1194532.4402 | 2604529.1323 | 1194524.5882
15 | 2604468.1694 | 1194473.9345 | 2604478.0149 | 1194446.9182
16 | 2604468.1694 | 1194473.9345 | 2604465.9171 | 1194469.7195 | 2604462.7266 | 1194466.7155 | 2604426.148 | 1194451.6253
17 | 2604485.3565 | 1194426.7727 | 2604478.0149 | 1194446.9182
18 | 2604380.131 | 1194433.0265 | 2604390.0489 | 1194437.0358 | 2604426.148 | 1194451.6253
19 | 2604426.148 | 1194451.6253 | 2604434.1579 | 1194431.5556
20 | 2604564.7407 | 1194352.5199 | 2604573.7457 | 1194355.8443
21 | 2604551.0972 | 1194347.7516 | 2604564.7407 | 1194352.5199
22 | 2604551.0972 | 1194347.7516 | 2604553.0988 | 1194342.7243
23 | 2604436.9453 | 1194409.622 | 2604440.568 | 1194415.4945 | 2604434.1579 | 1194431.5556
24 | 2604380.131 | 1194433.0265 | 2604386.9612 | 1194412.4169
25 | 2604393.58 | 1194392.4449 | 2604386.9612 | 1194412.4169
26 | 2604558.5717 | 1194328.9789 | 2604553.0988 | 1194342.7243
27 | 2604560.7811 | 1194323.4298 | 2604558.5717 | 1194328.9789
28 | 2604571.1944 | 1194302.2204 | 2604568.2638 | 1194308.3103 | 2604562.7394 | 1194318.5115 | 2604560.7811 | 1194323.4298
29 | 2604571.1944 | 1194302.2204 | 2604596.9524 | 1194268.3331
30 | 2604571.1944 | 1194302.2204 | 2604548.5854 | 1194293.2987 | 2604532.8801 | 1194294.2319
31 | 2604596.9524 | 1194268.3331 | 2604569.902 | 1194257.896 | 2604572.5193 | 1194250.1282
32 | 2604441.9938 | 1194257.9901 | 2604523.4445 | 1194307.3763 | 2604532.8801 | 1194294.2319
33 | 2604442.7394 | 1194341.3314 | 2604439.4637 | 1194346.6556
34 | 2604433.2801 | 1194356.7059 | 2604439.4637 | 1194346.6556
35 | 2604448.9408 | 1194331.2522 | 2604442.7394 | 1194341.3314
36 | 2604430.0051 | 1194362.0288 | 2604433.2801 | 1194356.7059
37 | 2604448.9408 | 1194331.2522 | 2604452.2179 | 1194325.9259
38 | 2604430.0051 | 1194362.0288 | 2604423.826 | 1194372.0718
39 | 2604460.5541 | 1194312.3769 | 2604452.2179 | 1194325.9259
40 | 2604420.5477 | 1194377.4001 | 2604423.826 | 1194372.0718
41 | 2604460.5541 | 1194312.3769 | 2604442.4347 | 1194301.0687
42 | 2604460.5541 | 1194312.3769 | 2604465.1522 | 1194304.6536
43 | 2604460.5541 | 1194312.3769 | 2604482.4282 | 1194326.1113
44 | 2604495.2693 | 1194333.8867 | 2604495.2978 | 1194333.9039
45 | 2604482.4282 | 1194326.1113 | 2604495.2693 | 1194333.8867
46 | 2604502.2994 | 1194338.1435 | 2604495.2978 | 1194333.9039
47 | 2604482.4282 | 1194326.1113 | 2604467.3588 | 1194351.1149
48 | 2604482.4282 | 1194326.1113 | 2604487.1491 | 1194318.2941
49 | 2604512.1417 | 1194331.325 | 2604506.6409 | 1194340.6147 | 2604502.2994 | 1194338.1435
50 | 2604502.2994 | 1194338.1435 | 2604495.0421 | 1194350.0039
51 | 2604464.1336 | 1194356.4662 | 2604467.3588 | 1194351.1149
52 | 2604487.1491 | 1194318.2941 | 2604490.3797 | 1194312.9448
53 | 2604495.0421 | 1194350.0039 | 2604489.1286 | 1194359.668
54 | 2604464.1336 | 1194356.4662 | 2604457.94 | 1194366.7428
55 | 2604439.0017 | 1194306.6692 | 2604442.4347 | 1194301.0687
56 | 2604441.9938 | 1194257.9901 | 2604430.7734 | 1194273.7902 | 2604421.3217 | 1194288.4133 | 2604442.4347 | 1194301.0687
57 | 2604442.4347 | 1194301.0687 | 2604446.9103 | 1194293.7696
58 | 2604465.1522 | 1194304.6536 | 2604468.3502 | 1194299.2818
59 | 2604485.8675 | 1194364.9975 | 2604489.1286 | 1194359.668
60 | 2604454.7116 | 1194372.0994 | 2604457.94 | 1194366.7428
61 | 2604439.0017 | 1194306.6692 | 2604431.9051 | 1194318.1343
62 | 2604446.9103 | 1194293.7696 | 2604450.1797 | 1194288.4378
63 | 2604454.7116 | 1194372.0994 | 2604448.7629 | 1194381.9697
64 | 2604445.5346 | 1194387.3262 | 2604448.7629 | 1194381.9697
65 | 2604485.8675 | 1194364.9975 | 2604479.4627 | 1194375.4646
66 | 2604476.1999 | 1194380.7968 | 2604479.4627 | 1194375.4646
67 | 2604476.1999 | 1194380.7968 | 2604470.3892 | 1194390.2929
68 | 2604428.6138 | 1194323.4518 | 2604431.9051 | 1194318.1343
69 | 2604428.6138 | 1194323.4518 | 2604422.4303 | 1194333.4418
70 | 2604467.126 | 1194395.6259 | 2604470.3892 | 1194390.2929
71 | 2604409.7704 | 1194353.8949 | 2604413.0632 | 1194348.5752
72 | 2604409.7704 | 1194353.8949 | 2604403.5663 | 1194363.9182
73 | 2604419.1376 | 1194338.7614 | 2604413.0632 | 1194348.5752
74 | 2604400.2768 | 1194369.2326 | 2604403.5663 | 1194363.9182
75 | 2604419.1376 | 1194338.7614 | 2604422.4303 | 1194333.4418
76 | 2604580.1967 | 1194227.3432 | 2604572.5193 | 1194250.1282

## bus_geodata
| x | y | coords
0 | 2604552.9122 | 1194450.5898
1 | 2604528.2384 | 1194427.5732
2 | 2604558.7446 | 1194453.0796
3 | 2604538.2527 | 1194395.3449
4 | 2604526.8411 | 1194483.6386
5 | 2604546.777 | 1194398.364
6 | 2604524.7773 | 1194390.0543
7 | 2604512.7288 | 1194474.3565
8 | 2604493.2487 | 1194511.0059
9 | 2604565.5975 | 1194405.3474
10 | 2604529.5445 | 1194377.9564
11 | 2604522.025 | 1194397.1981
12 | 2604529.1323 | 1194524.5882
13 | 2604468.1694 | 1194473.9345
14 | 2604478.0149 | 1194446.9182
15 | 2604426.148 | 1194451.6253
16 | 2604549.8749 | 1194532.4402
17 | 2604573.7457 | 1194355.8443
18 | 2604564.7407 | 1194352.5199
19 | 2604551.0972 | 1194347.7516
20 | 2604434.1579 | 1194431.5556
21 | 2604436.9453 | 1194409.6221
22 | 2604380.131 | 1194433.0265
23 | 2604386.9612 | 1194412.4169
24 | 2604485.3565 | 1194426.7727
25 | 2604393.58 | 1194392.4449
26 | 2604553.0988 | 1194342.7243
27 | 2604558.5717 | 1194328.9789
28 | 2604560.7811 | 1194323.4298
29 | 2604571.1944 | 1194302.2204
30 | 2604596.9524 | 1194268.3331
31 | 2604532.8801 | 1194294.2319
32 | 2604439.4637 | 1194346.6556
33 | 2604442.7394 | 1194341.3314
34 | 2604433.2801 | 1194356.7059
35 | 2604448.9408 | 1194331.2522
36 | 2604430.0051 | 1194362.0288
37 | 2604452.2179 | 1194325.9259
38 | 2604423.826 | 1194372.0718
39 | 2604460.5541 | 1194312.3769
40 | 2604420.5477 | 1194377.4001
41 | 2604495.2693 | 1194333.8867
42 | 2604495.2978 | 1194333.9039
43 | 2604482.4282 | 1194326.1113
44 | 2604502.2994 | 1194338.1435
45 | 2604467.3588 | 1194351.1149
46 | 2604487.1491 | 1194318.2941
47 | 2604512.1417 | 1194331.325
48 | 2604495.0421 | 1194350.0039
49 | 2604464.1336 | 1194356.4662
50 | 2604490.3797 | 1194312.9448
51 | 2604442.4347 | 1194301.0687
52 | 2604465.1522 | 1194304.6536
53 | 2604489.1286 | 1194359.668
54 | 2604457.94 | 1194366.7428
55 | 2604439.0017 | 1194306.6692
56 | 2604441.9938 | 1194257.9901
57 | 2604446.9103 | 1194293.7696
58 | 2604468.3502 | 1194299.2818
59 | 2604454.7116 | 1194372.0994
60 | 2604448.7629 | 1194381.9697
61 | 2604445.5346 | 1194387.3262
62 | 2604485.8675 | 1194364.9975
63 | 2604479.4627 | 1194375.4646
64 | 2604476.1999 | 1194380.7968
65 | 2604450.1797 | 1194288.4378
66 | 2604431.9051 | 1194318.1343
67 | 2604428.6138 | 1194323.4518
68 | 2604470.3892 | 1194390.2929
69 | 2604467.126 | 1194395.6259
70 | 2604409.7704 | 1194353.8949
71 | 2604413.0632 | 1194348.5752
72 | 2604403.5663 | 1194363.9182
73 | 2604419.1376 | 1194338.7614
74 | 2604400.2768 | 1194369.2326
75 | 2604422.4303 | 1194333.4418
76 | 2604580.1967 | 1194227.3432
77 | 2604572.5193 | 1194250.1282
78 | 2604538.2527 | 1194395.3449

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1