## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_863-1_2_2_node_52 | 0.4 | n |  | TRUE
1 | bus_LV_863-1_2_2_node_53 | 0.4 | n |  | TRUE
2 | bus_LV_863-1_2_2_node_131 | 0.4 | n |  | TRUE
3 | bus_LV_863-1_2_2_node_129 | 0.4 | n |  | TRUE
4 | bus_LV_863-1_2_2_node_58 | 0.4 | n |  | TRUE
5 | bus_LV_863-1_2_2_node_59 | 0.4 | n |  | TRUE
6 | bus_LV_863-1_2_2_node_144 | 0.4 | n |  | TRUE
7 | bus_LV_863-1_2_2_node_128 | 0.4 | n |  | TRUE
8 | bus_LV_863-1_2_2_node_130 | 0.4 | n |  | TRUE
9 | bus_LV_863-1_2_2_node_147 | 0.4 | n |  | TRUE
10 | bus_LV_863-1_2_2_node_136 | 0.4 | n |  | TRUE
11 | bus_LV_863-1_2_2_node_137 | 0.4 | n |  | TRUE
12 | bus_LV_863-1_2_2_node_138 | 0.4 | n |  | TRUE
13 | bus_LV_863-1_2_2_node_139 | 0.4 | n |  | TRUE
14 | bus_LV_863-1_2_2_node_140 | 0.4 | n |  | TRUE
15 | bus_LV_863-1_2_2_node_141 | 0.4 | n |  | TRUE
16 | bus_LV_863-1_2_2_node_366 | 0.4 | n |  | TRUE
17 | bus_LV_863-1_2_2_node_145 | 0.4 | n |  | TRUE
18 | bus_LV_863-1_2_2_node_296 | 0.4 | n |  | TRUE
19 | bus_LV_863-1_2_2_node_297 | 0.4 | n |  | TRUE
20 | bus_LV_863-1_2_2_node_231 | 0.4 | n |  | TRUE
21 | bus_LV_863-1_2_2_node_149 | 0.4 | n |  | TRUE
22 | bus_LV_863-1_2_2_node_150 | 0.4 | n |  | TRUE
23 | bus_LV_863-1_2_2_node_151 | 0.4 | n |  | TRUE
24 | bus_LV_863-1_2_2_node_238 | 0.4 | n |  | TRUE
25 | bus_LV_863-1_2_2_node_152 | 0.4 | n |  | TRUE
26 | bus_LV_863-1_2_2_node_153 | 0.4 | n |  | TRUE
27 | bus_LV_863-1_2_2_node_154 | 0.4 | n |  | TRUE
28 | bus_LV_863-1_2_2_node_200 | 0.4 | n |  | TRUE
29 | bus_LV_863-1_2_2_node_180 | 0.4 | n |  | TRUE
30 | bus_LV_863-1_2_2_node_181 | 0.4 | n |  | TRUE
31 | bus_LV_863-1_2_2_node_182 | 0.4 | n |  | TRUE
32 | bus_LV_863-1_2_2_node_188 | 0.4 | n |  | TRUE
33 | bus_LV_863-1_2_2_node_184 | 0.4 | n |  | TRUE
34 | bus_LV_863-1_2_2_node_186 | 0.4 | n |  | TRUE
35 | bus_LV_863-1_2_2_node_193 | 0.4 | n |  | TRUE
36 | bus_LV_863-1_2_2_node_189 | 0.4 | n |  | TRUE
37 | bus_LV_863-1_2_2_node_190 | 0.4 | n |  | TRUE
38 | bus_LV_863-1_2_2_node_191 | 0.4 | n |  | TRUE
39 | bus_LV_863-1_2_2_node_192 | 0.4 | n |  | TRUE
40 | bus_LV_863-1_2_2_node_346 | 0.4 | n |  | TRUE
41 | bus_LV_863-1_2_2_node_242 | 0.4 | n |  | TRUE
42 | bus_LV_863-1_2_2_node_194 | 0.4 | n |  | TRUE
43 | bus_LV_863-1_2_2_node_195 | 0.4 | n |  | TRUE
44 | bus_LV_863-1_2_2_node_196 | 0.4 | n |  | TRUE
45 | bus_LV_863-1_2_2_node_197 | 0.4 | n |  | TRUE
46 | bus_LV_863-1_2_2_node_198 | 0.4 | n |  | TRUE
47 | bus_LV_863-1_2_2_node_199 | 0.4 | n |  | TRUE
48 | bus_LV_863-1_2_2_node_201 | 0.4 | n |  | TRUE
49 | bus_LV_863-1_2_2_node_229 | 0.4 | n |  | TRUE
50 | bus_LV_863-1_2_2_node_230 | 0.4 | n |  | TRUE
51 | bus_LV_863-1_2_2_node_233 | 0.4 | n |  | TRUE
52 | bus_LV_863-1_2_2_node_271 | 0.4 | n |  | TRUE
53 | bus_LV_863-1_2_2_node_253 | 0.4 | n |  | TRUE
54 | bus_LV_863-1_2_2_node_232 | 0.4 | n |  | TRUE
55 | bus_LV_863-1_2_2_node_234 | 0.4 | n |  | TRUE
56 | bus_LV_863-1_2_2_node_236 | 0.4 | n |  | TRUE
57 | bus_LV_863-1_2_2_node_235 | 0.4 | n |  | TRUE
58 | bus_LV_863-1_2_2_node_239 | 0.4 | n |  | TRUE
59 | bus_LV_863-1_2_2_node_240 | 0.4 | n |  | TRUE
60 | bus_LV_863-1_2_2_node_241 | 0.4 | n |  | TRUE
61 | bus_LV_863-1_2_2_node_237 | 0.4 | n |  | TRUE
62 | bus_LV_863-1_2_2_node_260 | 0.4 | n |  | TRUE
63 | bus_LV_863-1_2_2_node_258 | 0.4 | n |  | TRUE
64 | bus_LV_863-1_2_2_node_255 | 0.4 | n |  | TRUE
65 | bus_LV_863-1_2_2_node_321 | 0.4 | n |  | TRUE
66 | bus_LV_863-1_2_2_node_310 | 0.4 | n |  | TRUE
67 | bus_LV_863-1_2_2_node_259 | 0.4 | n |  | TRUE
68 | bus_LV_863-1_2_2_node_251 | 0.4 | n |  | TRUE
69 | bus_LV_863-1_2_2_node_252 | 0.4 | n |  | TRUE
70 | bus_LV_863-1_2_2_node_254 | 0.4 | n |  | TRUE
71 | bus_LV_863-1_2_2_node_270 | 0.4 | n |  | TRUE
72 | bus_LV_863-1_2_2_node_256 | 0.4 | n |  | TRUE
73 | bus_LV_863-1_2_2_node_257 | 0.4 | n |  | TRUE
74 | bus_LV_863-1_2_2_node_261 | 0.4 | n |  | TRUE
75 | bus_LV_863-1_2_2_node_272 | 0.4 | n |  | TRUE
76 | bus_LV_863-1_2_2_node_273 | 0.4 | n |  | TRUE
77 | bus_LV_863-1_2_2_node_274 | 0.4 | n |  | TRUE
78 | bus_LV_863-1_2_2_node_336 | 0.4 | n |  | TRUE
79 | bus_LV_863-1_2_2_node_298 | 0.4 | n |  | TRUE
80 | bus_LV_863-1_2_2_node_309 | 0.4 | n |  | TRUE
81 | bus_LV_863-1_2_2_node_311 | 0.4 | n |  | TRUE
82 | bus_LV_863-1_2_2_node_312 | 0.4 | n |  | TRUE
83 | bus_LV_863-1_2_2_node_313 | 0.4 | n |  | TRUE
84 | bus_LV_863-1_2_2_node_338 | 0.4 | n |  | TRUE
85 | bus_LV_863-1_2_2_node_337 | 0.4 | n |  | TRUE
86 | bus_LV_863-1_2_2_node_339 | 0.4 | n |  | TRUE
87 | bus_LV_863-1_2_2_node_340 | 0.4 | n |  | TRUE
88 | bus_LV_863-1_2_2_node_341 | 0.4 | n |  | TRUE
89 | bus_LV_863-1_2_2_node_342 | 0.4 | n |  | TRUE
90 | bus_LV_863-1_2_2_node_343 | 0.4 | n |  | TRUE
91 | bus_LV_863-1_2_2_node_344 | 0.4 | n |  | TRUE
92 | bus_LV_863-1_2_2_node_345 | 0.4 | n |  | TRUE
93 | bus_MV_122_1_node_111 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_863-1_2_2_load_52 | 0 | 0.0020706 | 0.00051895 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_863-1_2_2_load_131 | 2 | 0.00106 | 0.00026567 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_863-1_2_2_load_129 | 3 | 0.00051294 | 0.00012856 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_863-1_2_2_load_58 | 4 | 0.00038166 | 9.5653e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_863-1_2_2_load_59 | 5 | 0.0009784 | 0.00024521 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_863-1_2_2_load_128 | 7 | 0.00071661 | 0.0001796 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_863-1_2_2_load_130 | 8 | 0.0017373 | 0.00043541 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_863-1_2_2_load_136 | 10 | 0.00062061 | 0.00015554 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_863-1_2_2_load_137 | 11 | 0.00060521 | 0.00015168 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_863-1_2_2_load_139 | 13 | 0.0012221 | 0.00030628 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_863-1_2_2_load_140 | 14 | 0.00033971 | 8.5139e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_863-1_2_2_load_141 | 15 | 0.00049096 | 0.00012305 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_863-1_2_2_load_366 | 16 | 0.00061914 | 0.00015517 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_863-1_2_2_load_145 | 17 | 0.0016657 | 0.00041746 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_863-1_2_2_load_231 | 20 | 0.0024438 | 0.00061247 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_863-1_2_2_load_150 | 22 | 0.0009597 | 0.00024052 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_863-1_2_2_load_151 | 23 | 0.00074889 | 0.00018769 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_863-1_2_2_load_152 | 25 | 0.0032643 | 0.00081811 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_863-1_2_2_load_153 | 26 | 0.00090495 | 0.0002268 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_863-1_2_2_load_180 | 29 | 0.0019562 | 0.00049028 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_863-1_2_2_load_181 | 30 | 0.0018918 | 0.00047414 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_863-1_2_2_load_182 | 31 | 0.0013973 | 0.00035019 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_863-1_2_2_load_188 | 32 | 0.0013835 | 0.00034673 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_863-1_2_2_load_184 | 33 | 0.0017263 | 0.00043264 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_863-1_2_2_load_186 | 34 | 0.0010495 | 0.00026303 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_863-1_2_2_load_193 | 35 | 0.0011594 | 0.00029057 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_863-1_2_2_load_189 | 36 | 0.001347 | 0.00033759 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_863-1_2_2_load_190 | 37 | 0.0014283 | 0.00035797 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_863-1_2_2_load_191 | 38 | 0.0010493 | 0.00026297 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_863-1_2_2_load_192 | 39 | 0.0011134 | 0.00027906 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_863-1_2_2_load_346 | 40 | 0.0012227 | 0.00030644 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_863-1_2_2_load_194 | 42 | 0.0027993 | 0.00070157 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_863-1_2_2_load_195 | 43 | 0.0015577 | 0.0003904 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_863-1_2_2_load_196 | 44 | 0.00096989 | 0.00024308 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_863-1_2_2_load_198 | 46 | 0.00046132 | 0.00011562 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_863-1_2_2_load_199 | 47 | 0.00065542 | 0.00016426 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_863-1_2_2_load_201 | 48 | 0.00092496 | 0.00023182 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_863-1_2_2_load_229 | 49 | 0.0022666 | 0.00056807 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_863-1_2_2_load_230 | 50 | 0.0010608 | 0.00026586 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_863-1_2_2_load_233 | 51 | 0.00074132 | 0.00018579 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_863-1_2_2_load_271 | 52 | 0.0016179 | 0.0004055 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_863-1_2_2_load_253 | 53 | 0.00061328 | 0.0001537 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_863-1_2_2_load_232 | 54 | 0.0015797 | 0.00039591 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_863-1_2_2_load_236 | 56 | 0.00031954 | 8.0084e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_863-1_2_2_load_239 | 58 | 0.0018432 | 0.00046194 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_863-1_2_2_load_240 | 59 | 0.00064535 | 0.00016174 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_863-1_2_2_load_241 | 60 | 0.0022041 | 0.00055239 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_863-1_2_2_load_260 | 62 | 0.0035098 | 0.00087964 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_863-1_2_2_load_258 | 63 | 0.0021243 | 0.00053239 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_863-1_2_2_load_255 | 64 | 0.001684 | 0.00042206 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_863-1_2_2_load_321 | 65 | 0.0016027 | 0.00040167 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_863-1_2_2_load_310 | 66 | 0.00047728 | 0.00011962 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_863-1_2_2_load_259 | 67 | 0.0012782 | 0.00032035 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_863-1_2_2_load_251 | 68 | 0.0023045 | 0.00057757 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_863-1_2_2_load_252 | 69 | 0.0055862 | 0.0014 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_863-1_2_2_load_254 | 70 | 0.0012625 | 0.00031641 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_863-1_2_2_load_270 | 71 | 0.00047206 | 0.00011831 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_863-1_2_2_load_256 | 72 | 0.00094468 | 0.00023676 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_863-1_2_2_load_257 | 73 | 0.0018311 | 0.00045891 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_863-1_2_2_load_261 | 74 | 0.00095694 | 0.00023983 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_863-1_2_2_load_273 | 76 | 0.0016962 | 0.00042512 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_863-1_2_2_load_274 | 77 | 0.0024201 | 0.00060652 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_863-1_2_2_load_336 | 78 | 0.0018072 | 0.00045294 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_863-1_2_2_load_298 | 79 | 0.0047445 | 0.0011891 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_863-1_2_2_load_309 | 80 | 0.0014464 | 0.00036249 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_863-1_2_2_load_311 | 81 | 0.0014342 | 0.00035943 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_863-1_2_2_load_312 | 82 | 0.0011237 | 0.00028162 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_863-1_2_2_load_313 | 83 | 0.0022429 | 0.00056212 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_863-1_2_2_load_338 | 84 | 0.0014487 | 0.00036308 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_863-1_2_2_load_337 | 85 | 0.0021164 | 0.00053042 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_863-1_2_2_load_339 | 86 | 0.0019371 | 0.00048548 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_863-1_2_2_load_340 | 87 | 0.001941 | 0.00048645 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_863-1_2_2_load_341 | 88 | 0.0019203 | 0.00048127 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_863-1_2_2_load_342 | 89 | 0.0019392 | 0.00048601 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_863-1_2_2_load_343 | 90 | 0.0014795 | 0.00037081 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_863-1_2_2_load_344 | 91 | 0.0011627 | 0.00029141 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_863-1_2_2_load_345 | 92 | 0.00082109 | 0.00020578 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_863-1_2_2_line_0 |  | 0 | 1 | 0.1367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_863-1_2_2_line_1 |  | 1 | 2 | 0.087337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_863-1_2_2_line_2 |  | 1 | 3 | 0.13874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_863-1_2_2_line_3 |  | 2 | 9 | 0.014126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_863-1_2_2_line_4 |  | 3 | 7 | 0.022357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_863-1_2_2_line_5 |  | 4 | 5 | 0.012121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_863-1_2_2_line_6 |  | 5 | 6 | 0.10425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_863-1_2_2_line_7 |  | 6 | 17 | 0.044978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_863-1_2_2_line_8 |  | 7 | 8 | 0.00056308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_863-1_2_2_line_9 |  | 9 | 19 | 0.086028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_863-1_2_2_line_10 |  | 9 | 20 | 0.1321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_863-1_2_2_line_11 |  | 10 | 11 | 0.0039843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_863-1_2_2_line_12 |  | 10 | 12 | 0.022758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_863-1_2_2_line_13 |  | 11 | 13 | 0.013316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_863-1_2_2_line_14 |  | 12 | 14 | 0.039055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_863-1_2_2_line_15 |  | 14 | 15 | 0.0072147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_863-1_2_2_line_16 |  | 15 | 16 | 0.19231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_863-1_2_2_line_17 |  | 16 | 79 | 0.10096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_863-1_2_2_line_18 |  | 17 | 18 | 0.11025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_863-1_2_2_line_19 |  | 18 | 27 | 0.02275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_863-1_2_2_line_20 |  | 19 | 79 | 0.020037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_863-1_2_2_line_21 |  | 20 | 28 | 0.045235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_863-1_2_2_line_22 |  | 21 | 22 | 0.014591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_863-1_2_2_line_23 |  | 21 | 23 | 0.02238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_863-1_2_2_line_24 |  | 22 | 24 | 0.026646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_863-1_2_2_line_25 |  | 24 | 64 | 0.013626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_863-1_2_2_line_26 |  | 24 | 61 | 0.089456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_863-1_2_2_line_27 |  | 25 | 26 | 0.039618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_863-1_2_2_line_28 |  | 26 | 27 | 0.020502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_863-1_2_2_line_29 |  | 27 | 28 | 0.064274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_863-1_2_2_line_30 |  | 28 | 50 | 0.029176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_863-1_2_2_line_31 |  | 28 | 45 | 0.037352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_863-1_2_2_line_32 |  | 29 | 30 | 0.011396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_863-1_2_2_line_33 |  | 29 | 31 | 0.044773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_863-1_2_2_line_34 |  | 30 | 32 | 0.029019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_863-1_2_2_line_35 |  | 31 | 33 | 0.024824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_863-1_2_2_line_36 |  | 32 | 36 | 0.038047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_863-1_2_2_line_37 |  | 33 | 34 | 0.0040922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_863-1_2_2_line_38 |  | 34 | 35 | 0.037609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_863-1_2_2_line_39 |  | 35 | 41 | 0.033394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_863-1_2_2_line_40 |  | 36 | 37 | 0.020541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_863-1_2_2_line_41 |  | 37 | 38 | 0.010869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_863-1_2_2_line_42 |  | 38 | 39 | 0.012205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_863-1_2_2_line_43 |  | 39 | 40 | 0.016363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_863-1_2_2_line_44 |  | 40 | 92 | 0.0071334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_863-1_2_2_line_45 |  | 41 | 67 | 0.074908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_863-1_2_2_line_46 |  | 41 | 63 | 0.011231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_863-1_2_2_line_47 |  | 42 | 43 | 0.040083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_863-1_2_2_line_48 |  | 42 | 44 | 0.040775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_863-1_2_2_line_49 |  | 43 | 45 | 0.030664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_863-1_2_2_line_50 |  | 44 | 46 | 0.036858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_863-1_2_2_line_51 |  | 45 | 47 | 0.022702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_863-1_2_2_line_52 |  | 46 | 48 | 0.0099473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_863-1_2_2_line_53 |  | 47 | 49 | 0.031459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_863-1_2_2_line_54 |  | 48 | 51 | 0.0099984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_863-1_2_2_line_55 |  | 49 | 52 | 0.058315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_863-1_2_2_line_56 |  | 50 | 53 | 0.0065292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_863-1_2_2_line_57 |  | 51 | 54 | 0.0015392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_863-1_2_2_line_58 |  | 52 | 75 | 0.014318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_863-1_2_2_line_59 |  | 53 | 68 | 0.0084528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_863-1_2_2_line_60 |  | 54 | 55 | 0.031761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_863-1_2_2_line_61 |  | 55 | 56 | 0.0043828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_863-1_2_2_line_62 |  | 56 | 60 | 0.0069448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_863-1_2_2_line_63 |  | 57 | 58 | 0.008396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_863-1_2_2_line_64 |  | 57 | 59 | 0.016458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_863-1_2_2_line_65 |  | 58 | 65 | 0.0066949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_863-1_2_2_line_66 |  | 59 | 66 | 0.021748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_863-1_2_2_line_67 |  | 60 | 62 | 0.020181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_863-1_2_2_line_68 |  | 61 | 62 | 0.046818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_863-1_2_2_line_69 |  | 61 | 63 | 0.1664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_863-1_2_2_line_70 |  | 64 | 72 | 0.041413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_863-1_2_2_line_71 |  | 65 | 78 | 0.013971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_863-1_2_2_line_72 |  | 66 | 80 | 0.012571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_863-1_2_2_line_73 |  | 67 | 74 | 0.0043211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_863-1_2_2_line_74 |  | 68 | 69 | 0.018951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_863-1_2_2_line_75 |  | 69 | 70 | 0.011735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_863-1_2_2_line_76 |  | 70 | 71 | 0.18107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_863-1_2_2_line_77 |  | 72 | 73 | 0.031123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_863-1_2_2_line_78 |  | 75 | 76 | 0.0023099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_863-1_2_2_line_79 |  | 75 | 77 | 0.015633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_863-1_2_2_line_80 |  | 76 | 78 | 0.020777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_863-1_2_2_line_81 |  | 80 | 81 | 0.011033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_863-1_2_2_line_82 |  | 81 | 82 | 0.010746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_863-1_2_2_line_83 |  | 82 | 83 | 0.011162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_863-1_2_2_line_84 |  | 83 | 84 | 0.013368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_863-1_2_2_line_85 |  | 84 | 85 | 0.0033331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_863-1_2_2_line_86 |  | 86 | 87 | 0.001635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_863-1_2_2_line_87 |  | 87 | 88 | 0.020998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_863-1_2_2_line_88 |  | 88 | 89 | 0.0026719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_863-1_2_2_line_89 |  | 89 | 90 | 0.018991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_863-1_2_2_line_90 |  | 90 | 91 | 0.0041901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_863-1_2_2_line_91 |  | 91 | 92 | 0.0036997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_863-1_2_2_trafo_233 | 0.63 MVA 20/0.4 kV | 93 | 51 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2604529.4616 | 1182070.7618 | 2604541.9572 | 1182045.0468 | 2604548.4195 | 1182031.2668 | 2604552.7722 | 1182020.4645 | 2604553.7092 | 1182013.1837 | 2604553.5078 | 1182006.7802 | 2604550.3455 | 1181987.9905 | 2604549.2061 | 1181979.9966 | 2604548.9513 | 1181973.671 | 2604549.1082 | 1181967.9793 | 2604550.3421 | 1181961.9327 | 2604553.2358 | 1181951.9075 | 2604554.631 | 1181944.5381 | 2604554.8593 | 1181940.3038
1 | 2604529.4616 | 1182070.7618 | 2604512.5938 | 1182103.088 | 2604507.3501 | 1182110.9659 | 2604501.4805 | 1182118.5321 | 2604481.8249 | 1182142.0964 | 2604481.1572 | 1182143.0318
2 | 2604529.4616 | 1182070.7618 | 2604533.1055 | 1182068.4633 | 2604538.7442 | 1182063.4427 | 2604544.3291 | 1182058.9557 | 2604551.2809 | 1182054.314 | 2604560.7989 | 1182048.685 | 2604568.5064 | 1182044.3552 | 2604572.8838 | 1182041.3014 | 2604576.9561 | 1182037.8471 | 2604584.0545 | 1182031.2379 | 2604590.6102 | 1182025.3287 | 2604639.5517 | 1181986.8426
3 | 2604472.951 | 1182154.5296 | 2604481.1572 | 1182143.0318
4 | 2604657.1257 | 1181973.0229 | 2604639.5517 | 1181986.8426
5 | 2604160.0107 | 1182360.8825 | 2604156.8202 | 1182361.7118 | 2604148.1723 | 1182363.47
6 | 2604226.2033 | 1182280.3401 | 2604160.0107 | 1182360.8825
7 | 2604226.2033 | 1182280.3401 | 2604242.7331 | 1182280.9185 | 2604271.1474 | 1182282.0892
8 | 2604657.5683 | 1181972.6749 | 2604657.1257 | 1181973.0229
9 | 2604472.951 | 1182154.5296 | 2604466.9064 | 1182151.0011 | 2604457.0793 | 1182151.5831 | 2604434.1973 | 1182160.4376 | 2604396.1103 | 1182184.111
10 | 2604472.951 | 1182154.5296 | 2604471.9048 | 1182165.1898 | 2604469.5136 | 1182177.4388 | 2604467.3857 | 1182184.552 | 2604465.0751 | 1182191.0758 | 2604461.0983 | 1182199.833 | 2604456.0223 | 1182208.2225 | 2604452.7433 | 1182212.9669 | 2604450.3886 | 1182217.0451 | 2604449.0653 | 1182220.3792 | 2604448.9251 | 1182224.0921 | 2604449.7165 | 1182227.739 | 2604451.4548 | 1182231.2865 | 2604459.3289 | 1182238.7405 | 2604461.5327 | 1182242.5774 | 2604462.7572 | 1182249.0928 | 2604462.1327 | 1182257.3855 | 2604460.4449 | 1182276.7737
11 | 2604258.8223 | 1181894.6143 | 2604261.9984 | 1181892.2087
12 | 2604237.8201 | 1181902.121 | 2604242.4932 | 1181901.913 | 2604254.5757 | 1181897.8305 | 2604258.8223 | 1181894.6143
13 | 2604272.6132 | 1181884.1694 | 2604261.9984 | 1181892.2087
14 | 2604237.8201 | 1181902.121 | 2604244.993 | 1181908.6626 | 2604260.0362 | 1181918.267 | 2604269.3055 | 1181918.9293 | 2604271.4516 | 1181918.418
15 | 2604278.4698 | 1181916.7458 | 2604271.4516 | 1181918.418
16 | 2604335.123 | 1182100.5246 | 2604278.4698 | 1181916.7458
17 | 2604377.6729 | 1182192.0796 | 2604335.123 | 1182100.5246
18 | 2604380.8694 | 1182280.7162 | 2604370.2243 | 1182282.9541 | 2604359.5414 | 1182284.714 | 2604348.8286 | 1182285.5179 | 2604337.9863 | 1182285.9326 | 2604308.1494 | 1182283.9438 | 2604276.495 | 1182282.3095 | 2604271.1474 | 1182282.0892
19 | 2604380.8694 | 1182280.7162 | 2604384.4967 | 1182290.5016 | 2604388.3251 | 1182296.6964 | 2604392.1938 | 1182299.9342
20 | 2604377.6729 | 1182192.0796 | 2604396.1103 | 1182184.111
21 | 2604452.9541 | 1182321.3338 | 2604457.5206 | 1182299.537 | 2604459.5993 | 1182286.4874 | 2604460.4449 | 1182276.7737
22 | 2604684.7141 | 1182099.9276 | 2604681.2979 | 1182114.1127
23 | 2604684.7141 | 1182099.9276 | 2604687.6292 | 1182102.0087 | 2604689.4444 | 1182104.6225 | 2604694.5262 | 1182118.9671 | 2604694.6372 | 1182119.3492
24 | 2604677.5361 | 1182140.4762 | 2604678.1902 | 1182133.8399 | 2604680.8382 | 1182116.0217 | 2604681.2979 | 1182114.1127
25 | 2604677.5361 | 1182140.4762 | 2604664.1363 | 1182138.0037
26 | 2604677.5361 | 1182140.4762 | 2604677.4475 | 1182146.557 | 2604678.9444 | 1182155.8963 | 2604683.6099 | 1182165.427 | 2604698.4872 | 1182190.3957 | 2604720.5864 | 1182216.5484
27 | 2604371.9866 | 1182296.4726 | 2604363.3898 | 1182294.9999 | 2604353.5639 | 1182294.1035 | 2604343.4778 | 1182294.1963 | 2604333.499 | 1182293.6 | 2604332.5581 | 1182293.5014
28 | 2604392.1938 | 1182299.9342 | 2604371.9866 | 1182296.4726
29 | 2604392.1938 | 1182299.9342 | 2604398.1015 | 1182302.5287 | 2604452.9541 | 1182321.3338
30 | 2604452.9541 | 1182321.3338 | 2604447.0384 | 1182349.9037
31 | 2604452.9541 | 1182321.3338 | 2604488.5329 | 1182333.0214
32 | 2604949.1562 | 1182410.6394 | 2604947.7791 | 1182416.9318 | 2604947.6687 | 1182421.8849
33 | 2604949.1562 | 1182410.6394 | 2604951.7488 | 1182398.7924 | 2604951.3242 | 1182376.3917 | 2604948.6947 | 1182366.4938
34 | 2604921.9453 | 1182435.3158 | 2604947.6687 | 1182421.8849
35 | 2604948.6947 | 1182366.4938 | 2604945.623 | 1182354.9316 | 2604937.0731 | 1182345.3245
36 | 2604910.6718 | 1182399.4272 | 2604913.2655 | 1182411.5455 | 2604917.3061 | 1182428.3574 | 2604921.9453 | 1182435.3158
37 | 2604937.0731 | 1182345.3245 | 2604934.3526 | 1182342.2676
38 | 2604904.0268 | 1182320.3638 | 2604910.4424 | 1182324.1428 | 2604929.9701 | 1182337.3432 | 2604934.3526 | 1182342.2676
39 | 2604875.2534 | 1182303.415 | 2604904.0268 | 1182320.3638
40 | 2604910.6718 | 1182399.4272 | 2604909.2341 | 1182392.7104 | 2604905.5497 | 1182379.5445
41 | 2604905.5497 | 1182379.5445 | 2604904.5292 | 1182375.8979 | 2604898.4531 | 1182372.2585
42 | 2604887.8498 | 1182369.4037 | 2604891.0369 | 1182367.8163 | 2604897.7831 | 1182371.8571 | 2604898.4531 | 1182372.2585
43 | 2604882.3977 | 1182383.9921 | 2604884.287 | 1182377.8938 | 2604885.6444 | 1182370.5022 | 2604887.8498 | 1182369.4037
44 | 2604882.3977 | 1182383.9921 | 2604881.5772 | 1182386.6405 | 2604882.5434 | 1182390.8929
45 | 2604875.2534 | 1182303.415 | 2604913.12 | 1182289.2827 | 2604940.5748 | 1182272.1628 | 2604942.584 | 1182271.4405
46 | 2604875.2534 | 1182303.415 | 2604866.7389 | 1182296.0909
47 | 2604555.2593 | 1182339.2853 | 2604555.2593 | 1182339.2853 | 2604550.3938 | 1182341.8941 | 2604545.2767 | 1182343.958 | 2604539.9692 | 1182345.4771 | 2604532.9059 | 1182346.5835 | 2604525.7517 | 1182346.7004 | 2604518.6593 | 1182345.8392 | 2604516.7496 | 1182345.0267
48 | 2604555.2593 | 1182339.2853 | 2604586.9147 | 1182313.5837
49 | 2604488.5329 | 1182333.0214 | 2604516.7496 | 1182345.0267
50 | 2604616.0611 | 1182291.0985 | 2604609.8535 | 1182294.9593 | 2604586.9147 | 1182313.5837
51 | 2604488.5329 | 1182333.0214 | 2604491.8349 | 1182328.1658 | 2604496.1404 | 1182318.7753 | 2604497.9501 | 1182312.5331
52 | 2604616.0611 | 1182291.0985 | 2604624.5079 | 1182285.845
53 | 2604500.943 | 1182281.4735 | 2604501.6923 | 1182286.3183 | 2604501.0742 | 1182296.1229 | 2604499.2176 | 1182308.161 | 2604497.9501 | 1182312.5331
54 | 2604632.9981 | 1182280.5644 | 2604624.5079 | 1182285.845
55 | 2604500.943 | 1182281.4735 | 2604499.861 | 1182274.4776 | 2604499.0499 | 1182266.5173 | 2604498.6648 | 1182260.6807 | 2604500.2801 | 1182254.8789 | 2604501.7183 | 1182251.2114 | 2604504.9959 | 1182248.3569 | 2604512.1648 | 1182249.1737 | 2604519.355 | 1182252.125 | 2604527.0488 | 1182254.6229
56 | 2604445.336 | 1182356.1823 | 2604446.1578 | 1182354.1567 | 2604447.0384 | 1182349.9037
57 | 2604634.3051 | 1182279.7515 | 2604632.9981 | 1182280.5644
58 | 2604540.6674 | 1182259.0444 | 2604527.0488 | 1182254.6229
59 | 2604442.1584 | 1182364.0151 | 2604445.336 | 1182356.1823
60 | 2604661.2781 | 1182262.9821 | 2604656.5191 | 1182265.9355 | 2604634.3051 | 1182279.7515
61 | 2604661.2781 | 1182262.9821 | 2604663.454 | 1182263.2394 | 2604665.6453 | 1182263.1966
62 | 2604672.198 | 1182261.0339 | 2604669.0435 | 1182262.4878 | 2604665.6453 | 1182263.1966
63 | 2604592.6989 | 1182262.5408 | 2604584.3218 | 1182261.9779
64 | 2604592.6989 | 1182262.5408 | 2604594.1859 | 1182246.1502
65 | 2604584.3218 | 1182261.9779 | 2604577.6419 | 1182261.529
66 | 2604594.1859 | 1182246.1502 | 2604594.7007 | 1182240.4754 | 2604592.6665 | 1182224.5546 | 2604592.6665 | 1182224.5546
67 | 2604672.198 | 1182261.0339 | 2604685.3596 | 1182245.7349
68 | 2604720.5864 | 1182216.5484 | 2604709.978 | 1182220.3866 | 2604702.8581 | 1182225.3948 | 2604685.3596 | 1182245.7349
69 | 2604720.5864 | 1182216.5484 | 2604866.7389 | 1182296.0909
70 | 2604664.1363 | 1182138.0037 | 2604652.5491 | 1182135.8658 | 2604622.9297 | 1182135.0605
71 | 2604563.7028 | 1182260.5923 | 2604577.6419 | 1182261.529
72 | 2604586.3015 | 1182213.714 | 2604592.6665 | 1182224.5546
73 | 2604942.584 | 1182271.4405 | 2604946.6503 | 1182269.9787
74 | 2604442.1584 | 1182364.0151 | 2604439.5797 | 1182370.3714 | 2604442.0296 | 1182382.2125 | 2604442.0296 | 1182382.2125
75 | 2604442.0296 | 1182382.2125 | 2604452.9857 | 1182386.4176
76 | 2604452.9857 | 1182386.4176 | 2604410.5646 | 1182562.4488
77 | 2604602.3502 | 1182151.0354 | 2604603.3806 | 1182141.4423 | 2604613.8461 | 1182134.8135 | 2604622.9297 | 1182135.0605
78 | 2604540.6674 | 1182259.0444 | 2604542.9721 | 1182259.1993
79 | 2604540.6674 | 1182259.0444 | 2604544.8533 | 1182243.9823
80 | 2604563.7028 | 1182260.5923 | 2604542.9721 | 1182259.1993
81 | 2604586.3015 | 1182213.714 | 2604580.7154 | 1182204.1999
82 | 2604571.8926 | 1182201.301 | 2604578.7576 | 1182200.8653 | 2604580.7154 | 1182204.1999
83 | 2604560.7527 | 1182202.0079 | 2604560.7527 | 1182202.0079 | 2604571.8926 | 1182201.301
84 | 2604560.7527 | 1182202.0079 | 2604555.3728 | 1182214.2451
85 | 2604554.0314 | 1182217.2963 | 2604555.3728 | 1182214.2451
86 | 2604889.5671 | 1182442.5502 | 2604889.3842 | 1182440.9255
87 | 2604889.3842 | 1182440.9255 | 2604887.0357 | 1182420.0596
88 | 2604886.7369 | 1182417.4045 | 2604887.0357 | 1182420.0596
89 | 2604886.7369 | 1182417.4045 | 2604884.94 | 1182401.4397 | 2604884.2917 | 1182398.5866
90 | 2604883.3632 | 1182394.5006 | 2604884.2917 | 1182398.5866
91 | 2604883.3632 | 1182394.5006 | 2604882.5434 | 1182390.8929

## bus_geodata
| x | y | coords
0 | 2604554.8593 | 1181940.3038
1 | 2604529.4616 | 1182070.7618
2 | 2604481.1572 | 1182143.0318
3 | 2604639.5517 | 1181986.8426
4 | 2604148.1723 | 1182363.47
5 | 2604160.0107 | 1182360.8825
6 | 2604226.2033 | 1182280.3401
7 | 2604657.1257 | 1181973.0229
8 | 2604657.5683 | 1181972.6749
9 | 2604472.951 | 1182154.5296
10 | 2604258.8223 | 1181894.6143
11 | 2604261.9984 | 1181892.2087
12 | 2604237.8201 | 1181902.121
13 | 2604272.6132 | 1181884.1694
14 | 2604271.4516 | 1181918.418
15 | 2604278.4698 | 1181916.7458
16 | 2604335.123 | 1182100.5246
17 | 2604271.1474 | 1182282.0892
18 | 2604380.8694 | 1182280.7162
19 | 2604396.1103 | 1182184.111
20 | 2604460.4449 | 1182276.7737
21 | 2604684.7141 | 1182099.9276
22 | 2604681.2979 | 1182114.1127
23 | 2604694.6372 | 1182119.3492
24 | 2604677.5361 | 1182140.4762
25 | 2604332.5581 | 1182293.5014
26 | 2604371.9866 | 1182296.4726
27 | 2604392.1938 | 1182299.9342
28 | 2604452.9541 | 1182321.3338
29 | 2604949.1562 | 1182410.6394
30 | 2604947.6687 | 1182421.8849
31 | 2604948.6947 | 1182366.4938
32 | 2604921.9453 | 1182435.3158
33 | 2604937.0731 | 1182345.3245
34 | 2604934.3526 | 1182342.2676
35 | 2604904.0268 | 1182320.3638
36 | 2604910.6718 | 1182399.4272
37 | 2604905.5497 | 1182379.5445
38 | 2604898.4531 | 1182372.2584
39 | 2604887.8498 | 1182369.4037
40 | 2604882.3977 | 1182383.9921
41 | 2604875.2534 | 1182303.415
42 | 2604555.2593 | 1182339.2853
43 | 2604516.7496 | 1182345.0267
44 | 2604586.9147 | 1182313.5837
45 | 2604488.5329 | 1182333.0214
46 | 2604616.0611 | 1182291.0985
47 | 2604497.9501 | 1182312.5331
48 | 2604624.5079 | 1182285.845
49 | 2604500.943 | 1182281.4735
50 | 2604447.0384 | 1182349.9037
51 | 2604632.9981 | 1182280.5644
52 | 2604527.0488 | 1182254.6229
53 | 2604445.336 | 1182356.1823
54 | 2604634.3051 | 1182279.7515
55 | 2604661.2781 | 1182262.9821
56 | 2604665.6453 | 1182263.1966
57 | 2604592.6989 | 1182262.5408
58 | 2604584.3218 | 1182261.9779
59 | 2604594.1859 | 1182246.1502
60 | 2604672.198 | 1182261.0339
61 | 2604720.5864 | 1182216.5484
62 | 2604685.3596 | 1182245.7349
63 | 2604866.7389 | 1182296.0909
64 | 2604664.1363 | 1182138.0037
65 | 2604577.6419 | 1182261.529
66 | 2604592.6665 | 1182224.5546
67 | 2604942.584 | 1182271.4405
68 | 2604442.1584 | 1182364.0151
69 | 2604442.0296 | 1182382.2125
70 | 2604452.9857 | 1182386.4176
71 | 2604410.5646 | 1182562.4488
72 | 2604622.9297 | 1182135.0605
73 | 2604602.3502 | 1182151.0354
74 | 2604946.6503 | 1182269.9787
75 | 2604540.6674 | 1182259.0444
76 | 2604542.9721 | 1182259.1993
77 | 2604544.8533 | 1182243.9823
78 | 2604563.7028 | 1182260.5923
79 | 2604377.6729 | 1182192.0796
80 | 2604586.3015 | 1182213.714
81 | 2604580.7154 | 1182204.1999
82 | 2604571.8926 | 1182201.301
83 | 2604560.7527 | 1182202.0079
84 | 2604555.3728 | 1182214.2451
85 | 2604554.0314 | 1182217.2963
86 | 2604889.5671 | 1182442.5502
87 | 2604889.3842 | 1182440.9255
88 | 2604887.0357 | 1182420.0596
89 | 2604886.7369 | 1182417.4045
90 | 2604884.2917 | 1182398.5866
91 | 2604883.3632 | 1182394.5006
92 | 2604882.5434 | 1182390.8929
93 | 2604661.2781 | 1182262.9821

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1