## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_97-11_0_12_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_97-11_0_12_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_97-11_0_12_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_97-11_0_12_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_97-11_0_12_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_97-11_0_12_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_97-11_0_12_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_97-11_0_12_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_97-11_0_12_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_97-11_0_12_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_97-11_0_12_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_97-11_0_12_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_97-11_0_12_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_97-11_0_12_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_97-11_0_12_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_97-11_0_12_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_97-11_0_12_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_97-11_0_12_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_97-11_0_12_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_97-11_0_12_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_97-11_0_12_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_97-11_0_12_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_97-11_0_12_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_97-11_0_12_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_97-11_0_12_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_97-11_0_12_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_97-11_0_12_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_97-11_0_12_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_97-11_0_12_node_62 | 0.4 | n |  | TRUE
29 | bus_LV_97-11_0_12_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_97-11_0_12_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_97-11_0_12_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_97-11_0_12_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_97-11_0_12_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_97-11_0_12_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_97-11_0_12_node_42 | 0.4 | n |  | TRUE
36 | bus_LV_97-11_0_12_node_52 | 0.4 | n |  | TRUE
37 | bus_LV_97-11_0_12_node_51 | 0.4 | n |  | TRUE
38 | bus_LV_97-11_0_12_node_50 | 0.4 | n |  | TRUE
39 | bus_LV_97-11_0_12_node_48 | 0.4 | n |  | TRUE
40 | bus_LV_97-11_0_12_node_47 | 0.4 | n |  | TRUE
41 | bus_LV_97-11_0_12_node_46 | 0.4 | n |  | TRUE
42 | bus_LV_97-11_0_12_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_97-11_0_12_node_53 | 0.4 | n |  | TRUE
44 | bus_LV_97-11_0_12_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_97-11_0_12_node_54 | 0.4 | n |  | TRUE
46 | bus_LV_97-11_0_12_node_19 | 0.4 | n |  | TRUE
47 | bus_LV_97-11_0_12_node_20 | 0.4 | n |  | TRUE
48 | bus_LV_97-11_0_12_node_32 | 0.4 | n |  | TRUE
49 | bus_LV_97-11_0_12_node_23 | 0.4 | n |  | TRUE
50 | bus_LV_97-11_0_12_node_24 | 0.4 | n |  | TRUE
51 | bus_LV_97-11_0_12_node_25 | 0.4 | n |  | TRUE
52 | bus_LV_97-11_0_12_node_56 | 0.4 | n |  | TRUE
53 | bus_LV_97-11_0_12_node_60 | 0.4 | n |  | TRUE
54 | bus_LV_97-11_0_12_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_97-11_0_12_node_59 | 0.4 | n |  | TRUE
56 | bus_LV_97-11_0_12_node_57 | 0.4 | n |  | TRUE
57 | bus_LV_97-11_0_12_node_31 | 0.4 | n |  | TRUE
58 | bus_MV_469_0_node_171 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_97-11_0_12_load_0 | 0 | 0.00090778 | 0.00022751 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_97-11_0_12_load_3 | 2 | 0.024211 | 0.0060678 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_97-11_0_12_load_7 | 4 | 0.020898 | 0.0052375 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_97-11_0_12_load_9 | 5 | 0.0027757 | 0.00069565 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_97-11_0_12_load_30 | 10 | 0.00043334 | 0.00010861 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_97-11_0_12_load_10 | 11 | 0.00038705 | 9.7005e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_97-11_0_12_load_18 | 13 | 0.0010247 | 0.0002568 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_97-11_0_12_load_34 | 15 | 0.00035064 | 8.7878e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_97-11_0_12_load_26 | 18 | 0.00019537 | 4.8964e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_97-11_0_12_load_29 | 19 | 0.00024513 | 6.1436e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_97-11_0_12_load_28 | 20 | 0.0019156 | 0.00048009 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_97-11_0_12_load_17 | 21 | 0.0015534 | 0.00038933 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_97-11_0_12_load_12 | 22 | 0.00041981 | 0.00010521 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_97-11_0_12_load_35 | 26 | 0.00031635 | 7.9284e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_97-11_0_12_load_62 | 28 | 0.00047023 | 0.00011785 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_97-11_0_12_load_36 | 29 | 0.036976 | 0.009267 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_97-11_0_12_load_41 | 34 | 0.0046863 | 0.0011745 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_97-11_0_12_load_42 | 35 | 0.03815 | 0.0095613 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_97-11_0_12_load_52 | 36 | 0.002668 | 0.00066866 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_97-11_0_12_load_51 | 37 | 0.065564 | 0.016432 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_97-11_0_12_load_48 | 39 | 0.051975 | 0.013026 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_97-11_0_12_load_46 | 41 | 0.032048 | 0.0080321 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_97-11_0_12_load_49 | 44 | 0.053122 | 0.013314 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_97-11_0_12_load_54 | 45 | 0.045397 | 0.011378 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_97-11_0_12_load_19 | 46 | 0.0020991 | 0.0005261 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_97-11_0_12_load_20 | 47 | 0.00032316 | 8.0991e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_97-11_0_12_load_32 | 48 | 0.0009862 | 0.00024716 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_97-11_0_12_load_23 | 49 | 0.00035624 | 8.9282e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_97-11_0_12_load_24 | 50 | 0.00039904 | 0.00010001 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_97-11_0_12_load_56 | 52 | 0.010774 | 0.0027003 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_97-11_0_12_load_60 | 53 | 0.035516 | 0.0089011 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_97-11_0_12_load_55 | 54 | 0.01788 | 0.0044812 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_97-11_0_12_load_59 | 55 | 0.029121 | 0.0072984 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_97-11_0_12_load_57 | 56 | 0.022207 | 0.0055655 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_97-11_0_12_load_31 | 57 | 0.00020079 | 5.0322e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_97-11_0_12_line_0 |  | 0 | 1 | 0.20346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_97-11_0_12_line_1 |  | 1 | 2 | 0.0097105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_97-11_0_12_line_2 |  | 1 | 3 | 0.26274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_97-11_0_12_line_3 |  | 2 | 4 | 0.029905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_97-11_0_12_line_4 |  | 3 | 5 | 0.039014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_97-11_0_12_line_5 |  | 4 | 6 | 0.087998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_97-11_0_12_line_6 |  | 5 | 11 | 0.018722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_97-11_0_12_line_7 |  | 6 | 7 | 0.31208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_97-11_0_12_line_8 |  | 7 | 12 | 0.032933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_97-11_0_12_line_9 |  | 7 | 13 | 0.049169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_97-11_0_12_line_10 |  | 8 | 9 | 0.23582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_97-11_0_12_line_11 |  | 8 | 10 | 0.041869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_97-11_0_12_line_12 |  | 9 | 16 | 0.021613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_97-11_0_12_line_13 |  | 9 | 17 | 0.042373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_97-11_0_12_line_14 |  | 10 | 19 | 0.016004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_97-11_0_12_line_15 |  | 12 | 20 | 0.026555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_97-11_0_12_line_16 |  | 12 | 14 | 0.042924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_97-11_0_12_line_17 |  | 13 | 21 | 0.034059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_97-11_0_12_line_18 |  | 14 | 15 | 0.04224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_97-11_0_12_line_19 |  | 15 | 48 | 0.010605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_97-11_0_12_line_20 |  | 16 | 18 | 0.040187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_97-11_0_12_line_21 |  | 17 | 28 | 0.010517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_97-11_0_12_line_22 |  | 17 | 24 | 0.11119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_97-11_0_12_line_23 |  | 18 | 51 | 0.052528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_97-11_0_12_line_24 |  | 19 | 57 | 0.0067239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_97-11_0_12_line_25 |  | 21 | 46 | 0.0045982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_97-11_0_12_line_26 |  | 22 | 23 | 0.04568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_97-11_0_12_line_27 |  | 22 | 24 | 0.20897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_97-11_0_12_line_28 |  | 23 | 25 | 0.26291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_97-11_0_12_line_29 |  | 25 | 26 | 0.024304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_97-11_0_12_line_30 |  | 25 | 27 | 0.60821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_97-11_0_12_line_31 |  | 27 | 41 | 0.039895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_97-11_0_12_line_32 |  | 29 | 30 | 0.020326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_97-11_0_12_line_33 |  | 29 | 31 | 0.029097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_97-11_0_12_line_34 |  | 30 | 32 | 0.037942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_97-11_0_12_line_35 |  | 30 | 33 | 0.045935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_97-11_0_12_line_36 |  | 30 | 34 | 0.03043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_97-11_0_12_line_37 |  | 31 | 35 | 0.028356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_97-11_0_12_line_38 |  | 32 | 36 | 0.02828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_97-11_0_12_line_39 |  | 32 | 37 | 0.022015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_97-11_0_12_line_40 |  | 33 | 38 | 0.048436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_97-11_0_12_line_41 |  | 33 | 39 | 0.030981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_97-11_0_12_line_42 |  | 34 | 40 | 0.012082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_97-11_0_12_line_43 |  | 38 | 45 | 0.012558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_97-11_0_12_line_44 |  | 39 | 44 | 0.0022097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_97-11_0_12_line_45 |  | 40 | 43 | 0.2764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_97-11_0_12_line_46 |  | 40 | 42 | 0.007206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_97-11_0_12_line_47 |  | 41 | 42 | 0.066549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_97-11_0_12_line_48 |  | 43 | 52 | 0.037824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_97-11_0_12_line_49 |  | 46 | 47 | 0.019827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_97-11_0_12_line_50 |  | 48 | 57 | 0.011057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_97-11_0_12_line_51 |  | 49 | 50 | 0.016859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_97-11_0_12_line_52 |  | 49 | 51 | 0.017984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_97-11_0_12_line_53 |  | 52 | 53 | 0.14914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_97-11_0_12_line_54 |  | 52 | 54 | 0.08696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_97-11_0_12_line_55 |  | 53 | 55 | 0.045211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_97-11_0_12_line_56 |  | 54 | 56 | 0.053417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_97-11_0_12_trafo_47 | 0.63 MVA 20/0.4 kV | 58 | 40 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2683059.5942 | 1254793.8978 | 2683043.3755 | 1254781.9725 | 2683023.822 | 1254759.3034 | 2682964.0865 | 1254678.5832 | 2682952.4732 | 1254664.2319 | 2682922.9961 | 1254646.2761
1 | 2683059.5942 | 1254793.8978 | 2683065.0141 | 1254785.8405
2 | 2682930.7598 | 1255022.877 | 2683005.8307 | 1254889.3608 | 2683030.1493 | 1254847.1252 | 2683059.5942 | 1254793.8978
3 | 2683065.0141 | 1254785.8405 | 2683081.7056 | 1254761.0269
4 | 2682930.7598 | 1255022.877 | 2682963.6312 | 1255043.8906
5 | 2683143.4199 | 1254699.7581 | 2683134.7882 | 1254706.2752 | 2683110.0359 | 1254723.9635 | 2683098.6896 | 1254736.3025 | 2683084.358 | 1254757.0839 | 2683081.7056 | 1254761.0269
6 | 2682963.6312 | 1255043.8906 | 2682979.4051 | 1255053.9744
7 | 2683143.4199 | 1254699.7581 | 2683210.2559 | 1254649.2584 | 2683236.2917 | 1254629.9318 | 2683262.8561 | 1254617.0287 | 2683294.155 | 1254607.5838 | 2683306.5662 | 1254602.7213 | 2683319.2436 | 1254593.4148 | 2683335.3074 | 1254573.4701 | 2683356.4279 | 1254539.4749 | 2683325.597 | 1254515.6342
8 | 2683325.597 | 1254515.6342 | 2683307.6924 | 1254498.5806 | 2683312.8447 | 1254492.1926
9 | 2683325.597 | 1254515.6342 | 2683310.3288 | 1254536.4018 | 2683306.9878 | 1254543.816 | 2683296.6497 | 1254555.0416
10 | 2683215.1102 | 1254439.7348 | 2683156.976 | 1254401.7897 | 2683152.1173 | 1254398.5635 | 2683219.1094 | 1254303.3879 | 2683244.5754 | 1254267.285
11 | 2683215.1102 | 1254439.7348 | 2683239.7707 | 1254431.8975 | 2683255.315 | 1254428.1355
12 | 2683244.5754 | 1254267.285 | 2683248.0138 | 1254267.4335 | 2683251.7497 | 1254268.4201 | 2683259.9947 | 1254256.7271
13 | 2683205.1655 | 1254281.4532 | 2683211.7982 | 1254281.4019 | 2683218.8091 | 1254279.132 | 2683240.1249 | 1254268.2899 | 2683244.5754 | 1254267.285
14 | 2683271.2462 | 1254427.5442 | 2683257.8338 | 1254427.5259 | 2683255.315 | 1254428.1355
15 | 2683312.8447 | 1254492.1926 | 2683318.9457 | 1254484.8729 | 2683328.6563 | 1254470.8878
16 | 2683279.935 | 1254477.7301 | 2683292.6443 | 1254487.0825 | 2683307.6924 | 1254498.5806 | 2683312.8447 | 1254492.1926
17 | 2683270.0252 | 1254575.995 | 2683289.9331 | 1254562.3346 | 2683296.6497 | 1254555.0416
18 | 2683279.935 | 1254477.7301 | 2683295.2616 | 1254457.1077 | 2683295.2907 | 1254440.5623
19 | 2683286.8112 | 1254434.1936 | 2683295.2907 | 1254440.5623 | 2683295.2907 | 1254440.5623
20 | 2683259.9947 | 1254256.7271 | 2683266.2506 | 1254257.7158 | 2683285.128 | 1254229.6143
21 | 2683205.1655 | 1254281.4532 | 2683200.1111 | 1254285.1628 | 2683195.8644 | 1254285.6257
22 | 2683095.5557 | 1254277.5561 | 2683142.9971 | 1254271.1614 | 2683151.4364 | 1254270.8685 | 2683159.895 | 1254271.3432 | 2683167.5504 | 1254272.6072 | 2683181.8422 | 1254275.6991 | 2683191.5625 | 1254278.2041 | 2683196.0505 | 1254279.368 | 2683205.1655 | 1254281.4532
23 | 2683309.364 | 1254183.0655 | 2683298.4422 | 1254206.4185 | 2683285.5934 | 1254228.9215 | 2683285.128 | 1254229.6143
24 | 2683271.2462 | 1254427.5442 | 2683277.9701 | 1254427.5534 | 2683277.9701 | 1254427.5534
25 | 2683266.2337 | 1254578.5967 | 2683270.0252 | 1254575.995
26 | 2683105.4924 | 1254035.7129 | 2683088.5472 | 1254057.6585 | 2683077.1235 | 1254071.5089
27 | 2683095.5557 | 1254277.5561 | 2683086.8637 | 1254208.2374 | 2683081.1059 | 1254156.7067 | 2683077.9883 | 1254126.7069 | 2683072.0415 | 1254081.634 | 2683073.3339 | 1254076.1035 | 2683077.1235 | 1254071.5089
28 | 2683105.4924 | 1254035.7129 | 2683115.0619 | 1254036.0919 | 2683225.3304 | 1254016.5252 | 2683308.627 | 1254002.2186 | 2683318.9816 | 1254000.4295 | 2683364.76 | 1253993.3571
29 | 2683364.76 | 1253993.3571 | 2683356.2052 | 1254016.1051
30 | 2683364.76 | 1253993.3571 | 2683971.596 | 1254034.1474
31 | 2683971.596 | 1254034.1474 | 2683972.5895 | 1254035.3846 | 2683997.8773 | 1254064.1609
32 | 2684079.9304 | 1254069.1771 | 2684070.6797 | 1254051.0783
33 | 2684057.437 | 1254025.1691 | 2684070.6797 | 1254051.0783
34 | 2684079.9304 | 1254069.1771 | 2684104.1496 | 1254098.4431
35 | 2684114.9936 | 1254039.3857 | 2684079.9304 | 1254069.1771
36 | 2684079.9304 | 1254069.1771 | 2684060.5468 | 1254085.659 | 2684056.9795 | 1254089.1425
37 | 2684057.437 | 1254025.1691 | 2684035.2698 | 1254042.8523
38 | 2684083.7849 | 1254118.1245 | 2684104.1496 | 1254098.4431
39 | 2684104.1496 | 1254098.4431 | 2684121.4541 | 1254084.8329
40 | 2684114.9936 | 1254039.3857 | 2684151.9591 | 1254007.9647
41 | 2684114.9936 | 1254039.3857 | 2684100.0208 | 1254012.2635
42 | 2684048.3354 | 1254097.5836 | 2684056.9795 | 1254089.1425
43 | 2684151.9591 | 1254007.9647 | 2684161.4352 | 1253999.7243
44 | 2684100.0208 | 1254012.2635 | 2684098.9528 | 1254010.3291
45 | 2684089.7078 | 1254328.4457 | 2683999.6841 | 1254168.3249 | 2684031.8942 | 1254144.3858 | 2684037.2695 | 1254140.4369 | 2684040.6432 | 1254137.1712 | 2684042.7447 | 1254133.1757 | 2684044.1974 | 1254128.1036 | 2684043.3224 | 1254115.8708 | 2684044.4262 | 1254106.6795 | 2684048.3354 | 1254097.5836
46 | 2684048.3354 | 1254097.5836 | 2684043.5072 | 1254092.2222
47 | 2684043.5072 | 1254092.2222 | 2684031.4049 | 1254102.3137 | 2683997.8773 | 1254064.1609
48 | 2684089.7078 | 1254328.4457 | 2684111.9075 | 1254359.0698
49 | 2683249.8852 | 1254589.8147 | 2683266.2337 | 1254578.5967
50 | 2683286.8112 | 1254434.1936 | 2683277.9701 | 1254427.5534
51 | 2683326.6601 | 1254187.1452 | 2683342.3943 | 1254181.09
52 | 2683309.364 | 1254183.0655 | 2683318.7067 | 1254186.6774 | 2683326.6601 | 1254187.1452 | 2683326.6601 | 1254187.1452
53 | 2684111.9075 | 1254359.0698 | 2684229.7317 | 1254267.6423
54 | 2684156.738 | 1254433.4081 | 2684128.5491 | 1254382.0267 | 2684111.9075 | 1254359.0698
55 | 2684264.2152 | 1254238.4037 | 2684229.7317 | 1254267.6423
56 | 2684156.738 | 1254433.4081 | 2684182.4312 | 1254480.2404

## bus_geodata
| x | y | coords
0 | 2682922.9961 | 1254646.2761
1 | 2683059.5942 | 1254793.8978
2 | 2683065.0141 | 1254785.8405
3 | 2682930.7598 | 1255022.877
4 | 2683081.7056 | 1254761.0269
5 | 2682963.6312 | 1255043.8906
6 | 2683143.4199 | 1254699.7581
7 | 2683325.597 | 1254515.6342
8 | 2683215.1102 | 1254439.7348
9 | 2683244.5754 | 1254267.285
10 | 2683255.315 | 1254428.1355
11 | 2682979.4051 | 1255053.9744
12 | 2683312.8447 | 1254492.1926
13 | 2683296.6497 | 1254555.0416
14 | 2683279.935 | 1254477.7301
15 | 2683295.2907 | 1254440.5623
16 | 2683259.9947 | 1254256.7271
17 | 2683205.1655 | 1254281.4532
18 | 2683285.128 | 1254229.6143
19 | 2683271.2462 | 1254427.5442
20 | 2683328.6563 | 1254470.8878
21 | 2683270.0252 | 1254575.995
22 | 2683077.1235 | 1254071.5089
23 | 2683105.4924 | 1254035.7129
24 | 2683095.5557 | 1254277.5561
25 | 2683364.76 | 1253993.3571
26 | 2683356.2052 | 1254016.1051
27 | 2683971.596 | 1254034.1474
28 | 2683195.8644 | 1254285.6257
29 | 2684070.6797 | 1254051.0783
30 | 2684079.9304 | 1254069.1771
31 | 2684057.437 | 1254025.1691
32 | 2684104.1496 | 1254098.4431
33 | 2684114.9936 | 1254039.3857
34 | 2684056.9795 | 1254089.1425
35 | 2684035.2698 | 1254042.8523
36 | 2684083.7849 | 1254118.1245
37 | 2684121.4541 | 1254084.8329
38 | 2684151.9591 | 1254007.9647
39 | 2684100.0208 | 1254012.2635
40 | 2684048.3354 | 1254097.5836
41 | 2683997.8773 | 1254064.1609
42 | 2684043.5072 | 1254092.2222
43 | 2684089.7078 | 1254328.4457
44 | 2684098.9528 | 1254010.3291
45 | 2684161.4352 | 1253999.7243
46 | 2683266.2337 | 1254578.5967
47 | 2683249.8852 | 1254589.8147
48 | 2683286.8112 | 1254434.1936
49 | 2683326.66 | 1254187.1452
50 | 2683342.3943 | 1254181.09
51 | 2683309.364 | 1254183.0655
52 | 2684111.9075 | 1254359.0698
53 | 2684229.7317 | 1254267.6423
54 | 2684156.738 | 1254433.4081
55 | 2684264.2152 | 1254238.4037
56 | 2684182.4312 | 1254480.2404
57 | 2683277.9701 | 1254427.5534
58 | 2684043.5072 | 1254092.2222

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1