## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_97-15_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_97-15_0_5_node_156 | 0.4 | n |  | TRUE
2 | bus_LV_97-15_0_5_node_43 | 0.4 | n |  | TRUE
3 | bus_LV_97-15_0_5_node_1 | 0.4 | n |  | TRUE
4 | bus_LV_97-15_0_5_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_97-15_0_5_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_97-15_0_5_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_97-15_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_97-15_0_5_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_97-15_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_97-15_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_97-15_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_97-15_0_5_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_97-15_0_5_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_97-15_0_5_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_97-15_0_5_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_97-15_0_5_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_97-15_0_5_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_97-15_0_5_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_97-15_0_5_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_97-15_0_5_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_97-15_0_5_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_97-15_0_5_node_162 | 0.4 | n |  | TRUE
23 | bus_LV_97-15_0_5_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_97-15_0_5_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_97-15_0_5_node_151 | 0.4 | n |  | TRUE
26 | bus_LV_97-15_0_5_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_97-15_0_5_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_97-15_0_5_node_152 | 0.4 | n |  | TRUE
29 | bus_LV_97-15_0_5_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_97-15_0_5_node_146 | 0.4 | n |  | TRUE
31 | bus_LV_97-15_0_5_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_97-15_0_5_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_97-15_0_5_node_140 | 0.4 | n |  | TRUE
34 | bus_LV_97-15_0_5_node_139 | 0.4 | n |  | TRUE
35 | bus_LV_97-15_0_5_node_141 | 0.4 | n |  | TRUE
36 | bus_LV_97-15_0_5_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_97-15_0_5_node_143 | 0.4 | n |  | TRUE
38 | bus_LV_97-15_0_5_node_144 | 0.4 | n |  | TRUE
39 | bus_LV_97-15_0_5_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_97-15_0_5_node_147 | 0.4 | n |  | TRUE
41 | bus_LV_97-15_0_5_node_50 | 0.4 | n |  | TRUE
42 | bus_LV_97-15_0_5_node_145 | 0.4 | n |  | TRUE
43 | bus_LV_97-15_0_5_node_165 | 0.4 | n |  | TRUE
44 | bus_LV_97-15_0_5_node_136 | 0.4 | n |  | TRUE
45 | bus_LV_97-15_0_5_node_134 | 0.4 | n |  | TRUE
46 | bus_LV_97-15_0_5_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_97-15_0_5_node_133 | 0.4 | n |  | TRUE
48 | bus_LV_97-15_0_5_node_135 | 0.4 | n |  | TRUE
49 | bus_LV_97-15_0_5_node_154 | 0.4 | n |  | TRUE
50 | bus_LV_97-15_0_5_node_150 | 0.4 | n |  | TRUE
51 | bus_LV_97-15_0_5_node_163 | 0.4 | n |  | TRUE
52 | bus_LV_97-15_0_5_node_117 | 0.4 | n |  | TRUE
53 | bus_LV_97-15_0_5_node_164 | 0.4 | n |  | TRUE
54 | bus_LV_97-15_0_5_node_131 | 0.4 | n |  | TRUE
55 | bus_LV_97-15_0_5_node_116 | 0.4 | n |  | TRUE
56 | bus_LV_97-15_0_5_node_130 | 0.4 | n |  | TRUE
57 | bus_LV_97-15_0_5_node_155 | 0.4 | n |  | TRUE
58 | bus_LV_97-15_0_5_node_153 | 0.4 | n |  | TRUE
59 | bus_LV_97-15_0_5_node_138 | 0.4 | n |  | TRUE
60 | bus_LV_97-15_0_5_node_142 | 0.4 | n |  | TRUE
61 | bus_LV_97-15_0_5_node_32 | 0.4 | n |  | TRUE
62 | bus_LV_97-15_0_5_node_33 | 0.4 | n |  | TRUE
63 | bus_LV_97-15_0_5_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_97-15_0_5_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_97-15_0_5_node_36 | 0.4 | n |  | TRUE
66 | bus_LV_97-15_0_5_node_161 | 0.4 | n |  | TRUE
67 | bus_LV_97-15_0_5_node_160 | 0.4 | n |  | TRUE
68 | bus_LV_97-15_0_5_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_97-15_0_5_node_39 | 0.4 | n |  | TRUE
70 | bus_LV_97-15_0_5_node_45 | 0.4 | n |  | TRUE
71 | bus_LV_97-15_0_5_node_40 | 0.4 | n |  | TRUE
72 | bus_LV_97-15_0_5_node_41 | 0.4 | n |  | TRUE
73 | bus_LV_97-15_0_5_node_44 | 0.4 | n |  | TRUE
74 | bus_LV_97-15_0_5_node_67 | 0.4 | n |  | TRUE
75 | bus_LV_97-15_0_5_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_97-15_0_5_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_97-15_0_5_node_47 | 0.4 | n |  | TRUE
78 | bus_LV_97-15_0_5_node_49 | 0.4 | n |  | TRUE
79 | bus_LV_97-15_0_5_node_48 | 0.4 | n |  | TRUE
80 | bus_LV_97-15_0_5_node_77 | 0.4 | n |  | TRUE
81 | bus_LV_97-15_0_5_node_62 | 0.4 | n |  | TRUE
82 | bus_LV_97-15_0_5_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_97-15_0_5_node_54 | 0.4 | n |  | TRUE
84 | bus_LV_97-15_0_5_node_55 | 0.4 | n |  | TRUE
85 | bus_LV_97-15_0_5_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_97-15_0_5_node_57 | 0.4 | n |  | TRUE
87 | bus_LV_97-15_0_5_node_58 | 0.4 | n |  | TRUE
88 | bus_LV_97-15_0_5_node_59 | 0.4 | n |  | TRUE
89 | bus_LV_97-15_0_5_node_60 | 0.4 | n |  | TRUE
90 | bus_LV_97-15_0_5_node_61 | 0.4 | n |  | TRUE
91 | bus_LV_97-15_0_5_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_97-15_0_5_node_79 | 0.4 | n |  | TRUE
93 | bus_LV_97-15_0_5_node_149 | 0.4 | n |  | TRUE
94 | bus_LV_97-15_0_5_node_88 | 0.4 | n |  | TRUE
95 | bus_LV_97-15_0_5_node_157 | 0.4 | n |  | TRUE
96 | bus_LV_97-15_0_5_node_125 | 0.4 | n |  | TRUE
97 | bus_LV_97-15_0_5_node_63 | 0.4 | n |  | TRUE
98 | bus_LV_97-15_0_5_node_64 | 0.4 | n |  | TRUE
99 | bus_LV_97-15_0_5_node_66 | 0.4 | n |  | TRUE
100 | bus_LV_97-15_0_5_node_68 | 0.4 | n |  | TRUE
101 | bus_LV_97-15_0_5_node_104 | 0.4 | n |  | TRUE
102 | bus_LV_97-15_0_5_node_102 | 0.4 | n |  | TRUE
103 | bus_LV_97-15_0_5_node_72 | 0.4 | n |  | TRUE
104 | bus_LV_97-15_0_5_node_108 | 0.4 | n |  | TRUE
105 | bus_LV_97-15_0_5_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_97-15_0_5_node_70 | 0.4 | n |  | TRUE
107 | bus_LV_97-15_0_5_node_69 | 0.4 | n |  | TRUE
108 | bus_LV_97-15_0_5_node_71 | 0.4 | n |  | TRUE
109 | bus_LV_97-15_0_5_node_73 | 0.4 | n |  | TRUE
110 | bus_LV_97-15_0_5_node_74 | 0.4 | n |  | TRUE
111 | bus_LV_97-15_0_5_node_76 | 0.4 | n |  | TRUE
112 | bus_LV_97-15_0_5_node_158 | 0.4 | n |  | TRUE
113 | bus_LV_97-15_0_5_node_159 | 0.4 | n |  | TRUE
114 | bus_LV_97-15_0_5_node_85 | 0.4 | n |  | TRUE
115 | bus_LV_97-15_0_5_node_148 | 0.4 | n |  | TRUE
116 | bus_LV_97-15_0_5_node_82 | 0.4 | n |  | TRUE
117 | bus_LV_97-15_0_5_node_80 | 0.4 | n |  | TRUE
118 | bus_LV_97-15_0_5_node_81 | 0.4 | n |  | TRUE
119 | bus_LV_97-15_0_5_node_83 | 0.4 | n |  | TRUE
120 | bus_LV_97-15_0_5_node_84 | 0.4 | n |  | TRUE
121 | bus_LV_97-15_0_5_node_86 | 0.4 | n |  | TRUE
122 | bus_LV_97-15_0_5_node_90 | 0.4 | n |  | TRUE
123 | bus_LV_97-15_0_5_node_87 | 0.4 | n |  | TRUE
124 | bus_LV_97-15_0_5_node_89 | 0.4 | n |  | TRUE
125 | bus_LV_97-15_0_5_node_101 | 0.4 | n |  | TRUE
126 | bus_LV_97-15_0_5_node_98 | 0.4 | n |  | TRUE
127 | bus_LV_97-15_0_5_node_124 | 0.4 | n |  | TRUE
128 | bus_LV_97-15_0_5_node_123 | 0.4 | n |  | TRUE
129 | bus_LV_97-15_0_5_node_91 | 0.4 | n |  | TRUE
130 | bus_LV_97-15_0_5_node_96 | 0.4 | n |  | TRUE
131 | bus_LV_97-15_0_5_node_94 | 0.4 | n |  | TRUE
132 | bus_LV_97-15_0_5_node_92 | 0.4 | n |  | TRUE
133 | bus_LV_97-15_0_5_node_93 | 0.4 | n |  | TRUE
134 | bus_LV_97-15_0_5_node_95 | 0.4 | n |  | TRUE
135 | bus_LV_97-15_0_5_node_97 | 0.4 | n |  | TRUE
136 | bus_LV_97-15_0_5_node_126 | 0.4 | n |  | TRUE
137 | bus_LV_97-15_0_5_node_129 | 0.4 | n |  | TRUE
138 | bus_LV_97-15_0_5_node_99 | 0.4 | n |  | TRUE
139 | bus_LV_97-15_0_5_node_100 | 0.4 | n |  | TRUE
140 | bus_LV_97-15_0_5_node_137 | 0.4 | n |  | TRUE
141 | bus_LV_97-15_0_5_node_132 | 0.4 | n |  | TRUE
142 | bus_LV_97-15_0_5_node_127 | 0.4 | n |  | TRUE
143 | bus_LV_97-15_0_5_node_122 | 0.4 | n |  | TRUE
144 | bus_LV_97-15_0_5_node_106 | 0.4 | n |  | TRUE
145 | bus_LV_97-15_0_5_node_105 | 0.4 | n |  | TRUE
146 | bus_LV_97-15_0_5_node_107 | 0.4 | n |  | TRUE
147 | bus_LV_97-15_0_5_node_112 | 0.4 | n |  | TRUE
148 | bus_LV_97-15_0_5_node_109 | 0.4 | n |  | TRUE
149 | bus_LV_97-15_0_5_node_114 | 0.4 | n |  | TRUE
150 | bus_LV_97-15_0_5_node_110 | 0.4 | n |  | TRUE
151 | bus_LV_97-15_0_5_node_111 | 0.4 | n |  | TRUE
152 | bus_LV_97-15_0_5_node_113 | 0.4 | n |  | TRUE
153 | bus_LV_97-15_0_5_node_115 | 0.4 | n |  | TRUE
154 | bus_LV_97-15_0_5_node_118 | 0.4 | n |  | TRUE
155 | bus_LV_97-15_0_5_node_119 | 0.4 | n |  | TRUE
156 | bus_LV_97-15_0_5_node_120 | 0.4 | n |  | TRUE
157 | bus_LV_97-15_0_5_node_121 | 0.4 | n |  | TRUE
158 | bus_LV_97-15_0_5_node_128 | 0.4 | n |  | TRUE
159 | bus_MV_468_0_node_22 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_97-15_0_5_load_0 | 0 | 0.00034928 | 8.7537e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_97-15_0_5_load_156 | 1 | 0.00046107 | 0.00011556 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_97-15_0_5_load_1 | 3 | 0.00081855 | 0.00020515 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_97-15_0_5_load_3 | 5 | 0.00035106 | 8.7984e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_97-15_0_5_load_7 | 6 | 0.00052239 | 0.00013092 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_97-15_0_5_load_5 | 7 | 0.00065411 | 0.00016394 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_97-15_0_5_load_4 | 8 | 0.0010891 | 0.00027297 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_97-15_0_5_load_6 | 9 | 0.00039102 | 9.7998e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_97-15_0_5_load_8 | 10 | 0.00046338 | 0.00011613 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_97-15_0_5_load_9 | 11 | 0.00040673 | 0.00010194 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_97-15_0_5_load_11 | 13 | 0.00082848 | 0.00020764 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_97-15_0_5_load_12 | 14 | 0.00042994 | 0.00010775 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_97-15_0_5_load_13 | 15 | 0.00075633 | 0.00018955 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_97-15_0_5_load_34 | 16 | 0.0010241 | 0.00025667 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_97-15_0_5_load_35 | 18 | 0.00045147 | 0.00011315 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_97-15_0_5_load_31 | 21 | 0.0023588 | 0.00059118 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_97-15_0_5_load_162 | 22 | 0.0019185 | 0.00048082 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_97-15_0_5_load_151 | 25 | 0.0019277 | 0.00048313 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_97-15_0_5_load_152 | 28 | 0.016777 | 0.0042047 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_97-15_0_5_load_146 | 30 | 0.0034906 | 0.00087483 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_97-15_0_5_load_140 | 33 | 0.0052369 | 0.0013125 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_97-15_0_5_load_139 | 34 | 0.0069724 | 0.0017474 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_97-15_0_5_load_141 | 35 | 0.0052454 | 0.0013146 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_97-15_0_5_load_143 | 37 | 0.0091601 | 0.0022957 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_97-15_0_5_load_144 | 38 | 0.024728 | 0.0061974 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_97-15_0_5_load_147 | 40 | 0.0099766 | 0.0025004 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_97-15_0_5_load_145 | 42 | 0.0012102 | 0.00030331 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_97-15_0_5_load_165 | 43 | 0.0090576 | 0.00227 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_97-15_0_5_load_136 | 44 | 0.030991 | 0.0077671 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_97-15_0_5_load_134 | 45 | 0.0027655 | 0.00069309 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_97-15_0_5_load_30 | 46 | 0.00061864 | 0.00015505 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_97-15_0_5_load_135 | 48 | 0.042285 | 0.010598 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_97-15_0_5_load_154 | 49 | 0.001816 | 0.00045514 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_97-15_0_5_load_163 | 51 | 0.01414 | 0.0035439 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_97-15_0_5_load_164 | 53 | 0.0017455 | 0.00043747 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_97-15_0_5_load_130 | 56 | 0.0034467 | 0.00086382 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_97-15_0_5_load_155 | 57 | 0.0085793 | 0.0021502 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_97-15_0_5_load_153 | 58 | 0.014165 | 0.0035501 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_97-15_0_5_load_138 | 59 | 0.0015758 | 0.00039493 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_97-15_0_5_load_32 | 61 | 0.00066837 | 0.00016751 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_97-15_0_5_load_33 | 62 | 0.00058223 | 0.00014592 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_97-15_0_5_load_37 | 63 | 0.0017588 | 0.0004408 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_97-15_0_5_load_36 | 65 | 0.00041207 | 0.00010327 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_97-15_0_5_load_161 | 66 | 0.0005316 | 0.00013323 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_97-15_0_5_load_160 | 67 | 0.00086072 | 0.00021572 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_97-15_0_5_load_42 | 68 | 0.001856 | 0.00046516 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_97-15_0_5_load_39 | 69 | 0.0019903 | 0.00049882 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_97-15_0_5_load_45 | 70 | 0.001775 | 0.00044485 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_97-15_0_5_load_40 | 71 | 0.0016043 | 0.00040209 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_97-15_0_5_load_41 | 72 | 0.00018954 | 4.7502e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_97-15_0_5_load_44 | 73 | 0.00054395 | 0.00013633 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_97-15_0_5_load_67 | 74 | 0.00044089 | 0.0001105 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_97-15_0_5_load_46 | 75 | 0.0032288 | 0.00080922 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_97-15_0_5_load_49 | 78 | 0.0033062 | 0.00082861 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_97-15_0_5_load_48 | 79 | 0.0015651 | 0.00039226 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_97-15_0_5_load_75 | 82 | 0.0024796 | 0.00062144 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_97-15_0_5_load_54 | 83 | 0.0067674 | 0.0016961 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_97-15_0_5_load_55 | 84 | 0.0030959 | 0.0007759 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_97-15_0_5_load_57 | 86 | 0.0027437 | 0.00068764 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_97-15_0_5_load_58 | 87 | 0.0075757 | 0.0018987 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_97-15_0_5_load_59 | 88 | 0.0047032 | 0.0011787 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_97-15_0_5_load_61 | 90 | 0.0043849 | 0.0010989 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_97-15_0_5_load_78 | 91 | 0.0071563 | 0.0017935 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_97-15_0_5_load_149 | 93 | 0.0086345 | 0.002164 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_97-15_0_5_load_88 | 94 | 0.0046747 | 0.0011716 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_97-15_0_5_load_157 | 95 | 0.0034623 | 0.00086774 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_97-15_0_5_load_125 | 96 | 0.0035454 | 0.00088855 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_97-15_0_5_load_63 | 97 | 0.0012194 | 0.00030561 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_97-15_0_5_load_64 | 98 | 0.0012706 | 0.00031843 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_97-15_0_5_load_68 | 100 | 0.00083227 | 0.00020859 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_97-15_0_5_load_104 | 101 | 0.0015934 | 0.00039933 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_97-15_0_5_load_102 | 102 | 0.0011143 | 0.00027928 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_97-15_0_5_load_72 | 103 | 0.00023117 | 5.7938e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_97-15_0_5_load_108 | 104 | 0.0016394 | 0.00041087 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_97-15_0_5_load_103 | 105 | 0.0027767 | 0.00069592 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_97-15_0_5_load_70 | 106 | 0.00083186 | 0.00020848 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_97-15_0_5_load_69 | 107 | 0.00023128 | 5.7965e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_97-15_0_5_load_71 | 108 | 0.00016492 | 4.1334e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_97-15_0_5_load_73 | 109 | 0.0037592 | 0.00094215 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_97-15_0_5_load_74 | 110 | 0.0023432 | 0.00058727 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_97-15_0_5_load_76 | 111 | 0.0034861 | 0.00087369 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_97-15_0_5_load_158 | 112 | 0.00092403 | 0.00023158 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_97-15_0_5_load_159 | 113 | 0.0080136 | 0.0020084 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_97-15_0_5_load_85 | 114 | 0.0080205 | 0.0020101 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_97-15_0_5_load_148 | 115 | 0.0066459 | 0.0016656 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_97-15_0_5_load_80 | 117 | 0.0032158 | 0.00080596 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_97-15_0_5_load_81 | 118 | 0.0034547 | 0.00086584 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_97-15_0_5_load_83 | 119 | 0.0049221 | 0.0012336 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_97-15_0_5_load_84 | 120 | 0.0027801 | 0.00069677 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_97-15_0_5_load_86 | 121 | 0.0048483 | 0.0012151 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_97-15_0_5_load_90 | 122 | 0.010788 | 0.0027037 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_97-15_0_5_load_87 | 123 | 0.0051754 | 0.0012971 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_97-15_0_5_load_98 | 126 | 0.0041775 | 0.001047 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_97-15_0_5_load_124 | 127 | 0.0019468 | 0.00048793 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_97-15_0_5_load_123 | 128 | 0.00187 | 0.00046867 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_97-15_0_5_load_91 | 129 | 0.01182 | 0.0029624 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_97-15_0_5_load_94 | 131 | 0.010983 | 0.0027525 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_97-15_0_5_load_92 | 132 | 0.004177 | 0.0010469 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_97-15_0_5_load_93 | 133 | 0.0042089 | 0.0010549 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_97-15_0_5_load_129 | 137 | 0.0034101 | 0.00085465 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_97-15_0_5_load_137 | 140 | 0.0021002 | 0.00052635 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_97-15_0_5_load_132 | 141 | 0.0020061 | 0.00050278 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_97-15_0_5_load_127 | 142 | 0.0025013 | 0.0006269 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_97-15_0_5_load_122 | 143 | 0.0038322 | 0.00096043 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_97-15_0_5_load_105 | 145 | 0.0016689 | 0.00041826 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_97-15_0_5_load_112 | 147 | 0.0026643 | 0.00066774 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_97-15_0_5_load_109 | 148 | 0.0030134 | 0.00075523 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_97-15_0_5_load_114 | 149 | 0.0072315 | 0.0018124 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_97-15_0_5_load_110 | 150 | 0.0024343 | 0.0006101 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_97-15_0_5_load_111 | 151 | 0.0031961 | 0.00080101 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_97-15_0_5_load_115 | 153 | 0.0032827 | 0.00082273 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_97-15_0_5_load_118 | 154 | 0.0021029 | 0.00052704 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_97-15_0_5_load_119 | 155 | 0.0015612 | 0.00039128 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_97-15_0_5_load_120 | 156 | 0.0012704 | 0.0003184 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_97-15_0_5_load_121 | 157 | 0.0013936 | 0.00034928 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_97-15_0_5_load_128 | 158 | 0.001845 | 0.0004624 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 120 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_97-15_0_5_line_0 |  | 0 | 1 | 0.23448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_97-15_0_5_line_1 |  | 1 | 2 | 0.055625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_97-15_0_5_line_2 |  | 2 | 74 | 0.012917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_97-15_0_5_line_3 |  | 3 | 4 | 0.005862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_97-15_0_5_line_4 |  | 4 | 5 | 0.0049492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_97-15_0_5_line_5 |  | 5 | 6 | 0.012331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_97-15_0_5_line_6 |  | 6 | 7 | 0.0041009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_97-15_0_5_line_7 |  | 7 | 8 | 0.011525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_97-15_0_5_line_8 |  | 8 | 9 | 0.018519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_97-15_0_5_line_9 |  | 9 | 10 | 0.00051795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_97-15_0_5_line_10 |  | 10 | 11 | 0.038173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_97-15_0_5_line_11 |  | 11 | 12 | 0.01483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_97-15_0_5_line_12 |  | 12 | 13 | 0.01834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_97-15_0_5_line_13 |  | 12 | 14 | 0.030291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_97-15_0_5_line_14 |  | 13 | 15 | 0.026179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_97-15_0_5_line_15 |  | 14 | 16 | 0.015564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_97-15_0_5_line_16 |  | 15 | 17 | 0.015184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_97-15_0_5_line_17 |  | 16 | 18 | 0.0086711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_97-15_0_5_line_18 |  | 17 | 19 | 0.036413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_97-15_0_5_line_19 |  | 18 | 65 | 0.010373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_97-15_0_5_line_20 |  | 19 | 20 | 0.06268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_97-15_0_5_line_21 |  | 19 | 21 | 0.01939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_97-15_0_5_line_22 |  | 20 | 22 | 0.049517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_97-15_0_5_line_23 |  | 21 | 46 | 0.0048118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_97-15_0_5_line_24 |  | 22 | 51 | 0.0005439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_97-15_0_5_line_25 |  | 23 | 24 | 0.021258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_97-15_0_5_line_26 |  | 23 | 25 | 0.027843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_97-15_0_5_line_27 |  | 24 | 29 | 0.031273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_97-15_0_5_line_28 |  | 24 | 30 | 0.018877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_97-15_0_5_line_29 |  | 25 | 31 | 0.03755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_97-15_0_5_line_30 |  | 26 | 27 | 0.028395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_97-15_0_5_line_31 |  | 26 | 28 | 0.030863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_97-15_0_5_line_32 |  | 27 | 35 | 0.022492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_97-15_0_5_line_33 |  | 27 | 33 | 0.011764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_97-15_0_5_line_34 |  | 28 | 58 | 0.0099649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_97-15_0_5_line_35 |  | 29 | 33 | 0.01203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_97-15_0_5_line_36 |  | 29 | 34 | 0.021102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_97-15_0_5_line_37 |  | 30 | 42 | 0.023523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_97-15_0_5_line_38 |  | 31 | 32 | 0.016855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_97-15_0_5_line_39 |  | 32 | 43 | 0.01794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_97-15_0_5_line_40 |  | 34 | 59 | 0.026527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_97-15_0_5_line_41 |  | 35 | 36 | 0.031974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_97-15_0_5_line_42 |  | 36 | 37 | 0.020626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_97-15_0_5_line_43 |  | 36 | 38 | 0.045127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_97-15_0_5_line_44 |  | 37 | 60 | 0.031161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_97-15_0_5_line_45 |  | 39 | 40 | 0.041335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_97-15_0_5_line_46 |  | 39 | 41 | 0.027349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_97-15_0_5_line_47 |  | 39 | 42 | 0.010679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_97-15_0_5_line_48 |  | 40 | 57 | 0.024777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_97-15_0_5_line_49 |  | 41 | 44 | 0.031395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_97-15_0_5_line_50 |  | 41 | 45 | 0.044921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_97-15_0_5_line_51 |  | 45 | 47 | 0.13841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_97-15_0_5_line_52 |  | 46 | 61 | 0.015549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_97-15_0_5_line_53 |  | 47 | 48 | 0.037651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_97-15_0_5_line_54 |  | 49 | 50 | 0.024389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_97-15_0_5_line_55 |  | 50 | 93 | 0.031309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_97-15_0_5_line_56 |  | 50 | 88 | 0.022651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_97-15_0_5_line_57 |  | 52 | 53 | 0.047532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_97-15_0_5_line_58 |  | 52 | 54 | 0.10273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_97-15_0_5_line_59 |  | 52 | 55 | 0.10717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_97-15_0_5_line_60 |  | 54 | 56 | 0.023778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_97-15_0_5_line_61 |  | 55 | 153 | 0.036717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_97-15_0_5_line_62 |  | 56 | 138 | 0.0033805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_97-15_0_5_line_63 |  | 59 | 140 | 0.018564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_97-15_0_5_line_64 |  | 60 | 115 | 0.027543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_97-15_0_5_line_65 |  | 60 | 92 | 0.024903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_97-15_0_5_line_66 |  | 61 | 62 | 0.015225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_97-15_0_5_line_67 |  | 62 | 63 | 0.019637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_97-15_0_5_line_68 |  | 63 | 64 | 0.017272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_97-15_0_5_line_69 |  | 64 | 68 | 0.0055685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_97-15_0_5_line_70 |  | 64 | 69 | 0.013859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_97-15_0_5_line_71 |  | 65 | 66 | 0.0046691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_97-15_0_5_line_72 |  | 66 | 67 | 0.012092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_97-15_0_5_line_73 |  | 67 | 73 | 0.0020038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_97-15_0_5_line_74 |  | 68 | 70 | 0.027281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_97-15_0_5_line_75 |  | 69 | 71 | 0.0023594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_97-15_0_5_line_76 |  | 70 | 75 | 0.001154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_97-15_0_5_line_77 |  | 72 | 73 | 0.014863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_97-15_0_5_line_78 |  | 74 | 76 | 0.01856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_97-15_0_5_line_79 |  | 75 | 77 | 0.013734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_97-15_0_5_line_80 |  | 76 | 100 | 0.018138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_97-15_0_5_line_81 |  | 76 | 97 | 0.0055181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_97-15_0_5_line_82 |  | 77 | 78 | 0.019685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_97-15_0_5_line_83 |  | 77 | 79 | 0.018369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_97-15_0_5_line_84 |  | 78 | 80 | 0.046865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_97-15_0_5_line_85 |  | 80 | 81 | 0.011945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_97-15_0_5_line_86 |  | 80 | 82 | 0.014194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_97-15_0_5_line_87 |  | 81 | 95 | 0.014318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_97-15_0_5_line_88 |  | 81 | 89 | 0.008745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_97-15_0_5_line_89 |  | 82 | 109 | 3.7311e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_97-15_0_5_line_90 |  | 83 | 84 | 0.02391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_97-15_0_5_line_91 |  | 83 | 85 | 0.018595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_97-15_0_5_line_92 |  | 84 | 86 | 0.0099684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_97-15_0_5_line_93 |  | 85 | 87 | 0.034359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_97-15_0_5_line_94 |  | 85 | 88 | 0.01711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_97-15_0_5_line_95 |  | 86 | 89 | 0.029884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_97-15_0_5_line_96 |  | 89 | 90 | 0.011454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_97-15_0_5_line_97 |  | 90 | 94 | 0.020292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_97-15_0_5_line_98 |  | 91 | 92 | 0.013478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_97-15_0_5_line_99 |  | 92 | 114 | 0.003558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_97-15_0_5_line_100 |  | 95 | 96 | 0.024577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_97-15_0_5_line_101 |  | 96 | 125 | 0.03517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_97-15_0_5_line_102 |  | 97 | 98 | 0.023441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_97-15_0_5_line_103 |  | 98 | 99 | 0.021268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_97-15_0_5_line_104 |  | 99 | 101 | 0.0038704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_97-15_0_5_line_105 |  | 99 | 102 | 0.014199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_97-15_0_5_line_106 |  | 100 | 103 | 0.0012025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_97-15_0_5_line_107 |  | 101 | 104 | 0.027431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_97-15_0_5_line_108 |  | 102 | 105 | 0.013261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_97-15_0_5_line_109 |  | 103 | 106 | 0.021495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_97-15_0_5_line_110 |  | 104 | 144 | 0.0053315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_97-15_0_5_line_111 |  | 106 | 107 | 0.0013936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_97-15_0_5_line_112 |  | 107 | 108 | 0.0043045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_97-15_0_5_line_113 |  | 109 | 110 | 0.01478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_97-15_0_5_line_114 |  | 110 | 111 | 0.01358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_97-15_0_5_line_115 |  | 111 | 112 | 0.011025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_97-15_0_5_line_116 |  | 112 | 113 | 0.012719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_97-15_0_5_line_117 |  | 114 | 116 | 0.018978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_97-15_0_5_line_118 |  | 116 | 120 | 0.021333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_97-15_0_5_line_119 |  | 116 | 117 | 0.031428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_97-15_0_5_line_120 |  | 117 | 118 | 0.0057791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_97-15_0_5_line_121 |  | 118 | 119 | 0.028297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_97-15_0_5_line_122 |  | 119 | 121 | 0.011206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_97-15_0_5_line_123 |  | 120 | 122 | 0.037507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_97-15_0_5_line_124 |  | 121 | 123 | 0.0076279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_97-15_0_5_line_125 |  | 123 | 124 | 0.018987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_97-15_0_5_line_126 |  | 124 | 125 | 0.002969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
127 | LV_97-15_0_5_line_127 |  | 124 | 126 | 0.019789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_97-15_0_5_line_128 |  | 125 | 127 | 0.033281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_97-15_0_5_line_129 |  | 125 | 128 | 0.015563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_97-15_0_5_line_130 |  | 127 | 136 | 0.01758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_97-15_0_5_line_131 |  | 128 | 143 | 0.0082748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_97-15_0_5_line_132 |  | 129 | 130 | 0.0072567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_97-15_0_5_line_133 |  | 130 | 131 | 0.015234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_97-15_0_5_line_134 |  | 131 | 132 | 0.031861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_97-15_0_5_line_135 |  | 132 | 133 | 0.0046358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_97-15_0_5_line_136 |  | 133 | 134 | 0.022786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_97-15_0_5_line_137 |  | 134 | 135 | 0.006724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_97-15_0_5_line_138 |  | 135 | 136 | 0.010994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_97-15_0_5_line_139 |  | 135 | 137 | 0.035932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_97-15_0_5_line_140 |  | 136 | 142 | 0.016474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_97-15_0_5_line_141 |  | 137 | 138 | 0.015847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_97-15_0_5_line_142 |  | 139 | 140 | 0.0055976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_97-15_0_5_line_143 |  | 139 | 141 | 0.012047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_97-15_0_5_line_144 |  | 142 | 158 | 0.021673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_97-15_0_5_line_145 |  | 143 | 156 | 0.011339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_97-15_0_5_line_146 |  | 144 | 146 | 0.019184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_97-15_0_5_line_147 |  | 144 | 145 | 0.0257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_97-15_0_5_line_148 |  | 146 | 147 | 0.018394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_97-15_0_5_line_149 |  | 146 | 148 | 0.0020445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_97-15_0_5_line_150 |  | 147 | 149 | 0.01596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_97-15_0_5_line_151 |  | 148 | 150 | 0.03075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_97-15_0_5_line_152 |  | 150 | 151 | 0.0050688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_97-15_0_5_line_153 |  | 151 | 152 | 0.025674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_97-15_0_5_line_154 |  | 152 | 153 | 0.0076443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_97-15_0_5_line_155 |  | 154 | 155 | 0.019566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_97-15_0_5_line_156 |  | 154 | 156 | 0.0051277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_97-15_0_5_line_157 |  | 155 | 157 | 0.013182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_97-15_0_5_trafo_84 | 0.63 MVA 20/0.4 kV | 159 | 120 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2681774.7681 | 1256438.6981 | 2681593.0201 | 1256586.8417
1 | 2681774.7681 | 1256438.6981 | 2681795.9612 | 1256427.2488 | 2681826.1923 | 1256417.7926
2 | 2681826.1923 | 1256417.7926 | 2681824.5775 | 1256412.3995 | 2681824.2319 | 1256407.9358 | 2681824.7555 | 1256405.1747
3 | 2681843.9056 | 1256655.7514 | 2681838.1886 | 1256657.0468
4 | 2681843.9056 | 1256655.7514 | 2681848.5508 | 1256654.0437
5 | 2681860.1249 | 1256649.789 | 2681848.5508 | 1256654.0437
6 | 2681860.1249 | 1256649.789 | 2681863.974 | 1256648.374
7 | 2681874.4421 | 1256643.6326 | 2681869.5878 | 1256646.3103 | 2681863.974 | 1256648.374
8 | 2681890.6587 | 1256634.6887 | 2681882.1731 | 1256639.368 | 2681874.4421 | 1256643.6326
9 | 2681891.1123 | 1256634.4386 | 2681890.6587 | 1256634.6887
10 | 2681891.1123 | 1256634.4386 | 2681918.6826 | 1256619.2354 | 2681924.4583 | 1256615.8627
11 | 2681937.2651 | 1256608.3843 | 2681924.4583 | 1256615.8627
12 | 2681937.2651 | 1256608.3843 | 2681951.5492 | 1256596.8804
13 | 2681937.2651 | 1256608.3843 | 2681922.2879 | 1256582.0556
14 | 2681951.5492 | 1256596.8804 | 2681965.8509 | 1256585.3624 | 2681971.7347 | 1256580.2181
15 | 2681914.5922 | 1256568.5273 | 2681922.2879 | 1256582.0556
16 | 2681983.1656 | 1256570.2239 | 2681971.7347 | 1256580.2181
17 | 2681914.5922 | 1256568.5273 | 2681910.3047 | 1256560.9903
18 | 2681983.1656 | 1256570.2239 | 2681985.5915 | 1256566.5992 | 2681995.8807 | 1256558.2909 | 2682010.3632 | 1256546.1711
19 | 2681910.3047 | 1256560.9903 | 2681905.1757 | 1256551.974
20 | 2682010.3632 | 1256546.1711 | 2682017.3341 | 1256543.2988 | 2682037.9987 | 1256535.1567 | 2682070.1577 | 1256528.0747
21 | 2682010.3632 | 1256546.1711 | 2681998.8497 | 1256530.5691
22 | 2682070.1577 | 1256528.0747 | 2682054.6962 | 1256509.6242 | 2682035.1998 | 1256493.274
23 | 2681998.8497 | 1256530.5691 | 2681997.571 | 1256528.8364 | 2681995.9076 | 1256526.7628
24 | 2682035.1998 | 1256493.274 | 2682034.7831 | 1256492.9245
25 | 2682188.5941 | 1256293.6726 | 2682184.8839 | 1256289.8293 | 2682182.8492 | 1256284.8195 | 2682182.6519 | 1256278.9345 | 2682184.2134 | 1256274.5751
26 | 2682188.5941 | 1256293.6726 | 2682192.606 | 1256296.4304 | 2682202.5146 | 1256303.6289 | 2682212.3442 | 1256307.9238
27 | 2682159.0104 | 1256278.1392 | 2682163.2898 | 1256275.2074 | 2682169.394 | 1256272.857 | 2682174.0623 | 1256267.451 | 2682178.8054 | 1256270.786 | 2682184.2134 | 1256274.5751
28 | 2682184.2134 | 1256274.5751 | 2682187.2108 | 1256271.0918 | 2682198.1124 | 1256261.8652
29 | 2682246.7527 | 1256322.9578 | 2682212.3442 | 1256307.9238
30 | 2682149.866 | 1256299.5508 | 2682155.218 | 1256303.0277 | 2682160.4773 | 1256306.659 | 2682155.8671 | 1256314.9457 | 2682153.8858 | 1256320.756
31 | 2682153.8858 | 1256320.756 | 2682157.9253 | 1256320.9789 | 2682161.3761 | 1256323.9512 | 2682166.5952 | 1256328.8496 | 2682179.8874 | 1256335.7059 | 2682180.0073 | 1256335.7949
32 | 2682149.866 | 1256299.5508 | 2682145.8193 | 1256306.3665 | 2682141.0584 | 1256320.132
33 | 2682149.866 | 1256299.5508 | 2682153.9976 | 1256292.6028 | 2682154.4127 | 1256288.9463
34 | 2682180.0073 | 1256335.7949 | 2682187.1212 | 1256341.077 | 2682188.1604 | 1256341.4508
35 | 2682159.0104 | 1256278.1392 | 2682156.702 | 1256280.887 | 2682154.7538 | 1256285.9416 | 2682154.4127 | 1256288.9463
36 | 2682159.0104 | 1256278.1392 | 2682145.194 | 1256262.1887
37 | 2682216.0721 | 1256246.6744 | 2682214.5105 | 1256247.9865 | 2682198.1124 | 1256261.8652
38 | 2682254.5555 | 1256308.5553 | 2682254.0349 | 1256310.7386 | 2682252.2677 | 1256314.706 | 2682249.4114 | 1256316.7123 | 2682246.7527 | 1256322.9578
39 | 2682246.704 | 1256297.7047 | 2682244.2278 | 1256303.8416 | 2682254.5555 | 1256308.5553
40 | 2682145.194 | 1256262.1887 | 2682128.3594 | 1256242.7538 | 2682127.7859 | 1256242.1747
41 | 2682137.5037 | 1256351.7523 | 2682138.0931 | 1256333.2019 | 2682140.4839 | 1256321.7931 | 2682141.0584 | 1256320.132
42 | 2682137.5037 | 1256351.7523 | 2682129.2182 | 1256349.8804 | 2682117.3823 | 1256347.2166
43 | 2682137.5037 | 1256351.7523 | 2682137.7721 | 1256357.4159 | 2682140.8591 | 1256375.1833 | 2682146.1455 | 1256395.944
44 | 2682087.785 | 1256349.6279 | 2682101.6837 | 1256343.7606 | 2682112.632 | 1256346.1475 | 2682117.3823 | 1256347.2166
45 | 2682259.2585 | 1256261.5961 | 2682249.2778 | 1256257.4098 | 2682229.9332 | 1256243.7419 | 2682224.2482 | 1256239.8044
46 | 2682224.2482 | 1256239.8044 | 2682220.0005 | 1256235.5644 | 2682215.671 | 1256231.2344 | 2682226.0457 | 1256220.0922
47 | 2682224.2482 | 1256239.8044 | 2682216.0721 | 1256246.6744
48 | 2682259.2585 | 1256261.5961 | 2682271.0632 | 1256243.0793 | 2682272.7334 | 1256240.8099
49 | 2682226.0457 | 1256220.0922 | 2682229.4758 | 1256216.4148 | 2682236.8369 | 1256207.1989 | 2682242.4784 | 1256197.4476 | 2682244.0319 | 1256194.5293
50 | 2682226.0457 | 1256220.0922 | 2682205.2006 | 1256207.4599 | 2682199.7458 | 1256207.0394 | 2682186.5549 | 1256199.7388
51 | 2682147.7335 | 1256113.6023 | 2682136.1397 | 1256128.8864 | 2682131.7873 | 1256140.8685 | 2682129.1763 | 1256144.7686 | 2682123.225 | 1256155.1161 | 2682121.0543 | 1256160.9905 | 2682120.9803 | 1256166.3157 | 2682123.0209 | 1256169.8244 | 2682125.787 | 1256171.5975 | 2682135.9519 | 1256175.5637 | 2682141.218 | 1256181.4301 | 2682150.7004 | 1256184.5751 | 2682166.386 | 1256183.1361 | 2682170.8789 | 1256185.478 | 2682173.9677 | 1256189.535 | 2682185.7941 | 1256199.3177 | 2682186.5549 | 1256199.7388
52 | 2681986.1282 | 1256514.6743 | 2681988.1627 | 1256517.1083 | 2681995.9076 | 1256526.7628
53 | 2682147.7335 | 1256113.6023 | 2682158.2406 | 1256120.0863 | 2682177.9647 | 1256131.4575 | 2682180.3199 | 1256132.402
54 | 2682054.9953 | 1256443.4558 | 2682075.6987 | 1256456.3474
55 | 2682054.9953 | 1256443.4558 | 2682066.089 | 1256422.8384 | 2682069.5786 | 1256415.7552
56 | 2682054.9953 | 1256443.4558 | 2682037.4141 | 1256429.1747
57 | 2681964.2016 | 1256156.1249 | 2681952.3635 | 1256202.1626
58 | 2681964.2016 | 1256156.1249 | 2682019.1885 | 1256168.4511 | 2682044.2766 | 1256177.0051 | 2682061.9893 | 1256186.024
59 | 2681887.9895 | 1256181.4453 | 2681893.2557 | 1256163.8937 | 2681898.6255 | 1256142.663 | 2681964.2016 | 1256156.1249
60 | 2682061.9893 | 1256186.024 | 2682050.7949 | 1256198.1003 | 2682045.8821 | 1256203.5144
61 | 2681887.9895 | 1256181.4453 | 2681877.9993 | 1256216.7771
62 | 2682043.6104 | 1256206.0179 | 2682045.8821 | 1256203.5144
63 | 2682114.7222 | 1256228.9849 | 2682127.7859 | 1256242.1747
64 | 2682087.785 | 1256349.6279 | 2682089.7974 | 1256355.7049 | 2682089.1531 | 1256366.2706 | 2682085.5235 | 1256376.1834
65 | 2682087.785 | 1256349.6279 | 2682079.5401 | 1256352.9829 | 2682073.0769 | 1256352.9488 | 2682065.3959 | 1256347.1936
66 | 2681976.364 | 1256502.9931 | 2681986.1282 | 1256514.6743
67 | 2681976.364 | 1256502.9931 | 2681963.7698 | 1256487.9263
68 | 2681952.6923 | 1256474.674 | 2681963.7698 | 1256487.9263
69 | 2681952.6923 | 1256474.674 | 2681949.1415 | 1256470.3844
70 | 2681952.6923 | 1256474.674 | 2681941.6109 | 1256482.9968
71 | 2681905.1757 | 1256551.974 | 2681902.8671 | 1256547.9157
72 | 2681896.8881 | 1256537.4051 | 2681902.8671 | 1256547.9157
73 | 2681896.8881 | 1256537.4051 | 2681896.8881 | 1256537.4051 | 2681895.9584 | 1256535.63
74 | 2681931.7458 | 1256449.3692 | 2681949.1415 | 1256470.3844
75 | 2681941.6109 | 1256482.9968 | 2681939.7244 | 1256484.4136
76 | 2681931.7458 | 1256449.3692 | 2681931.0099 | 1256448.4803
77 | 2681889.0627 | 1256522.4633 | 2681895.9584 | 1256535.63
78 | 2681829.2856 | 1256387.1788 | 2681825.0373 | 1256403.6882 | 2681824.7555 | 1256405.1747
79 | 2681923.8913 | 1256436.9468 | 2681925.9506 | 1256442.3683 | 2681931.0099 | 1256448.4803
80 | 2681829.2856 | 1256387.1788 | 2681846.4923 | 1256392.9169
81 | 2681829.2856 | 1256387.1788 | 2681830.8123 | 1256381.8761
82 | 2681923.8913 | 1256436.9468 | 2681924.3413 | 1256432.2272 | 2681931.6743 | 1256419.2059
83 | 2681923.8913 | 1256436.9468 | 2681909.1088 | 1256447.8506
84 | 2681947.227 | 1256375.3674 | 2681946.2265 | 1256382.8037 | 2681940.4735 | 1256401.7495 | 2681935.3828 | 1256412.6207 | 2681931.6743 | 1256419.2059
85 | 2681951.0042 | 1256364.0333 | 2681947.227 | 1256375.3674
86 | 2681947.227 | 1256375.3674 | 2681933.3671 | 1256372.3082
87 | 2681951.0042 | 1256364.0333 | 2681951.5087 | 1256358.1024 | 2681952.7967 | 1256349.8363
88 | 2681951.0042 | 1256364.0333 | 2681958.1595 | 1256369.0917
89 | 2681933.3307 | 1256372.3001 | 2681933.3671 | 1256372.3082
90 | 2682009.2379 | 1256407.257 | 2681990.0843 | 1256392.9457
91 | 2682024.1337 | 1256418.387 | 2682009.2379 | 1256407.257
92 | 2681982.0989 | 1256386.979 | 2681990.0843 | 1256392.9457
93 | 2682024.1337 | 1256418.387 | 2682033.4786 | 1256410.7551 | 2682044.8112 | 1256398.4695 | 2682046.7525 | 1256393.2384
94 | 2682024.1337 | 1256418.387 | 2682037.4141 | 1256429.1747
95 | 2681958.1595 | 1256369.0917 | 2681982.0989 | 1256386.979
96 | 2681958.1595 | 1256369.0917 | 2681957.0791 | 1256362.1493 | 2681957.4318 | 1256357.7354
97 | 2681957.4318 | 1256357.7354 | 2681958.5754 | 1256343.4224 | 2681959.8973 | 1256337.6378
98 | 2682065.3959 | 1256347.1936 | 2682061.7348 | 1256358.2957 | 2682060.7534 | 1256359.7897
99 | 2682065.3959 | 1256347.1936 | 2682065.4754 | 1256343.6364
100 | 2681952.7967 | 1256349.8363 | 2681955.7221 | 1256331.0625 | 2681956.9287 | 1256325.6181
101 | 2681972.296 | 1256294.3195 | 2681963.5984 | 1256308.0318 | 2681958.5057 | 1256318.5026 | 2681956.9287 | 1256325.6181
102 | 2681830.8123 | 1256381.8761 | 2681837.2978 | 1256359.3497
103 | 2681843.182 | 1256338.912 | 2681837.2978 | 1256359.3497
104 | 2681843.182 | 1256338.912 | 2681844.259 | 1256335.1944
105 | 2681843.182 | 1256338.912 | 2681856.9062 | 1256342.5517
106 | 2681846.4923 | 1256392.9169 | 2681847.633 | 1256393.2974
107 | 2681844.259 | 1256335.1944 | 2681851.892 | 1256308.8472
108 | 2681869.7237 | 1256345.9509 | 2681856.9062 | 1256342.5517
109 | 2681868.0242 | 1256400.0975 | 2681847.633 | 1256393.2974
110 | 2681853.3755 | 1256303.7262 | 2681851.892 | 1256308.8472
111 | 2681868.0242 | 1256400.0975 | 2681869.3462 | 1256400.5384
112 | 2681873.4296 | 1256401.9001 | 2681869.3462 | 1256400.5384
113 | 2681918.8984 | 1256369.1145 | 2681933.3307 | 1256372.3001
114 | 2681918.8984 | 1256369.1145 | 2681905.6376 | 1256366.1875
115 | 2681905.6376 | 1256366.1875 | 2681905.5181 | 1256366.1612 | 2681908.053 | 1256355.557
116 | 2681911.0101 | 1256343.1864 | 2681908.053 | 1256355.557
117 | 2682053.9204 | 1256328.9763 | 2682055.8582 | 1256333.9069 | 2682065.4754 | 1256343.6364
118 | 2682053.9204 | 1256328.9763 | 2682054.2227 | 1256325.6668 | 2682055.0745 | 1256318.6288 | 2682054.2224 | 1256307.7421
119 | 2682053.9204 | 1256328.9763 | 2682050.4886 | 1256333.332 | 2682042.9097 | 1256334.35 | 2682037.9372 | 1256334.5035 | 2682031.6352 | 1256333.1818 | 2682025.6931 | 1256329.8303
120 | 2682025.6931 | 1256329.8303 | 2682022.3495 | 1256325.1167
121 | 2681998.8013 | 1256322.3045 | 2682005.3712 | 1256321.8984 | 2682012.2114 | 1256317.045 | 2682019.161 | 1256320.6217 | 2682022.3495 | 1256325.1167
122 | 2681998.8013 | 1256322.3045 | 2681994.6446 | 1256322.5615 | 2681989.4629 | 1256319.8543 | 2681988.8058 | 1256318.8562
123 | 2682054.2224 | 1256307.7421 | 2682058.1829 | 1256299.5241 | 2682064.791 | 1256295.6349 | 2682072.0008 | 1256294.0447 | 2682077.2086 | 1256289.9805 | 2682081.4142 | 1256284.7292
124 | 2681984.6119 | 1256312.4848 | 2681988.8058 | 1256318.8562
125 | 2681974.1723 | 1256296.625 | 2681984.6119 | 1256312.4848
126 | 2681972.296 | 1256294.3195 | 2681974.1723 | 1256296.625
127 | 2681974.1723 | 1256296.625 | 2681976.8619 | 1256291.9365 | 2681985.9013 | 1256280.7479
128 | 2681972.296 | 1256294.3195 | 2681991.6176 | 1256267.222
129 | 2681972.296 | 1256294.3195 | 2681957.6634 | 1256289.0207
130 | 2682002.5039 | 1256253.4178 | 2681991.6176 | 1256267.222
131 | 2681957.6634 | 1256289.0207 | 2681950.7128 | 1256286.5038 | 2681949.9055 | 1256286.1472
132 | 2682064.3968 | 1256239.22 | 2682071.6489 | 1256239.4762 | 2682071.6489 | 1256239.4762
133 | 2682064.3968 | 1256239.22 | 2682058.7666 | 1256247.0924 | 2682056.9338 | 1256252.3363
134 | 2682035.2415 | 1256266.7258 | 2682048.2204 | 1256267.3728 | 2682051.7069 | 1256266.1423 | 2682055.7475 | 1256260.305 | 2682056.7168 | 1256252.9573 | 2682056.9338 | 1256252.3363
135 | 2682035.2415 | 1256266.7258 | 2682035.2415 | 1256266.7258 | 2682031.5239 | 1256263.9564
136 | 2682013.8171 | 1256249.6272 | 2682026.2982 | 1256260.0635 | 2682031.5239 | 1256263.9564
137 | 2682009.2391 | 1256244.7156 | 2682011.3696 | 1256246.6355 | 2682013.8171 | 1256249.6272
138 | 2682009.2391 | 1256244.7156 | 2682007.4097 | 1256247.1921 | 2682002.5039 | 1256253.4178
139 | 2682009.2391 | 1256244.7156 | 2682021.3826 | 1256229.9948 | 2682032.8371 | 1256217.639
140 | 2682002.5039 | 1256253.4178 | 2681989.9623 | 1256242.7365
141 | 2682043.6104 | 1256206.0179 | 2682032.8371 | 1256217.639
142 | 2682110.7832 | 1256225.0077 | 2682114.7222 | 1256228.9849
143 | 2682110.7832 | 1256225.0077 | 2682102.3073 | 1256216.4462
144 | 2681989.9623 | 1256242.7365 | 2681973.4622 | 1256228.6836
145 | 2681939.5336 | 1256281.5654 | 2681949.9055 | 1256286.1472
146 | 2681853.3755 | 1256303.7262 | 2681858.6313 | 1256285.2737
147 | 2681853.3755 | 1256303.7262 | 2681876.9657 | 1256313.9241
148 | 2681858.6313 | 1256285.2737 | 2681876.5784 | 1256289.3026
149 | 2681858.6313 | 1256285.2737 | 2681859.1876 | 1256283.3063
150 | 2681892.1505 | 1256292.7984 | 2681876.5784 | 1256289.3026
151 | 2681859.1876 | 1256283.3063 | 2681867.5545 | 1256253.7161
152 | 2681867.5545 | 1256253.7161 | 2681868.9337 | 1256248.8386
153 | 2681875.9194 | 1256224.133 | 2681868.9337 | 1256248.8386
154 | 2681875.9194 | 1256224.133 | 2681877.9993 | 1256216.7771
155 | 2681939.5278 | 1256276.7719 | 2681951.3198 | 1256261.1587
156 | 2681939.5278 | 1256276.7719 | 2681938.8274 | 1256277.6993 | 2681939.4607 | 1256281.5332 | 2681939.5336 | 1256281.5654
157 | 2681959.2646 | 1256250.6394 | 2681951.3198 | 1256261.1587

## bus_geodata
| x | y | coords
0 | 2681593.0201 | 1256586.8417
1 | 2681774.7681 | 1256438.6981
2 | 2681826.1923 | 1256417.7926
3 | 2681838.1886 | 1256657.0468
4 | 2681843.9056 | 1256655.7514
5 | 2681848.5508 | 1256654.0437
6 | 2681860.1249 | 1256649.789
7 | 2681863.974 | 1256648.374
8 | 2681874.4421 | 1256643.6326
9 | 2681890.6587 | 1256634.6887
10 | 2681891.1123 | 1256634.4386
11 | 2681924.4583 | 1256615.8627
12 | 2681937.2651 | 1256608.3843
13 | 2681951.5492 | 1256596.8804
14 | 2681922.2879 | 1256582.0556
15 | 2681971.7347 | 1256580.2181
16 | 2681914.5922 | 1256568.5273
17 | 2681983.1656 | 1256570.2239
18 | 2681910.3047 | 1256560.9903
19 | 2682010.3632 | 1256546.1711
20 | 2682070.1577 | 1256528.0747
21 | 2681998.8497 | 1256530.5691
22 | 2682035.1998 | 1256493.274
23 | 2682188.5941 | 1256293.6726
24 | 2682184.2134 | 1256274.5751
25 | 2682212.3442 | 1256307.9238
26 | 2682153.8858 | 1256320.756
27 | 2682149.866 | 1256299.5508
28 | 2682180.0073 | 1256335.7949
29 | 2682159.0104 | 1256278.1392
30 | 2682198.1124 | 1256261.8652
31 | 2682246.7527 | 1256322.9578
32 | 2682254.5555 | 1256308.5553
33 | 2682154.4127 | 1256288.9463
34 | 2682145.194 | 1256262.1887
35 | 2682141.0584 | 1256320.1321
36 | 2682137.5037 | 1256351.7523
37 | 2682117.3823 | 1256347.2166
38 | 2682146.1455 | 1256395.944
39 | 2682224.2482 | 1256239.8044
40 | 2682259.2585 | 1256261.5961
41 | 2682226.0457 | 1256220.0922
42 | 2682216.0721 | 1256246.6744
43 | 2682246.704 | 1256297.7047
44 | 2682244.0319 | 1256194.5293
45 | 2682186.5549 | 1256199.7388
46 | 2681995.9076 | 1256526.7628
47 | 2682147.7335 | 1256113.6023
48 | 2682180.3199 | 1256132.402
49 | 2682075.6987 | 1256456.3474
50 | 2682054.9953 | 1256443.4558
51 | 2682034.7831 | 1256492.9245
52 | 2681964.2016 | 1256156.1249
53 | 2681952.3635 | 1256202.1626
54 | 2682061.9893 | 1256186.024
55 | 2681887.9895 | 1256181.4453
56 | 2682045.8821 | 1256203.5144
57 | 2682272.7334 | 1256240.8099
58 | 2682188.1604 | 1256341.4508
59 | 2682127.7859 | 1256242.1747
60 | 2682087.785 | 1256349.6279
61 | 2681986.1282 | 1256514.6743
62 | 2681976.364 | 1256502.9931
63 | 2681963.7698 | 1256487.9263
64 | 2681952.6923 | 1256474.674
65 | 2681905.1757 | 1256551.974
66 | 2681902.8671 | 1256547.9157
67 | 2681896.8881 | 1256537.4051
68 | 2681949.1415 | 1256470.3844
69 | 2681941.6109 | 1256482.9968
70 | 2681931.7458 | 1256449.3692
71 | 2681939.7244 | 1256484.4136
72 | 2681889.0627 | 1256522.4633
73 | 2681895.9584 | 1256535.63
74 | 2681824.7555 | 1256405.1747
75 | 2681931.0099 | 1256448.4803
76 | 2681829.2856 | 1256387.1788
77 | 2681923.8913 | 1256436.9468
78 | 2681931.6743 | 1256419.2059
79 | 2681909.1088 | 1256447.8506
80 | 2681947.227 | 1256375.3674
81 | 2681951.0042 | 1256364.0333
82 | 2681933.3671 | 1256372.3082
83 | 2682009.2379 | 1256407.257
84 | 2681990.0843 | 1256392.9457
85 | 2682024.1337 | 1256418.387
86 | 2681982.0989 | 1256386.979
87 | 2682046.7525 | 1256393.2384
88 | 2682037.4141 | 1256429.1747
89 | 2681958.1595 | 1256369.0917
90 | 2681957.4318 | 1256357.7354
91 | 2682060.7534 | 1256359.7897
92 | 2682065.3959 | 1256347.1936
93 | 2682069.5786 | 1256415.7552
94 | 2681959.8973 | 1256337.6378
95 | 2681952.7967 | 1256349.8363
96 | 2681956.9287 | 1256325.6181
97 | 2681830.8123 | 1256381.8761
98 | 2681837.2978 | 1256359.3497
99 | 2681843.182 | 1256338.912
100 | 2681846.4923 | 1256392.9169
101 | 2681844.259 | 1256335.1944
102 | 2681856.9062 | 1256342.5517
103 | 2681847.633 | 1256393.2974
104 | 2681851.892 | 1256308.8472
105 | 2681869.7237 | 1256345.9509
106 | 2681868.0242 | 1256400.0975
107 | 2681869.3462 | 1256400.5384
108 | 2681873.4296 | 1256401.9001
109 | 2681933.3307 | 1256372.3001
110 | 2681918.8984 | 1256369.1145
111 | 2681905.6376 | 1256366.1875
112 | 2681908.053 | 1256355.557
113 | 2681911.0101 | 1256343.1864
114 | 2682065.4754 | 1256343.6364
115 | 2682085.5235 | 1256376.1834
116 | 2682053.9204 | 1256328.9763
117 | 2682025.6931 | 1256329.8303
118 | 2682022.3495 | 1256325.1167
119 | 2681998.8013 | 1256322.3045
120 | 2682054.2224 | 1256307.7421
121 | 2681988.8058 | 1256318.8562
122 | 2682081.4142 | 1256284.7292
123 | 2681984.6119 | 1256312.4848
124 | 2681974.1723 | 1256296.625
125 | 2681972.296 | 1256294.3195
126 | 2681985.9013 | 1256280.7479
127 | 2681991.6176 | 1256267.222
128 | 2681957.6634 | 1256289.0207
129 | 2682071.6489 | 1256239.4762
130 | 2682064.3968 | 1256239.22
131 | 2682056.9338 | 1256252.3364
132 | 2682035.2415 | 1256266.7258
133 | 2682031.5239 | 1256263.9564
134 | 2682013.8171 | 1256249.6272
135 | 2682009.2391 | 1256244.7156
136 | 2682002.5039 | 1256253.4178
137 | 2682032.8371 | 1256217.639
138 | 2682043.6104 | 1256206.0179
139 | 2682110.7832 | 1256225.0077
140 | 2682114.7222 | 1256228.9849
141 | 2682102.3073 | 1256216.4462
142 | 2681989.9623 | 1256242.7365
143 | 2681949.9055 | 1256286.1472
144 | 2681853.3755 | 1256303.7262
145 | 2681876.9657 | 1256313.9241
146 | 2681858.6313 | 1256285.2737
147 | 2681876.5784 | 1256289.3026
148 | 2681859.1876 | 1256283.3063
149 | 2681892.1505 | 1256292.7984
150 | 2681867.5545 | 1256253.7161
151 | 2681868.9337 | 1256248.8386
152 | 2681875.9194 | 1256224.133
153 | 2681877.9993 | 1256216.7771
154 | 2681939.5278 | 1256276.7719
155 | 2681951.3198 | 1256261.1587
156 | 2681939.5336 | 1256281.5654
157 | 2681959.2646 | 1256250.6394
158 | 2681973.4622 | 1256228.6836
159 | 2682053.9204 | 1256328.9763

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1